Growatt Inverter Modbus RTU Protocol

V1.20

Make： weiwei.shi

Check：  qixing.ren

Authorize： liangcai.wu

Effective date：

Change Record

| Index | Version | Change Content | Make | Make date |
| --- | --- | --- | --- | --- |
| 1 | 00 | First Republic | Weiwei.shi | 2020.4.28 |

Instruction：Register range for various types of inverter  TL-X（MIN Type）：03 register range：0~124,3000~3124；04 register range：3000~3124,3125~3249

TL3-X(MAX、MID、MAC Type)：03 register range：0~124,125~249；

04 register range：0~124,125~249

Storage(MIX Type)：03 register range：0~124,1000~1124；04 register range：0~124,1000~1124

Storage(SPA Type)：03 register range：0~124,1000~1124；04 register range：1000~1124,2000~2124

Storage(SPH Type)：03 register range：0~124,1000~1124；04 register range：0~124,1000~1124

catalog

1 Data format	5

2 Command Format	5

3 Device Message Transmission Mode / Framing	8

4  Register map	9

4.1 Holding Reg	9

4.2 Input Reg	33

5 Set address	65

6 Notice	65

# Data format

Valid slave device addresses are in the range of 0 – 254 decimal.

The individual slave devices are assigned addresses in the range of 1 – 254.

0 is the broadcast address

It is 16bits (two bytes) unsigned integer for each holding and input register;

# Command Format

Function 3 Read holding register

Response Error:

11 0x80|0x03 ErrornumCRC(Errornum as a byte)

Function 4 Read input  register

Response Error:

11 0x80|0x04 ErrornumCRC  (Errornum as a byte)

Function 6 Preset single register

Response Error:

11 0x80|0x06 ErrornumCRC  (Errornum as a byte)

Function 16 Preset multiple register

Response Error:

11 0x80|0x10 ErrornumCRC  (Errornum as a byte)

# Device Message Transmission Mode / Framing

RTU Mode

When controllers are setup to communicate on a Modbus network using RTU (Remote Terminal Unit) mode, each 8–bit byte in a message contains two 4–bit hexadecimal characters. Each message must be transmitted in a continuous stream.

The format for each byte in RTU mode is:

Coding System: 8–bit binary, hexadecimal 0–9, A–F

Two hexadecimal characters contained in each

8–bit field of the message

Bits per Byte:

1 start bit

8 data bits, least significant bit sent first

None parity

1 stop bit

Error Check Field: Cyclical Redundancy Check (CRC)

The baud rate of the transmission is:

Default Baud Rate: 9600 bps

Can be set through hold register 22

Minimum CMD period (RS485 Time out): 850ms.

Wait for minimum850ms to send a new CMD after last CMD. Suggestion is 1s;

Maximum Data Length Define:

Maximum read data length is 125 words in read command;

Maximum update data length is 125 words in preset command;

Note:

Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing other registers;

# Register map

It is 16bits (two bytes) unsigned integer for each holding and input register;

## Holding Reg

| Registe r NO. | Variable Name | Description | Write or not | Value | Unit | Initial value | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
| First group |  |  |  |  |  |  |  |
| 00 | OnOff | Remote On/Off . On（1）；Off（0） | W | 0or1 |  | 1 | When PV restart, recover 1. |
| 01 | SaftyFuncEn | Bit0: SPI enable Bit1: AutoTestStart Bit2: LVFRT enable Bit3:FreqDerating Enable Bit4: Softstart enable Bit5: DRMS enable Bit6:PowerVoltFunc Enable Bit7: HVFRT enable Bit8:ROCOF enable Bit9: Recover FreqDeratingMode Enable Bit10~15:预留 | W | 0 : disable 1: enable |  |  | SPI: system protection interface Bit0~3:for CEI0-21 Bit4~6:for SAA |
| 02 | PF CMD memory state | Set Holding register3,4,5,99 CMD will be memory or not(1/0), if not, these settings are the initial value. | W | 0or1 |  | 0 | Means these settings will be acting or not when next power on |
| 03 | Active P Rate | Inverter Max output active power percent | W | 0-100 or 255 | % | 255 | 255: power is not be limited |
| 04 | Reactive P Rate | Inverter max output reactive power percent | W | -100-100 or 255 | % | 255 | 255: power is not be limited |
| 05 | Power factor | Inverter output power factor’s 10000 times | W | 0-20000, 0-10000 is |  | 0 |  |

|  |  |  |  | underexci ted, other is overexcit ed |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 06 | Pmax H | Normal power (high) |  |  | 0.1VA |  |  |
| 07 | Pmax L | Normal power (low) |  |  | 0.1VA |  |  |
| 08 | Vnormal | Normal work PV voltage |  |  | 0.1V |  |  |
| 09 | Fw version H | Firmware version (high) |  |  | ASCII |  |  |
| 10 | Fw version M | Firmware version (middle) |  |  |  |  |  |
| 11 | Fw version L | Firmware version (low) |  |  |  |  |  |
| 12 | Fw version2 H | Control Firmware version (high) |  |  | ASCII |  |  |
| 13 | Fw version2 M | Control Firmware version (middle) |  |  |  |  |  |
| 14 | Fw version2 L | Control Firmware version (low) |  |  |  |  |  |
| 15 | LCD language | LCD language | W | 0-5 |  |  | 0: Italian; 1: English; 2: German; 3: Spanish; 4: French; 5: Chinese; 6：Polish 7：Portugues 8：Hungary |
| 16 | CountrySele cted | Country Selected or not | W | 0: need to select; 1: have selected |  |  |  |
| 17 | Vpv start | Input start voltage | W |  | 0.1V |  |  |
| 18 | Time start | Start time | W |  | 1s |  |  |
| 19 | RestartDelay Time | Restart Delay Time after fault back; | W |  | 1s |  |  |
| 20 | wPowerStart Slope | Power start slope | W | 1-1000 | 0.1% |  |  |
| 21 | wPowerRest artSlopeEE | Power restart slope | W | 1-1000 | 0.1% |  |  |
| 22 | wSelectBaud | Select | W | 0-1 |  | 0 |  |

|  | rate | communicationbaudrat e 0: 9600bps 1:38400bps |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 23 | Serial NO | Serial number 1-2 |  |  | ASCII |  |  |
| 24 | Serial NO | Serial number 3-4 |  |  |  |  |  |
| 25 | Serial NO | Serial number 5-6 |  |  |  |  |  |
| 26 | Serial NO | Serial number 7-8 |  |  |  |  |  |
| 27 | Serial NO | Serial number 9-10 |  |  |  |  |  |
| 28 | Module H | Inverter Module (high) |  | &*5 |  |  |  |
| 29 | Module L | Inverter Module (low) |  | &*5 |  |  |  |
| 30 | Com Address | Communicate address | W | 1-254 |  | 1 |  |
| 31 | FlashStart | Update firmware | W | 1 |  |  |  |
| 32 | Reset User Info | Reset User Information | W | 0x0001 |  |  |  |
| 33 | Reset to factory | Reset to factory | W | 0x0001 |  |  |  |
| 34 | Manufacture r Info 8 | Manufacturer information (high) |  |  | ASCII |  |  |
| 35 | Manufacture r Info 7 | Manufacturer information (middle) |  |  |  |  |  |
| 36 | Manufacture r Info 6 | Manufacturer information (low) |  |  |  |  |  |
| 37 | Manufacture r Info 5 | Manufacturer information (high) |  |  |  |  |  |
| 38 | Manufacture r Info 4 | Manufacturer information (middle) |  |  |  |  |  |
| 39 | Manufacture r Info3 | Manufacturer information (low) |  |  |  |  |  |
| 40 | Manufacture r Info 2 | Manufacturer information (low) |  |  |  |  |  |
| 41 | Manufacture r Info 1 | Manufacturer information (high) |  |  |  |  |  |
| 42 | bfailsafeEn; | G100 fail safe | W | Enable:1 Disable:0 |  |  | English G100 fail safe set |
| 43 | DTC | Device Type Code |  | &*6 |  |  |  |
| 44 | TP | Input tracker num and output phase num |  | Eg:0x020 3 is two MPPT and 3ph output |  |  |  |

| 45 | Sys Year | System time-year | W | Year offset is 0 |  |  | Local time |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 46 | Sys Month | System time- Month | W |  |  |  |  |
| 47 | Sys Day | System time- Day | W |  |  |  |  |
| 48 | Sys Hour | System time- Hour | W |  |  |  |  |
| 49 | Sys Min | System time- Min | W |  |  |  |  |
| 50 | Sys Sec | System time- Second | W |  |  |  |  |
| 51 | Sys Weekly | System Weekly | W | 0-6 |  |  |  |
| 52 | Vac low | Grid voltage low limit protect | W |  | 0.1V |  |  |
| 53 | Vac high | Grid voltage high limit protect | W |  | 0.1V |  |  |
| 54 | Fac low | Grid frequency low limit protect | W |  | 0.01 Hz |  |  |
| 55 | Fac high | Grid high frequencylimit protect | W |  | 0.01 Hz |  |  |
| 56 | Vac low 2 | Grid voltage low limit protect 2 | W |  | 0.1V |  |  |
| 57 | Vac high 2 | Grid voltage high limit protect 2 | W |  | 0.1V |  |  |
| 58 | Fac low 2 | Grid frequency low limit protect 2 | W |  | 0.01 Hz |  |  |
| 59 | Fac high 2 | Grid high frequency limit protect 2 | W |  | 0.01 Hz |  |  |
| 60 | Vac low 3 | Grid voltage low limit protect 3 | W |  | 0.1V |  |  |
| 61 | Vac high 3 | Grid voltage high limit protect 3 | W |  | 0.1V |  |  |
| 62 | Fac low 3 | Grid frequency low limit protect 3 | W |  | 0.01Hz |  |  |
| 63 | Fac high 3 | Grid frequency high limit protect 3 | W |  | 0.01Hz |  |  |
| 64 | Vac low C | Grid low voltage limit connect to Grid | W |  | 0.1V |  |  |
| 65 | Vac high C | Grid high voltage limit connect to Grid | W |  | 0.1V |  |  |
| 66 | Fac low C | Grid low frequency limit connect to Grid | W |  | 0.01 Hz |  |  |
| 67 | Fac high C | Grid high frequency limit connect to Grid | W |  | 0.01 Hz |  |  |
| 68 | Vac low1 time | Grid voltage low limit protect time 1 | W |  | Cycle |  |  |

| 69 | Vac time | high1 | Grid voltage high limit protect time 1 | W |  | Cycle |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 70 | Vac time | low2 | Grid voltage low limit protect time 2 | W |  | Cycle |  |  |
| 71 | Vac time | high2 | Grid voltage high limit protect time 2 | W |  | Cycle |  |  |
| 72 | Fac time | low1 | Grid frequency low limit protect time 1 | W |  | Cycle |  |  |
| 73 | Fac time | high1 | Grid frequency high limit protect time 1 | W |  | Cycle |  |  |
| 74 | Fac time | low2 | Grid frequency low limit protect time 2 | W |  | Cycle |  |  |
| 75 | Fac time | high2 | Grid frequency high limit protect time 2 | W |  | Cycle |  |  |
| 76 | Vac time | low3 | Grid voltage low limit protect time 3 | W |  | Cycle |  |  |
| 77 | Vac time | high3 | Grid voltage high limit protect time 3 | W |  | Cycle |  |  |
| 78 | Fac time | low3 | Grid frequency low limit protect time 3 | W |  | Cycle |  |  |
| 79 | Fac time | high3 | Grid frequency high limit protect time 3 | W |  | Cycle |  |  |
| 80 | U10min |  | Volt protection for 10 min | W |  | 0.1V | 1.1Vn |  |
| 81 | PV Voltage High Fault |  | PV Voltage High Fault | W |  | 0.1V |  |  |
| 82 | FW Build No. 5 |  | FW Build version |  |  | ASCII |  |  |
| 83 | FW Build No. 4 |  | FW Build version |  |  | ASCII |  |  |
| 84 | FW Build No. 3 |  | DSP1 FW Build No. |  |  | ASCII |  |  |
| 85 | FW Build No. 2 |  | DSP2 FW Build No. |  |  | ASCII |  |  |
| 86 | FW Build No. 1 |  | M3 FW Build No. |  |  | ASCII |  |  |
| 87 | FW Build No. 0 |  | CPLD FW Build No. |  |  | ASCII |  |  |
| 88 | ModbusVers ion |  | Modbus Version |  | Eg：207 is V2.07 | Int(16 bits) |  |  |
| 89 | PFModel |  | Set PF function Model 0: PF=1 | W |  |  |  |  |

|  |  | 1: PF by set 2: default PF line 3: User PF line 4: UnderExcited (Inda) Reactive Power 5: OverExcited(Capa) Reactive Power 6：Q(v)model 7：Direct Control mode |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 90 | GPRS IP Flag | Bit0-3:read:1;Set GPRS IP Successed Write:2;Read GPRS IP Successed Bit4-7:GPRS status | W | Bit0-3:ab out GPRS IP SET Bit4-7:ab out GRPRS Status |  |  |  |
| 91 | FreqDerateS tart | Frequency derating start point | W |  | 0.01H Z |  |  |
| 92 | FLrate | Frequency – load limit rate | W | 0-100 | 10tim es |  |  |
| 93 | V1S | CEI021 V1S Q(v) | W | V1S<V2S | 0.1V |  |  |
| 94 | V2S | CEI021 V2S Q(v) | W |  | 0.1V |  |  |
| 95 | V1L | CEI021 V1L Q(v) | W | V1L<V1S | 0.1V |  |  |
| 96 | V2L | CEI021 V2L Q(v) | W | V2L<V1L | 0.1V |  |  |
| 97 | Qlockinpow er | Q(v) lock in active power of CEI021 | W | 0-100 | Percen t |  |  |
| 98 | QlockOutpo wer | Q(v) lock Out active power of CEI021 | W | 0-100 | Percen t |  |  |
| 99 | LIGridV | Lock in gird volt of CEI021 PF line | W | nVn | 0.1V |  |  |
| 100 | LOGridV | Lock out gird volt of CEI021 PF line | W | nVn | 0.1V |  |  |
| 101 | PFAdj1 | PF adjust value 1 |  | 4096 is 1 |  |  |  |
| 102 | PFAdj2 | PF adjust value 2 |  | 4096 is 1 |  |  |  |
| 103 | PFAdj3 | PF adjust value 3 |  | 4096 is 1 |  |  |  |
| 104 | PFAdj4 | PF adjust value 4 |  | 4096 is 1 |  |  |  |
| 105 | PFAdj5 | PF adjust value 5 |  | 4096 is 1 |  |  |  |
| 106 | PFAdj6 | PF adjust value 6 |  | 4096 is 1 |  |  |  |
| 107 | QVRPDelayTi meEE | QV Reactive Power delaytime | W | 0-30 | 1S | 3S |  |
| 108 | OverFDeratD | Overfrequency derati | W | 0-20 | 50ms | 0 |  |

|  | elayTimeEE | ngdelaytime |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 109 | QpercentMa x | Qmax for Q(V) curve | W | 0-1000 | 0.1% |  |  |
| 110 | PFLineP1_LP | PF limit line point 1 load percent | W | 0-255 | percen t |  | 255 means no this point |
| 111 | PFLineP1_PF | PF limit line point 1 power factor | W | 0-20000 |  |  |  |
| 112 | PFLineP2_LP | PF limit line point 2 load percent | W | 0-255 | percen t |  | 255 means no this point |
| 113 | PFLineP2_PF | PF limit line point 2power factor | W | 0-20000 |  |  |  |
| 114 | PFLineP3_LP | PF limit line point 3 load percent | W | 0-255 | percen t |  | 255 means no this point |
| 115 | PFLineP3_PF | PF limit line point 3 power factor | W | 0-20000 |  |  |  |
| 116 | PFLineP4_LP | PF limit line point 4 load percent | W | 0-255 | percen t |  | 255 means no this point |
| 117 | PFLineP4_PF | PF limit line point 4 power factor | W | 0-20000 |  |  |  |
| 118 | Module 4 | Inverter Module (4) |  | &*11 |  |  | SxxBxx |
| 119 | Module 3 | Inverter Module (3) |  | &*11 |  |  | DxxTxx |
| 120 | Module 2 | Inverter Module (2) |  | &*11 |  |  | PxxUxx |
| 121 | Module 1 | Inverter Module (1) |  | &*11 |  |  | Mxxxx Power |
| 122 | ExportLimit_ En/dis | ExportLimit_En/dis | R/W | 1/0 |  |  | ExportLimit enable, 0: Disable exportLimit; 1: Enable 485 exportLimit; 2: Enable 232 exportLimit; 3: Enable CT exportLimit; |
| 123 | ExportLimitP owerRate | ExportLimitPowerRate | R/W | -1000~+1 000 | 0.1% |  | ExportLimit PowerRate |
| 124 | TrakerModel | Traker Model | W | 0,1,2 |  |  | 0:Independent 1:DC Source 2:Parallel |
| Second group |  |  |  |  |  |  |  |
| 125 | INV Type-1 | Inverter type-1 | R |  | ASCII |  | Reserved |
| 126 | INV Type-2 | Inverter type-2 | R |  | ASCII |  |  |
| 127 | INV Type-3 | Inverter type-3 | R |  | ASCII |  |  |
| 128 | INV Type-4 | Inverter type-4 | R |  | ASCII |  |  |
| 129 | INV Type-5 | Inverter type-5 | R |  | ASCII |  |  |
| 130 | INV Type-6 | Inverter type-6 | R |  | ASCII |  |  |
| 131 | INV Type-7 | Inverter type-7 | R |  | ASCII |  |  |
| 132 | INV Type-8 | Inverter type-8 | R |  | ASCII |  |  |

| 133 | BLVersion1 | Boot loader version1 | R |  |  |  | Reserved |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 134 | BLVersion2 | Boot loader version2 | R |  |  |  | Reserved |
| 135 | BLVersion3 | Boot loader version3 | R |  |  |  | Reserved |
| 136 | BLVersion4 | Boot loader version4 | R |  |  |  | Reserved |
| 137 | Reactive P ValueH | Reactive PowerH | R/W |  | 0.1var |  |  |
| 138 | Reactive P ValueL | Reactive PowerL | R/W |  | 0.1var |  |  |
| 139 | ReactiveOut putPriorityE nable | ReactiveOutput Priority Enable | R/W |  | 0/1 |  | 0：disable 1：enable |
| …… |  |  |  |  |  |  |  |
| 141 | SvgFunction Enable | Svg enable on night | R/W |  | 0/1 |  | 0：disable 1：enable |
| 142 | uwUnderFU ploadPoint | UnderF Upload Point | R/W |  | 0.01H Z |  |  |
| 143 | uwOFDerate RecoverPoin t | OFDerate RecoverPoint | R/W |  | 0.01H Z |  |  |
| 144 | uwOFDerate RecoverDela yTime | OFDerate RecoverDelayTime | R/W | 0-30000 | 50ms |  |  |
| 145 | ZeroCurrent Enable | ZeroCurrent Enable | R/W | 0-1 |  |  |  |
| 146 | uwZeroCurre ntStaticlowV olt | ZeroCurrent StaticlowVolt | R/W | 46-230V | 0.1V | 115V |  |
| 147 | uwZeroCurre ntStaticHigh Volt | ZeroCurrent StaticHighVolt | R/W | 230-276V | 0.1V | 276V |  |
| 148 | uwHVoltDer ateHighPoint | HVoltDerate HighPoint | R/W | 0-1000V | 0.1V |  |  |
| 149 | uwHVoltDer ateLowPoint | HVoltDerate LowPoint | R/W | 0-1000V | 0.1V |  |  |
| 150 | uwQVPower StableTime | QVPower Stable Time | R/W | 0-60S | 0.1S |  |  |
| 151 | uwUnderFU ploadStopPo int | UnderF Upload StopPoint | R/W |  | 0.01H Z |  |  |
| 152 | fUnderFreqP oint | Underfrequency load start point | R/W | 46.00-50. 00 | 0.01Hz | 49.80 | CEI |
| 153 | fUnderFreqE | Underfrequency down | R/W | 46.00-50. | 0.01Hz | 49.10 | CEI |

|  | ndPoint | load end point |  | 00 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 154 | fOverFreqPo int | Over frequency loading start point | R/W | 50.00-52. 00 | 0.01Hz | 50.20 | CEI |
| 155 | fOverFreqEn dPoint | Over frequency loading end point | R/W | 50.00-52. 00 | 0.01Hz | 51.50 | CEI |
| 156 | fUnderVoltP oint | Undervoltage load shedding start point | R/W | 160-300 | 0.1V | 220.0 | CEI |
| 157 | fUnderVoltE ndPoint | Undervoltage derating end point | R/W | 160-300 | 0.1V | 207.0 | CEI |
| 158 | fOverVoltPoi nt | Overvoltage loading start point | R/W | 160-300 | 0.1V | 230.0 | CEI |
| 159 | fOverVoltEn dPoint | Overvoltage loading end point | R/W | 160-300 | 0.1V | 245.0 | CEI |
| 160 | uwNominal GridVolt | NominalGridVolt Select | R/W | 0~3 |  |  | UL |
| 161 | uwGridWatt Delay | GridWatt DelayTime | R/W | 0~3000 | 20ms |  | UL |
| 162 | uwReconnec tStartSlope | Reconnect StartSlope | R/W | 1~1000 | 0.1 |  | UL |
| 163 | uwLFRTEE | LFRT1 Freq | R/W | 5500~650 0 | 0.01Hz |  | UL |
| 164 | uwLFRTTime EE | LFRT1 Time | R/W |  | 20ms |  | UL |
| 165 | uwLFRT2EE | LFRT2 Freq | R/W | 5500~650 0 | 0.01Hz |  | UL |
| 166 | uwLFRTTime 2EE | LFRT2 Time | R/W |  | 20ms |  | UL |
| 167 | uwHFRTEE | HFRT1 Freq | R/W | 5500~650 0 | 0.01Hz |  | UL |
| 168 | uwHFRTTim eEE | HFRT1 Time | R/W |  | 20ms |  | UL |
| 169 | uwHFRT2EE | HFRT2 Freq | R/W | 5500~650 0 | 0.01Hz |  | UL |
| 170 | uwHFRTTim e2EE | HFRT2 Time | R/W |  | 20ms |  | UL |
| 171 | uwHVRTEE | HVRT1 Volt | R/W |  | 0.001 Un |  | UL |
| 172 | uwHVRTTim eEE | HVRT1 Time | R/W |  | 20ms |  | UL |
| 173 | uwHVRT2EE | HVRT2 Volt | R/W |  | 0.001 Un |  | UL |
| 174 | uwHVRTTim | HVRT2 Time | R/W |  | 0.001 |  | UL |

|  | e2EE |  |  |  | Un |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 175 | uwUnderFU ploadDelayTi me | UnderF UploadDelayTime | R/W | 0-2s | 50ms | 0s | 50549 |
| 176 | uwUnderFU ploadRateEE | UnderF UploadRate | R/W |  |  |  | 50549 |
| 177 | uwGridResta rt_H_Freq | GridRestart HighFreq | R/W |  | 0.01Hz |  | 50549 |
| 178 | OverFDeratR esponseTim e | OverFDerat ResponseTime | W/R | 0-500 |  |  |  |
| 179 | UnderFUplo adResponse Time | UnderFUpload ResponseTime | W/R | 0-500 |  |  |  |
| Intelligent control reads relevant data, used to identify the logo 180-200 |  |  |  |  |  |  |  |
| 180 | MeterLink | Whether to elect the meter | R/W |  |  |  | 0: Missed, 1: Received |
| 181 | OPT Number | Number of connection optimizers | R/W | 0-64 |  |  | The total number of optimizers connected to the inverter |
| 182 | OPT ConfigOK Flag | Optimizer configuration completion flag | R/W |  |  |  | 0x00:Not configured success 0x01:Configuration is complete |
| 183 | PvStrScan | String Num | R/W | 0、8、16、 32 |  |  | 0：Not support Other：PvString Num |
| …… |  |  |  |  |  |  |  |
| 200 | Reserved |  |  |  |  |  | Reserved |
| 201 | PID Working Model | PID Operating mode | W | 0: automati c 1: continuo us 2: All night |  |  |  |
| 202 | PID On/Off Ctrl | PID Break control | W | 0:On 1:Off |  |  |  |
| 203 | PID Volt Option | PID Output voltage option | W | 300~1000 | V |  |  |

| …… |  |  |  |  |  |  | Reserved |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 209 | New Serial NO | Serial number 1-2 |  |  | ASCII |  |  |
| 210 | New Serial NO | Serial number 3-4 |  |  | ASCII |  |  |
| 211 | New Serial NO | Serial number 5-6 |  |  | ASCII |  |  |
| 212 | New Serial NO | Serial number 7-8 |  |  | ASCII |  |  |
| 213 | New Serial NO | Serial number 9-10 |  |  | ASCII |  |  |
| 214 | New Serial NO | Serial number 11-12 |  |  | ASCII |  |  |
| 215 | New Serial NO | Serial number 13-14 |  |  | ASCII |  |  |
| 216 | New Serial NO | Serial number 15-16 |  |  | ASCII |  |  |
| 217 | New Serial NO | Serial number 17-18 |  |  | ASCII |  |  |
| 218 | New Serial NO | Serial number 19-20 |  |  | ASCII |  |  |
| 219 | New Serial NO | Serial number 21-22 |  |  | ASCII |  |  |
| 220 | New Serial NO | Serial number 23-24 |  |  | ASCII |  |  |
| 221 | New Serial NO | Serial number 25-26 |  |  | ASCII |  |  |
| 222 | New Serial NO | Serial number 27-28 |  |  | ASCII |  |  |
| 223 | New Serial NO | Serial number 29-30 |  |  | ASCII |  |  |
| …… |  |  |  |  |  |  | Reserved |
| 229 | EnergyAdjus t | Power generation incremental calibration coefficient | W/R |  | 0.1% |  | 1-1000,(Percent ratio) |
| 230~249 for growatt debug setting |  |  |  |  |  |  |  |
| 230 | IslandDisabl e | Island Disable or not. 1:disable 0:Enable | W | 0,1 |  | 0 |  |
| 231 | FanCheck | Start Fan Check | W | 1 |  |  |  |
| 232 | EnableNLine | Enable N Line of grid | W | 1 |  | 0 |  |
| 233 | wCheckHard | wCheckHardware |  |  |  |  |  |

|  | ware | Bit0: GFCIBreak; Bit1:SPSDamage Bit8:EepromReadWarni ng Bit9:EEWriteWarning …… |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 234 | wCheckHard ware2 |  |  |  |  |  | reserved |
| 235 | ubNToGNDD etect | Dis/enable N to GND detect function | W | 1:enable 0:disable |  | 1 |  |
| 236 | NonStdVacE nable | Enable/Disable Nonstandard Grid voltage range | W | 0-2 |  | 0 | 0:Disable; 1:Enable Voltgrade1 2:Enable Voltgrade2 |
| 237 | uwEnableSp ecSet | Disablse/enable appointed spec setting | W | 1:enable 0:disable | Binary | 0x000 0 | Bit 0: Hungary |
| 238 | Fast MPPT enable | About Fast mppt |  | 0,1,2 |  | 0 | Reserved |
| 239 | / | / | / | / |  | / | Reserved |
| 240 | Check Step |  | W |  |  |  |  |
| 241 | INV-Lng | Inverter Longitude | W |  |  |  | Longitude |
| 242 | INV-Lat | Inverter Latitude | W |  |  |  | Latitude |
| …… |  |  |  |  |  |  | Reserved |
| 249 |  |  |  |  |  |  | Reserved |
| Six group for Storage Power |  |  |  |  |  |  |  |
| Register NO. | Variable Name | Description | Write or not | Value | Unit | Initial value | Note |
| 1000. | Float charge current limit | When charge current battery need is lower than this value, enter into float charge | W |  | 0.1A | 600 | CC current |
| 1001. | PF CMD memory state | Set the following 19-22 CMD will be memory ornot(1/0), if not, these settings are the initial value. | W | 0or1, |  | 0 | Means these settings will be acting or not when next power on(02 repeat) |
| 1002. | VbatStartF orDischarg e | LV Vbat | R/W |  | 0.1V |  | Lead-acid battery LV voltage |
| 1003. | VbatlowWa rnClr | LoadPercent(only lead-Acid): | W |  | 0.1V |  | Clear battery low voltage error voltage point |

|  |  | 45.5V <20% 48.0V 20%~50% 49.0V >50 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1004. | Vbatstopfo rdischarge | Should stop discharge when lower than this voltage(only lead-Acid): 46.0V <20% 44.8V 20%~50% 44.2V >50% | W |  | 0.01V |  |  |
| 1005. | Vbat stop for charge | Should stop charge when higher than this voltage | W |  | 0.01V | 5800 |  |
| 1006. | Vbat start for discharge | Should not discharge when lower than this voltage | W |  | 0.01V | 4800 |  |
| 1007. | Vbat constant charge | can charge when lower than this voltage | W |  | 0.01V | 5800 | CV voltage（acid） |
| 1008. | EESysInfo.S ysSetEn | Bit0：Resved; Bit1：Resved; Bit2：Resved; Bit3：Resved; Bit4：Resved; Bit5：bDischargeEn； Bit6：ForceDischrEn； Bit7：ChargeEn； Bit8：bForceChrEn； Bit9：bBackUpEn； Bit10：bInvLimitLoadE； Bit11：bSpLimitLoadEn； Bit12：bACChargeEn； Bit13：bPVLoadLimitEn; Bit14,15:UnUsed; | W |  |  |  | System Enable |
| 1009. | Battemp lower limit d | Battery temperature lower limit for discharge | W | 0-200:0-2 0℃ 1000-140 | 0.1℃ | 1170 |  |

|  |  |  |  | 0：-40-0℃ |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1010. | Bat temp upper limit d | Battery temperature upper limit for discharge | W | 200-1000 | 0.1℃ | 420 |  |
| 1011. | Bat temp lower limit c | Battery temperature lower limit for charge | W | 0-200:0-2 0℃ 1000-140 0：-40-0℃ | 0.1℃ | 30 | Lower temperature limit |
| 1012. | Bat temp upper limit c | Battery temperature upper limit for charge | W | 200-1000 | 0.1℃ | 370 | Upper temperature limit |
| 1013. | uwUnderFr eDischarge DelyTime | Under Fre Delay Time | s | 0-20 | 50ms |  | Under Fre Delay Time |
| 1014. | BatMdlSeri alNum | Battery serial number | W | 00:00 |  |  | SPH4-11K used |
| 1015. | BatMdlPara llNum | Battery parallel section | W | 00:00 |  |  | SPH4-11K used |
| 1016. | / | / | / | / | / | / | Reserve |
| 1017. | / | / | / | / | / | / | Reserve |
| 1018. | / | / | / | / | / | / | Reserve |
| 1019. | / | / | / | / | / | / | Reserve |
| 1020. | / | / | / | / | / | / | Reserve |
| 1021. | / | / | / | / | / | / | Reserve |
| 1022. | / | / | / | / | / | / | Reserve |
| 1023. | / | / | / | / | / | / | Reserve |
| 1024. | / | / | / | / | / | / | Reserve |
| 1025. | / | / | / | / | / | / | Reserve |

| 1026. | / | / | / | / | / | / | Reserve |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1027. | / | / | / | / | / | / | Reserve |
| 1028. | / | / | / | / | / | / | Reserve |
| 1029. | / | / | / | / | / | / | Reserve |
| 1030. | / | / | / | / | / | / | Reserve |
| 1031. | / | / | / | / | / | / | Reserve |
| 1032. | / | / | / | / | / | / | Reserve |
| 1033. | / | / | / | / | / | / | Reserve |
| 1034. | / | / | / | / | / | / | Reserve |
| 1035. | / | / | / | / | / | / | Reserve |
| 1036. | / | / | / | / | / | / | Reserve |
| 1037. | bCTMode | Use the CTMode to Choose RFCT \ Cable CT\METER | W | 2:METER 1:cWirele ssCT 0:cWiredC T |  | 0 |  |
| 1038. | CTAdjust | CTAdjust enable | W | 0:disable 1:enable |  | 0 |  |
| 1039. | / | / | / | / | / | / | Reserve |
| 1040. | / | / | / | / | / | / | Reserve |
| 1041. | / | / | / | / | / | / | Reserve |
| 1042. | / | / | / | / | / |  | Reserve |
| 1043. | / | / | / | / | / | / | Reserve |

| 1044. | Priority | ForceChrEn/ForceDischr En Load first/bat first /grid first |  | R |  | 0.Load(de fault)/1.B attery/2.G rid |  |  |  |  | bForceChrEn/disbForceDischrE n/dis |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1045. | / | / |  | / |  | / |  | / |  | / | Reserve |  |
| 1046. | / | / |  | / |  | / |  | / |  | / | Reserve |  |
| 1047. | AgingTestSt ep Cmd | Command for aging test |  |  |  | 0: default 1: charge 2: discharge |  |  |  |  | Cmd for aging test |  |
| 1048. | BatteryTyp e | Battery type choose of buck-boost input |  |  |  | 0:Lithium 1:Lead-aci d 2:other |  |  |  | 0 | Battery type |  |
| 1049. | / | / |  | / |  | / |  | / |  |  | Reserve |  |
| 1050. | / | / |  | / |  | / |  | / |  | / | Reserve |  |
| 1051. | / | / |  | / |  | / |  | / |  |  | Reserve |  |
| 1052. | / | / |  | / |  | / |  | / |  |  | Reserve |  |
| 1053. | / | / |  | / |  | / |  | / |  |  | Reserve |  |
| 1054. | / | / |  | / |  | / |  | / |  | / | Reserve |  |
| 1060. | BuckUpsFunE n |  | Ups function enable or disable |  |  |  | 0:disable 1:enable |  |  |  |  |  |
| 1061. | BuckUPSVoltS et |  | UPS output voltage |  |  |  | 0:230 1:208 2:240 |  |  |  | 230V |  |
| 1062. | UPSFreqSet |  | UPS output frequency |  |  |  | 0:50Hz 1:60Hz |  |  |  | 50Hz |  |
| ... | / |  | / |  | / |  | / |  | / |  | / | reverse |
| Priority set |  |  |  |  |  |  |  |  |  |  |  |  |

| 1070. | GridFirstDisch argePowerRat e | Discharge Power Rate when Grid First | W | 0-100 | 1% | Discharge Power Rate when Grid First |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1071. | GridFirstStopS OC | Stop Discharge soc when Grid First | W | 0-100 | 1% | Stop Discharge soc when Grid First |  |
| 1072… 1079 | / | / | / | / | / | / | reverse |
| 1080. | Grid First Start Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1081. | Grid First Stop Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1082. | Grid First Stop Switch 1 | Enable :1 Disable:0 |  | 0 or 1 |  | Grid First enable |  |
| 1083. | Grid First Start Time 2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1084. | Grid First Stop Time 2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1085. | Grid First Stop Switch 2 | ForceDischarge.bSwitch&L CD_SET_FORCE_TRUE_2)= =LCD_SET_FORCE_TRUE_2 |  | 0 or 1 |  | Grid First enable | ForceDischarge; LCD_SET_FORCE_T RUE_2 |
| 1086. | Grid First Start Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1087. | Grid First Stop Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1088. | Grid First Stop Switch 3 | Enable :1 Disable:0 |  | 0 or 1 |  | Grid First enable |  |
| 1089. | / | / | / | / | / | / | reserve |
| 1090. | BatFirstPower Rate | Charge Power Rate when Bat First | W | 0-100 | 1% | Charge Power Rate when Bat First |  |
| 1091. | wBatFirst stop SOC | Stop Charge soc when Bat First | W | 0-100 | 1% | Stop Charge soc when Bat First |  |

| 1092. | AC charge Switch | When Bat First Enable:1 Disable:0 |  | Enable:1 Disable:0 |  | AC Charge Enable |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1093… 1099 |  |  |  |  |  |  |  |
| 1100. | Bat First Start Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1101. | Bat First Stop Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1102. | BatFirst on/off Switch 1 | Enable :1 Disable:0 |  | 0 or 1 |  | Bat First Enable1 |  |
| 1103. | Bat First Start Time 2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1104. | Bat First Stop Time 2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1105. | BatFirston/off Switch 2 | Enable :1 Disable:0 |  | 0 or 1 |  | Bat First Enable2 |  |
| 1106. | Bat First Start Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1107. | Bat First Stop Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1108. | BatFirston/off Switch 3 | Enable :1 Disable:0 |  | 0 or 1 |  | Bat First Enable3 |  |
| 1109. | / | / | / | / | / | / | reserve |
| 1110. | Load First Start Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| 1111. | Load First Stop Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| 1112. | Load First Switch 1 | Enable :1 Disable:0 |  | 0 or 1 |  | Load First Enable | SPA/ reserve |
| 1113. | Load First Start Time2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| 1114. | Load First Stop Time 2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| 1115. | Load First Switch 2 | Enable :1 Disable:0 |  | 0 or 1 |  | Load First Enable | SPA/ reserve |

| 1116. | Load First Start Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1117. | Load First Stop Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| 1118. | Load First Switch 3 | Enable :1 Disable:0 |  | 0 or 1 |  | Load First Enable | SPA/ reserve |
| 1119. | / | / | / | / | / | / | reserve |
| 1120. | BackUpEn | BackUp Enable |  |  |  |  | MIX US |
| 1121. | SGIPEn | SGIP Enable |  |  |  |  | MIX US |
| ……… | 1122~1124 | / | / | / | / | / | reserve |
| Use for TL-X and TL-XH |  |  |  |  |  |  |  |
| 3000 | ExportLimitFa iledPowerRat e | The power rate when exportLimit failed | R/W |  | 0.1% |  | The power rate when exportLimit failed |
| 3001 | New Serial NO | Serial number 1-2 | R/W |  | ASCII |  | The new model uses the following registers to record the serial number; The representation is the same as the original: one register holds two characters and the new serial number is 30 characters. |
| 3002 | New Serial NO | Serial number 3-4 | R/W |  | ASCII |  |  |
| 3003 | New Serial NO | Serial number 5-6 | R/W |  | ASCII |  |  |
| 3004 | New Serial NO | Serial number 7-8 | R/W |  | ASCII |  |  |
| 3005 | New Serial NO | Serial number 9-10 | R/W |  | ASCII |  |  |
| 3006 | New Serial NO | Serial number 11-12 | R/W |  | ASCII |  |  |
| 3007 | New Serial NO | Serial number 13-14 | R/W |  | ASCII |  |  |
| 3008 | New Serial NO | Serial number 15-16 | R/W |  | ASCII |  |  |
| 3009 | New Serial NO | Serial number 17-18 | R/W |  | ASCII |  |  |
| 3010 | New Serial NO | Serial number 19-20 | R/W |  | ASCII |  |  |
| 3011 | New Serial NO | Serial number 21-22 | R/W |  | ASCII |  |  |

| 3012 | New Serial NO | Serial number 23-24 | R/W |  | ASCII |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3013 | New Serial NO | Serial number 25-26 | R/W |  | ASCII |  |  |
| 3014 | New Serial NO | Serial number 27-28 | R/W |  | ASCII |  |  |
| 3015 | New Serial NO | Serial number 29-30 | R/W |  | ASCII |  |  |
| 3016 | DryContactFu ncEn | DryContact function enable | R/W | 0:Disable 1: Enable |  |  | DryContact function enable |
| 3017 | DryContactOn Rate | The power rate of drycontact turn on | R/W | 0~1000 | 0.1% |  | The power rate of drycontact turn on |
| 3018 | Reserved |  |  |  |  |  |  |
| 3019 | DryContactOf fRate | DryContactOffRate | Dry contact closure power | R/W | 0~100 0 | 0.1% | Dry contact closure power pe rcentage |
| 3020 | BoxCtrlInvOrd er | BoxCtrlInvOrder | Off-net box control instruct ion | R/W |  |  |  |
| 3021 | ExterCommOf fGridEn | External communication setting manual off-network enable | R/W |  |  |  | 0x00: Disable; （default） 0x01: Enable; |
| 3022 | Reserved |  |  |  |  |  |  |
| 3023 | Reserved |  |  |  |  |  |  |
| 3024 | Float charge current limit | When charge current battery need is lower than this value, enter into float charge | R/W |  | 0.1A | 600 | CC current |
| 3025 | VbatWarning | "Battery-low" warning setup voltage | R/W |  | 0.1V | 4800 | Lead acid battery LV voltage |
| 3026 | VbatlowWarn Clr | "Battery-low" warning clear voltage | R/W |  | 0.1V |  | Clear battery low voltage error voltage point LoadPercent(only lead-Acid): |

|  |  |  |  |  |  |  | 45.5V(Load < 20%); 48.0V(20%<=Load <=50%); 49.0V(Load > 50%); |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3027 | Vbatstopfordi scharge | Battery cut off voltage | R/W |  | 0.1V |  | Should stop discharge when lower than this voltage(only lead-Acid): 46.0V(Load < 20%); 44.8V(20%<=Load <=50%); 44.2V(Load > 50%); |
| 3028 | Vbat stop for charge | Battery over charge voltage | R/W |  | 0.01V | 5800 | Should stop charge when higher than this voltage |
| 3029 | Vbat start for discharge | Battery start discharge voltage | R/W |  | 0.01V | 4800 | Should not discharge when lower than this voltage |
| 3030 | Vbat constant charge | Battery constant charge voltage | R/W |  | 0.01V | 5800 | CV voltage（acid） can charge when lower than this voltage |
| 3031 | Battemp lower limit d | Battery temperature lower limit for discharge | R/W |  | 0.1℃ | 1170 | 0-200:0-20℃ 1000-1400： -40-0℃ |
| 3032 | Bat temp upper limit d | Battery temperature upper limit for discharge | R/W |  | 0.1℃ | 420 |  |
| 3033 | Bat temp lower limit c | Battery temperature lower limit for charge | R/W |  | 0.1℃ | 30 | Battery temperature lower limit 0-200:0-20℃ 1000-1400： -40-0℃ |

| 3034 | Bat temp upper limit c | Battery temperature upper limit for charge | R/W |  | 0.1℃ | 370 | Battery temperature upper limit |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3035 | uwUnderFreD ischargeDelyT ime | Under Fre Delay Time | R/W |  | 50ms |  | Under Fre Delay Time |
| 3036 | GridFirstDisch argePowerRat e | Discharge Power Rate when Grid First |  |  |  | 1-255 |  |
| 3037 | GridFirstStopS OC | Stop Discharge soc when Grid First |  |  |  | 1-100 |  |
| 3038 | Time 1(xh) | Period 1: [Start Time ~ End Time], [Charge/Discharge], [Disable/Enable] 3038 enable, charge and discharge, start time, end time 3039 | R/W |  |  |  | Bit0~7: minutes; Bit8~12: hour; Bit13~14, 0: load priority; 1: battery priority; 2: Grid priority; Bit15, 0: prohibited; 1: enabled; |
| 3039 |  |  | R/W |  |  |  | Bit0~7: minutes; Bit8~12: hour; Bit13~15: reserved |
| 3040 | Time 2(xh) | Time period 2: [start time ~ end time], [charge / discharge], [disable / enable] 3040 enable, charge and discharge, start time, 3041 end time | R/W |  |  |  | Bit0~7: minutes; Bit8~12: hour; Bit13~14, 0: load priority; 1: battery priority; 2: Grid priority; Bit15, 0: prohibited; 1: enabled; |
| 3041 |  |  | R/W |  |  |  | Bit0~7: minutes; Bit8~12: hour; Bit13~15: reserved |
| 3042 | Time 3(xh) | With Time1 | R/W |  |  |  | With Time1 |
| 3043 |  |  | R/W |  |  |  | With Time1 |
| 3044 | Time 4(xh) | With Time1 | R/W |  |  |  | With Time1 |
| 3045 |  |  | R/W |  |  |  | With Time1 |
| 3046 | Grid First Stop Switch 3 | Grid first time-3 enable |  |  |  |  | Enable :1 Disable:0 |

| 3047 | BatFirstPower Rate | Charge Power Rate when Bat First |  |  |  | 1-100 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3048 | wBatFirst stop SOC | Stop Charge soc when Bat First |  |  |  | 1-100 |  |
| 3049 | AcChargeEna ble | AcChargeEnable |  |  |  |  | Enable :1 Disable:0 |
| 3050 | Time 5(xh) | 同 Time1 | R/W |  |  |  | With Time1 |
| 3051 |  |  | R/W |  |  |  | With Time1 |
| 3052 | Time 6(xh) | 同 Time1 | R/W |  |  |  | With Time1 |
| 3053 |  |  | R/W |  |  |  | With Time1 |
| 3054 | Time 7(xh) | 同 Time1 | R/W |  |  |  | With Time1 |
| 3055 |  |  | R/W |  |  |  | With Time1 |
| 3056 | Time 8(xh) | 同 Time1 | R/W |  |  |  | With Time1 |
| 3057 |  |  | R/W |  |  |  | With Time1 |
| 3058 | Time 9(xh) | 同 Time1 | R/W |  |  |  | With Time1 |
| 3059 |  |  | R/W |  |  |  | With Time1 |
| 3060~ 3069 | Reserved |  |  |  |  |  |  |
| 3070 | BatteryType | Battery type choose of buck-boost input | R/W |  |  |  | Battery type 0:Lithium 1:Lead-acid 2:other |
| 3071 | BatMdlSeria/ ParalNum | BatMdlSeria/ParalNum | R/W |  |  |  | BatMdlSeria/Paral Num; SPH4-11K used The upper 8 bits indicate the number of series segments； The lower 8 bits |

|  |  |  |  |  |  |  | indicate the number of parallel sections; |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3072 | Reserved |  |  |  |  |  |  |
| 3073 | Reserved |  |  |  |  |  |  |
| 3074 | Reserved |  |  |  |  |  |  |
| 3075 | Reserved |  |  |  |  |  |  |
| 3076 | Reserved |  |  |  |  |  |  |
| 3077 | Reserved |  |  |  |  |  |  |
| 3078 | Reserved |  |  |  |  |  |  |
| 3079 | UpsFunEn | Ups function enable or disable | R/W |  |  | 0 | 0:disable 1:enable |
| 3080 | UPSVoltSet | UPS output voltage | R/W |  |  | 0 | 0:230V 1:208V 2:240V |
| 3081 | UPSFreqSet | UPS output frequency | R/W |  |  | 0 | 0:50Hz 1:60Hz |
| 3082 | bLoadFirstSto pSocSet | StopSoc When LoadFirst | R/W |  |  | 13-100 | ratio |
| 3083 | Reserved |  |  |  |  |  |  |
| 3084 | Reserved |  |  |  |  |  |  |
| 3085 | Com Address | Communication addr | R/W |  |  | 1 | 1 : Communication addr=1 1 ~ 254 : Communication addr=1~254 |
| 3086 | BaudRate | Communication BaudRate | R/W |  |  | 0 | 0: 9600 bps 1: 38400 bps |
| 3087 | Serial NO | Serial Number 1-2 | R/W |  | ASCII |  | For battery |
| 3088 | Serial No | Serial Number 3-4 | R/W |  | ASCII |  |  |
| 3089 | Serial No | Serial Number 5-6 | R/W |  | ASCII |  |  |
| 3090 | Serial No | Serial Number 7-8 | R/W |  | ASCII |  |  |
| 3091 | Serial No | Serial Number 9-10 | R/W |  | ASCII |  |  |
| 3092 | Model H | Model H | R/W |  |  |  |  |
| 3093 | Model L | Model L | R/W |  |  |  |  |
| 3094 | Pdischr max H | Max Discharge Power | R |  | 0.1W |  |  |
| 3095 | Pdischr max L |  |  |  |  |  |  |
| 3096 | Pchr max H | Max Charge Power | R |  | 0.1W |  |  |
| 3097 | Pchr max L |  |  |  |  |  |  |
| 3098 | DTC | DTC | R |  |  |  |  |
| 3099 | FW Code1 | FW Code1 | R |  | ASCII |  |  |
| 3100 | FW Code2 | FW Code2 | R |  | ASCII |  |  |
| 3101 | Processor1 FW Vision | Processor1 FW Vision | R |  | ASCII |  |  |
| 3102 | Reset User Info | Reset User Info | W |  |  |  |  |
| 3103 | Reset to factory | Reset to factory | W |  |  |  |  |
| 3104 ~ 3124 | Reserved |  |  |  |  |  |  |

## Input Reg

| NO. | Variable Name |  | Description | Value | Unit | Note |
| --- | --- | --- | --- | --- | --- | --- |
| First group |  |  |  |  |  |  |
| 0. |  | Inverter Status | Inverter run state | 0:waiting, 1:normal, 3:fault |  |  |
| 1. |  | Ppv H | Input power (high) |  | 0.1W |  |
| 2. |  | Ppv L | Input power (low) |  | 0.1W |  |
| 3. |  | Vpv1 | PV1 voltage |  | 0.1V |  |
| 4. |  | PV1Curr | PV1 input current |  | 0.1A |  |
| 5. |  | Ppv1 H | PV1 input power(high) |  | 0.1W |  |
| 6. |  | Ppv1 L | PV1 input power(low) |  | 0.1W |  |
| 7. |  | Vpv2 | PV2 voltage |  | 0.1V |  |
| 8. |  | PV2Curr | PV2 input current |  | 0.1A |  |
| 9. |  | Ppv2 H | PV2 input power (high) |  | 0.1W |  |
| 10. |  | Ppv2 L | PV2 input power (low) |  | 0.1W |  |
| 11. |  | Vpv3 | PV3 voltage |  | 0.1V |  |
| 12. |  | PV3Curr | PV3 input current |  | 0.1A |  |
| 13. |  | Ppv3 H | PV3 input power (high) |  | 0.1W |  |
| 14. |  | Ppv3 L | PV3 input power (low) |  | 0.1W |  |
| 15. |  | Vpv4 | PV4 voltage |  | 0.1V |  |
| 16. |  | PV4Curr | PV4 input current |  | 0.1A |  |
| 17. |  | Ppv4 H | PV4 input power (high) |  | 0.1W |  |
| 18. |  | Ppv4 L | PV4 input power (low) |  | 0.1W |  |
| 19. |  | Vpv5 | PV5 voltage |  | 0.1V |  |
| 20. |  | PV5Curr | PV5 input current |  | 0.1A |  |
| 21. |  | Ppv5H | PV5 input power(high) |  | 0.1W |  |

| 22. | Ppv5 L | PV5 input power(low) |  | 0.1W |  |
| --- | --- | --- | --- | --- | --- |
| 23. | Vpv6 | PV6 voltage |  | 0.1V |  |
| 24. | PV6Curr | PV6 input current |  | 0.1A |  |
| 25. | Ppv6 H | PV6 input power (high) |  | 0.1W |  |
| 26. | Ppv6 L | PV6 input power (low) |  | 0.1W |  |
| 27. | Vpv7 | PV7 voltage |  | 0.1V |  |
| 28. | PV7Curr | PV7 input current |  | 0.1A |  |
| 29. | Ppv7 H | PV7 input power (high) |  | 0.1W |  |
| 30. | Ppv7 L | PV7 input power (low) |  | 0.1W |  |
| 31. | Vpv8 | PV8 voltage |  | 0.1V |  |
| 32. | PV8Curr | PV8 input current |  | 0.1A |  |
| 33. | Ppv8 H | PV8 input power (high) |  | 0.1W |  |
| 34. | Ppv8 L | PV8 input power (low) |  | 0.1W |  |
| 35. | Pac H | Output power (high) |  | 0.1W |  |
| 36. | Pac L | Output power (low) |  | 0.1W |  |
| 37. | Fac | Grid frequency |  | 0.01Hz |  |
| 38. | Vac1 | Three/single phase grid voltage |  | 0.1V |  |
| 39. | Iac1 | Three/single phase grid output current |  | 0.1A |  |
| 40. | Pac1 H | Three/single phase grid output watt VA (high) |  | 0.1VA |  |
| 41. | Pac1 L | Three/single phase grid output watt VA(low) |  | 0.1VA |  |
| 42. | Vac2 | Three phase grid voltage |  | 0.1V |  |
| 43. | Iac2 | Three phase grid output current |  | 0.1A |  |
| 44. | Pac2 H | Three phase grid output power (high) |  | 0.1VA |  |
| 45. | Pac2 L | Three phase grid output power (low) |  | 0.1VA |  |
| 46. | Vac3 | Three phase grid voltage |  | 0.1V |  |
| 47. | Iac3 | Three phase grid output current |  | 0.1A |  |
| 48. | Pac3 H | Three phase grid output power (high) |  | 0.1VA |  |
| 49. | Pac3 L | Three phase grid output power (low) |  | 0.1VA |  |
| 50. | Vac_RS | Three phase grid voltage |  | 0.1V | Line voltage |
| 51. | Vac_ST | Three phase grid voltage |  | 0.1V | Line voltage |
| 52. | Vac_TR | Three phase grid voltage |  | 0.1V | Line voltage |
| 53. | Eactoday H | Today generate energy (high) |  | 0.1kWH |  |
| 54. | Eac today L | Today generate energy (low) |  | 0.1kWH |  |
| 55. | Eac total H | Total generate energy (high) |  | 0.1kWH |  |
| 56. | Eac total L | Total generate energy (low) |  | 0.1kWH |  |
| 57. | Time total H | Work time total (high) |  | 0.5s |  |
| 58. | Time total L | Work time total (low) |  | 0.5s |  |
| 59. | Epv1_today H | PV1Energy today(high) |  | 0.1kWh |  |
| 60. | Epv1_today L | PV1Energy today (low) |  | 0.1kWh |  |

| 61. | Epv1_total H | PV1Energy total(high) |  | 0.1kWh |  |
| --- | --- | --- | --- | --- | --- |
| 62. | Epv1_total L | PV1Energy total (low) |  | 0.1kWh |  |
| 63. | Epv2_today H | PV2Energy today(high) |  | 0.1kWh |  |
| 64. | Epv2_today L | PV2Energy today (low) |  | 0.1kWh |  |
| 65. | Epv2_total H | PV2Energy total(high) |  | 0.1kWh |  |
| 66. | Epv2_total L | PV2Energy total (low) |  | 0.1kWh |  |
| 67. | Epv3_today H | PV3 Energy today(high) |  | 0.1kWh |  |
| 68. | Epv3_today L | PV3 Energy today (low) |  | 0.1kWh |  |
| 69. | Epv3_total H | PV3 Energy total(high) |  | 0.1kWh |  |
| 70. | Epv3_total L | PV3 Energy total (low) |  | 0.1kWh |  |
| 71. | Epv4_today H | PV4Energy today(high) |  | 0.1kWh |  |
| 72. | Epv4_today L | PV4Energy today (low) |  | 0.1kWh |  |
| 73. | Epv4_total H | PV4Energy total(high) |  | 0.1kWh |  |
| 74. | Epv4_total L | PV4Energy total (low) |  | 0.1kWh |  |
| 75. | Epv5_today H | PV5Energy today(high) |  | 0.1kWh |  |
| 76. | Epv5_today L | PV5Energy today (low) |  | 0.1kWh |  |
| 77. | Epv5_total H | PV5Energy total(high) |  | 0.1kWh |  |
| 78. | Epv5_total L | PV5Energy total (low) |  | 0.1kWh |  |
| 79. | Epv6_today H | PV6Energy today(high) |  | 0.1kWh |  |
| 80. | Epv6_today L | PV6Energy today (low) |  | 0.1kWh |  |
| 81. | Epv6_total H | PV6Energy total(high) |  | 0.1kWh |  |
| 82. | Epv6_total L | PV6Energy total (low) |  | 0.1kWh |  |
| 83. | Epv7_today H | PV7Energy today(high) |  | 0.1kWh |  |
| 84. | Epv7_today L | PV7Energy today (low) |  | 0.1kWh |  |
| 85. | Epv7_total H | PV7 Energy total(high) |  | 0.1kWh |  |
| 86. | Epv7_total L | PV7Energy total (low) |  | 0.1kWh |  |
| 87. | Epv8_today H | PV8Energy today(high) |  | 0.1kWh |  |
| 88. | Epv8_today L | PV8Energy today (low) |  | 0.1kWh |  |
| 89. | Epv8_total H | PV8Energy total(high) |  | 0.1kWh |  |
| 90. | Epv8_total L | PV8Energy total (low) |  | 0.1kWh |  |
| 91. | Epv_total H | PV Energy total(high) |  | 0.1kWh |  |
| 92. | Epv_total L | PV Energy total (low) |  | 0.1kWh |  |
| 93. | Temp1 | Inverter temperature |  | 0.1C |  |
| 94. | Temp2 | The inside IPM in inverter Temperature |  | 0.1C |  |
| 95. | Temp3 | Boost temperature |  | 0.1C |  |
| 96. | Temp4 |  |  |  | reserved |
| 97. | uwBatVolt_DSP | BatVolt_DSP |  | 0.1V | BatVolt(DSP) |
| 98. | P Bus Voltage | P Bus inside Voltage |  | 0.1V |  |
| 99. | N Bus Voltage | N Bus inside Voltage |  | 0.1V |  |

| 100. | IPF | Inverter output PF now | 0-20000 |  |  |
| --- | --- | --- | --- | --- | --- |
| 101. | RealOPPercent | Real Output power Percent |  | 1% |  |
| 102. | OPFullwatt H | Output Maxpower Limited high |  |  |  |
| 103. | OPFullwatt L | Output Maxpower Limited low |  | 0.1W |  |
| 104. | DeratingMode | DeratingMode | 0:no derate; 1:PV; 2:*; 3:Vac; 4:Fac; 5:Tboost; 6:Tinv; 7:Control; 8:*; 9:*OverBack ByTime; |  |  |
| 105. | Fault code | Inverter fault code | &*1 |  | MAX |
| 106. | Fault Bitcode H | Inverter fault code high | &*8 |  | MAX |
| 107. | Fault Bitcode L | Inverter fault code low |  |  |  |
| 108. | RemoteCtrlEn | / | 0.Load First 1.BatFirst 2.Grid | / | StoragePow er (SPA) |
| 109. | RemoteCtrlPow er | / |  | / | StoragePow er (SPA) |
| 110. | Warning bit H | Warning bit H | &*8 |  |  |
| 111. | Warning bit L | Warning bit L |  |  |  |
| 112. | bINVWarnCode | bINVWarnCode |  |  | MAX |
|  | EACharge_Today _H | ACCharge energy today |  | 0.1kwh | Storage Power |
| 113. | real Power Percent | real Power Percent | 0-100 | % | MAX |
|  | EACharge_Today _L | ACCharge energy today |  | 0.1kwh | Storage Power |
| 114. | inv start delay time | inv start delay time |  |  | MAX |
|  | EACharge_Total _H | ACCharge energy total |  | 0.1kwh | Storage Power |
| 115. | bINVAllFaultCod e | bINVAllFaultCode |  |  | MAX |
|  | EACharge_Total _L | ACCharge energy total |  | 0.1kwh | Storage Power |
| 116. | AC charge Power_H | Grid power to local load |  | 0.1kwh | Storage Power |

| 117. | AC charge Power_L | Grid power to local load |  |  | 0.1kwh | Storage Power |
| --- | --- | --- | --- | --- | --- | --- |
| 118. | Priority | 0:Load First 1:Battery First 2:Grid First |  |  |  | Storage Power |
| 119. | Battery Type | 0：Lead-acid 1：Lithium battery |  |  |  | Storage Power |
| 120. | AutoProofreadC MD | Aging mode 自动校准命令 |  |  |  | Storage Power |
| … | reserved |  |  |  |  | reserved |
| 124. | reserved |  |  |  |  | reserved |
| Second group |  |  |  |  |  |  |
| 125. | PID PV1+ Voltage |  | PID PV1PE Volt | 0~1000V | 0.1V |  |
| 126. | PID PV1+ Current |  | PID PV1PE Curr | -10~10mA | 0.1mA |  |
| 127. | PID PV2+ Voltage |  | PID PV2PE Volt | 0~1000V | 0.1V |  |
| 128. | PID PV2+ Current |  | PID PV2PE Curr | -10~10mA | 0.1mA |  |
| 129. | PID PV3+ Voltage |  | PID PV3PE Volt | 0~1000V | 0.1V |  |
| 130. | PID PV3+ Current |  | PID PV3PE Curr | -10~10mA | 0.1mA |  |
| 131. | PID PV4+ Voltage |  | PID PV4PE Volt | 0~1000V | 0.1V |  |
| 132. | PID PV4+ Current |  | PID PV4PE Curr | -10~10mA | 0.1mA |  |
| 133. | PID PV5+ Voltage |  | PID PV5PE Volt | 0~1000V | 0.1V |  |
| 134. | PID PV5+ Current |  | PID PV5PE Curr | -10~10mA | 0.1mA |  |
| 135. | PID PV6+ Voltage |  | PID PV6PE Volt | 0~1000V | 0.1V |  |
| 136. | PID PV6+ Current |  | PID PV6PE Curr | -10~10mA | 0.1mA |  |
| 137. | PID PV7+ Voltage |  | PID PV7PE Volt | 0~1000V | 0.1V |  |
| 138. | PID PV7+ Current |  | PID PV7PE Curr | -10~10mA | 0.1mA |  |
| 139. | PID PV8+ Voltage |  | PID PV8PE Volt | 0~1000V | 0.1V |  |
| 140. | PID PV8+ Current |  | PID PV8PE Curr | -10~10mA | 0.1mA |  |
| 141. | PID Status |  | Bit0~7:PID Working Status 1:Wait Status 2:Normal Status 3:Fault Status Bit8~15:Reversed | 0~3 |  |  |
| 142. | V _String1 |  | PV String1 voltage |  | 0.1V |  |
| 143. | Curr _String1 |  | PV String1 current | -15~15A | 0.1A |  |
| 144. | V _String2 |  | PV String2 voltage |  | 0.1V |  |
| 145. | Curr _String2 |  | PV String2 current | -15~15A | 0.1A |  |
| 146. | V _String3 |  | PV String3 voltage |  | 0.1V |  |
| 147. | Curr _String3 |  | PV String3 current | -15~15A | 0.1A |  |
| 148. | V _String4 |  | PV String4 voltage |  | 0.1V |  |

| 149. | Curr _String4 | PV String4 current | -15~15A | 0.1A |  |
| --- | --- | --- | --- | --- | --- |
| 150. | V _String5 | PV String5 voltage |  | 0.1V |  |
| 151. | Curr _String5 | PV String5 current | -15~15A | 0.1A |  |
| 152. | V _String6 | PV String6 voltage |  | 0.1V |  |
| 153. | Curr _String6 | PV String6 current | -15~15A | 0.1A |  |
| 154. | V _String7 | PV String7 voltage |  | 0.1V |  |
| 155. | Curr _String7 | PV String7 current | -15~15A | 0.1A |  |
| 156. | V _String8 | PV String8 voltage |  | 0.1V |  |
| 157. | Curr _String8 | PV String8 current | -15A~15A | 0.1A |  |
| 158. | V _String9 | PV String9 voltage |  | 0.1V |  |
| 159. | Curr _String9 | PV String9 current | -15A~15A | 0.1A |  |
| 160. | V _String10 | PV String10 voltage |  | 0.1V |  |
| 161. | Curr _String10 | PV String10 current | -15~15A | 0.1A |  |
| 162. | V _String11 | PV String11 voltage |  | 0.1V |  |
| 163. | Curr _String11 | PV String11 current | -15~15A | 0.1A |  |
| 164. | V _String12 | PV String12 voltage |  | 0.1V |  |
| 165. | Curr _String12 | PV String12 current | -15~15A | 0.1A |  |
| 166. | V _String13 | PV String13 voltage |  | 0.1V |  |
| 167. | Curr _String13 | PV String13 current | -15A~15A | 0.1A |  |
| 168. | V _String14 | PV String14 voltage |  | 0.1V |  |
| 169. | Curr _String14 | PV String14 current | -15~15A | 0.1A |  |
| 170. | V _String15 | PV String15 voltage |  | 0.1V |  |
| 171. | Curr _String15 | PV String15 current | -15~15A | 0.1A |  |
| 172. | V _String16 | PV String16 voltage |  | 0.1V |  |
| 173. | Curr _String16 | PV String16 current | -15~15A | 0.1A |  |
| 174. | StrUnmatch | Bit0~15: String1~16 unmatch |  |  | suggestive |
| 175. | StrCurrentUnblan ce | Bit0~15: String1~16 current unblance |  |  | suggestive |
| 176. | StrDisconnect | Bit0~15: String1~16 disconnect |  |  | suggestive |
| 177. | PIDFaultCode | Bit0:Output over voltage Bit1: ISO fault Bit2: BUS voltage abnormal Bit3~15:reserved |  |  |  |
| 178. | String Prompt | String Prompt Bit0:String Unmatch Bit1:StrDisconnect Bit2:StrCurrentUnblance Bit3~15:reserved |  |  |  |
| 179 | PV Warning Value | PV Warning Value |  |  |  |
| 180 | DSP075 Warning Value | DSP075 Warning Value |  |  |  |

| 181 | DSP075 Value | Fault | DSP075 Fault Value |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 182 | DSP067 Data1 | Debug | DSP067 Debug Data1 |  |  |  |
| 183 | DSP067 Data2 | Debug | DSP067 Debug Data2 |  |  |  |
| 184 | DSP067 Data3 | Debug | DSP067 Debug Data3 |  |  |  |
| 185 | DSP067 Data4 | Debug | DSP067 Debug Data4 |  |  |  |
| 186 | DSP067 Data5 | Debug | DSP067 Debug Data5 |  |  |  |
| 187 | DSP067 Data6 | Debug | DSP067 Debug Data6 |  |  |  |
| 188 | DSP067 Data7 | Debug | DSP067 Debug Data7 |  |  |  |
| 189 | DSP067 Data8 | Debug | DSP067 Debug Data8 |  |  |  |
| 190 | DSP075 Data1 | Debug | DSP075 Debug Data1 |  |  |  |
| 191 | DSP075 Data2 | Debug | DSP075 Debug Data2 |  |  |  |
| 192 | DSP075 Data3 | Debug | DSP075 Debug Data3 |  |  |  |
| 193 | DSP075 Data4 | Debug | DSP075 Debug Data4 |  |  |  |
| 194 | DSP075 Data55 | Debug | DSP075 Debug Data5 |  |  |  |
| 195 | DSP075 Data6 | Debug | DSP075 Debug Data6 |  |  |  |
| 196 | DSP075 Data7 | Debug | DSP075 Debug Data7 |  |  |  |
| 197 | DSP075 Data8 | Debug | DSP075 Debug Data8 |  |  |  |
| 198 | bUSBAgingTestOk Flag |  | USBAgingTestOkFlag | 0-1 |  |  |
| 199 | bFlashEraseAging OkFlag |  | FlashEraseAgingOkFlag | 0-1 |  |  |
| 200 | PVISO |  | PVISOValue |  | KΩ |  |
| 201 | R_DCI |  | R DCI Curr |  | 0.1mA |  |
| 202 | S_DCI |  | S DCI Curr |  | 0.1mA |  |
| 203 | T_DCI |  | T DCI Curr |  | 0.1mA |  |

| 204 | PID_Bus | PIDBusVolt |  | 0.1V |  |
| --- | --- | --- | --- | --- | --- |
| 205 | GFCI | GFCI Curr |  | mA |  |
| 206 | SVG/APF Status+SVGAPFEq ualRatio | SVG/APF Status+SVGAPFEqualRatio | High 8 bit： SVGAPFEqua lRatio Low 8 bit： SVG/APF Status 0:None 1:SVG Run 2:APF Run 3:SVG/APF Run |  |  |
| 207 | CT_I _R | R phase load side current for SVG |  | 0.1A |  |
| 208 | CT_I _S | S phase load side current for SVG |  | 0.1A |  |
| 209 | CT_I _T | T phase load side current for SVG |  | 0.1A |  |
| 210 | CT_Q _R H | R phase load side output reactive power for SVG(High) |  | 0.1Var |  |
| 211 | CT_Q _R L | R phase load side output reactive power for SVG(low) |  | 0.1Var |  |
| 212 | CT_Q _S H | S phase load side output reactive power for SVG(High) |  | 0.1Var |  |
| 213 | CT_Q _S L | S phase load side output reactive power for SVG(low) |  | 0.1Var |  |
| 214 | CT_Q _T H | T phase load side output reactive power for SVG(High) |  | 0.1Var |  |
| 215 | CT_Q _T L | T phase load side output reactive power for SVG(low) |  | 0.1Var |  |
| 216 | CT HAR_I_R | R phase load side harmonic |  | 0.1A |  |
| 217 | CT HAR_I_S | S phase load side harmonic |  | 0.1A |  |
| 218 | CT HAR_I_T | T phase load side harmonic |  | 0.1A |  |
| 219 | COMP_Q _R H | R phase compensate reactive power for SVG(High) |  | 0.1Var |  |
| 220 | COMP_Q _R L | R phase compensate reactive power for SVG(low) |  | 0.1Var |  |
| 221 | COMP_Q _S H | S phase compensate reactive power for SVG(High) |  | 0.1Var |  |
| 222 | COMP_Q _S L | S phase compensate reactive power for SVG(low) |  | 0.1Var |  |
| 223 | COMP_Q _T H | T phase compensate reactive power for SVG(High) |  | 0.1Var |  |
| 224 | COMP_Q _T L | T phase compensate reactive power |  | 0.1Var |  |

|  |  | for SVG(low) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 225 | COMP HAR_I_R | R phase compensate harmonic for SVG |  |  |  |  | 0.1A |  |  |
| 226 | COMP HAR_I_S | S phase compensate harmonic for SVG |  |  |  |  | 0.1A |  |  |
| 227 | COMP HAR_I_T | T phase compensate harmonic for SVG |  |  |  |  | 0.1A |  |  |
| 228 | bRS232AgingTest OkFlag | RS232AgingTestOkFlag |  |  | 0-1 |  |  |  |  |
| 229 | bFanFaultBit | Bit0: Fan 1 fault bit Bit1: Fan 2 fault bit Bit2: Fan 3 fault bit Bit3: Fan 4 fault bit Bit4-7: Reserved |  |  |  |  |  |  |  |
| 230 | Sac H | Output apparent power H |  |  |  |  | 0.1W |  |  |
| 231 | Sac L | Output apparent power L |  |  |  |  | 0.1W |  |  |
| 232 | ReActPowerH | Real Output Reactive Power H |  |  | Int32 |  | 0.1W |  |  |
| 233 | ReActPowerL | Real Output Reactive Power L |  |  |  |  |  |  |  |
| 234 | ReActPowerMaxH | Nominal Output Reactive Power H |  |  |  |  | 0.1var |  |  |
| 235 | ReActPowerMaxL | Nominal Output Reactive Power L |  |  |  |  |  |  |  |
| 236 | ReActPower_Total H | Reactive power generation |  |  |  |  | 0.1kwh |  |  |
| 237 | ReActPower_Total L | Reactive power generation |  |  |  |  |  |  |  |
| … | 238~249 |  |  |  |  |  |  |  | reserved |
| Ninth group for Storage power |  |  |  |  |  |  |  |  |  |
| 1000. | uwSysWorkMode |  | System work mode | 0x00:waiting module 0x01: Self-test mode, optional 0x02 : Reserved 0x03：SysFault module 0x04: Flash module 0x05 ： PVBATOnline module, 0x06 ： BatOnline |  |  |  | Theworkingmode displayed by the monitoring to the customer is： 0x00: waiting module 0x01: Self-test mode, 0x03:fault module 0x04:flash module 0x05¦0x06¦0x07¦0 x08:normal module |  |

|  |  |  | module, 0x07 ： PVOfflineMod e module, 0x08 ： BatOfflineMo de module, |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1001. | Systemfault word0 | System fault word0 |  |  | Please refer to thefault description Hybrid | of |
| 1002. | Systemfault word1 | System fault word1 |  |  |  |  |
| 1003. | Systemfault word2 | System fault word2 |  |  |  |  |
| 1004. | Systemfault word3 | System fault word3 |  |  |  |  |
| 1005. | Systemfault word4 | System fault word4 |  |  |  |  |
| 1006. | Systemfault word5 | System fault word5 |  |  |  |  |
| 1007. | Systemfault word6 | System fault word6 |  |  |  |  |
| 1008. | Systemfault word7 | System fault word7 |  |  |  |  |
| 1009. | Pdischarge1 H | Discharge power(high) |  | 0.1W |  |  |
| 1010. | Pdischarge1 L | Discharge power (low) |  | 0.1W |  |  |
| 1011. | Pcharge1 H | Charge power(high) |  | 0.1W |  |  |
| 1012. | Pcharge1 L | Charge power (low) |  | 0.1W |  |  |
| 1013. | Vbat | Battery voltage |  | 0.1V |  |  |
| 1014. | SOC | State of charge Capacity | 0-100 | 1% | lith/leadacid |  |
| 1015. | Pactouser R H | AC power to user H |  | 0.1w |  |  |
| 1016. | Pactouser R L | AC power to user L |  | 0.1w |  |  |
| 1017. | Pactouser S H | Pactouser S H |  | 0.1w |  |  |
| 1018. | Pactouser S L | Pactouser S L |  | 0.1w |  |  |
| 1019. | Pactouser T H | Pactouser T H |  | 0.1w |  |  |
| 1020. | Pactouser T L | Pactouser T H |  | 0.1w |  |  |
| 1021. | PactouserTotal H | AC power to user total H |  | 0.1w |  |  |
| 1022. | PactouserTotal L | AC power to user total L |  | 0.1w |  |  |
| 1023. | Pac to grid R H | AC power to grid H |  | 0.1w | Ac output |  |
| 1024. | Pac to grid R L | AC power to grid L |  | 0.1w |  |  |
| 1025. | Pactogrid S H |  |  | 0.1w |  |  |
| 1026. | Pactogrid S L |  |  | 0.1w |  |  |
| 1027. | Pactogrid T H |  |  | 0.1w |  |  |
| 1028. | Pactogrid T L |  |  | 0.1w |  |  |
| 1029. | Pactogrid total H | AC power to grid total H |  | 0.1w |  |  |
| 1030. | Pactogrid total L | AC power to grid total L |  | 0.1w |  |  |
| 1031. | PLocalLoad R H | INV power to local load H |  | 0.1w |  |  |

| 1032. |  | PLocalLoad R L |  | INV power to local load L |  |  | 0.1w |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1033. |  | PLocalLoad S H |  |  |  |  | 0.1w |  |
| 1034. |  | PLocalLoad S L |  |  |  |  | 0.1w |  |
| 1035. |  | PLocalLoadT H |  |  |  |  | 0.1w |  |
| 1036. |  | PLocalLoadT L |  |  |  |  | 0.1w |  |
| 1037. |  | PLocalLoad total H |  | INV power to local load total H |  |  | 0.1w |  |
| 1038. |  | PLocalLoad total L |  | INV power to local load total L |  |  | 0.1w |  |
| 1039. |  | IPM Temperature |  | REC Temperature |  |  | 0.1℃ | No use |
| 1040. |  | Battery Temperature |  | Battery Temperature |  |  | 0.1℃ | Lead acid/lithium battery temp |
| 1041. |  | SP DSP Status |  | SP state |  |  |  | CHG/DisCHG |
| 1042. |  | SP Bus Volt |  | SP BUS2 Volt |  |  | 0.1V |  |
| 1043 |  |  |  |  |  |  |  |  |
| 发电量数据 |  |  |  |  |  |  |  |  |
| 1044. | Etouser_today H |  | Energy to user today high |  |  | 0.1kWh |  |  |
| 1045. | Etouser_today L |  | Energy to user today low |  |  | 0.1kWh |  |  |
| 1046. | Etouser_total H |  | Energy to user total high |  |  | 0.1kWh |  |  |
| 1047. | Etouser_ total L |  | Energy to user total high |  |  | 0.1kWh |  |  |
| 1048. | Etogrid_today H |  | Energy to grid today high |  |  | 0.1kWh |  |  |
| 1049. | Etogrid _today L |  | Energy to grid today low |  |  | 0.1kWh |  |  |
| 1050. | Etogrid _total H |  | Energy to grid total high |  |  | 0.1kWh |  |  |
| 1051. | Etogrid _ total L |  | Energy to grid total high |  |  | 0.1kWh |  |  |
| 1052. | Edischarge1_toda y H |  | Discharge energy1 today |  |  | 0.1kWh |  |  |
| 1053. | Edischarge1_toda y L |  | Discharge energy1 today |  |  | 0.1kWh |  |  |
| 1054. | Edischarge1_total H |  | Total discharge energy1 (high) |  |  | 0.1kWh |  |  |
| 1055. | Edischarge1_total L |  | Total discharge energy1 (low) |  |  | 0.1kWh |  |  |
| 1056. | Echarge1_today H |  | Charge1 energy today |  |  | 0.1kWh |  |  |
| 1057. | Echarge1_today L |  | Charge1 energy today |  |  | 0.1kWh |  |  |
| 1058. | Echarge1_total H |  | Charge1 energy total |  |  | 0.1kWh |  |  |
| 1059. | Echarge1_total L |  | Charge1 energy total |  |  | 0.1kWh |  |  |
| 1060. | ELocalLoad_Today H |  | Local load energy today |  |  | 0.1kWh |  |  |
| 1061. | ELocalLoad_Today L |  | Local load energy today |  |  | 0.1kWh |  |  |
| 1062. | ELocalLoad_Total |  | Local load energy total |  |  | 0.1kWh |  |  |

|  |  | H |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1063. |  | ELocalLoad_Total L |  |  |  | Local load energy total |  | 0.1kWh |  |
| 1064. |  | dwExportLimitAp parentPower |  |  |  | ExportLimitApparentPower H |  | 0.1kWh | ApparentPower |
| 1065. |  | dwExportLimitAp parentPower |  |  |  | ExportLimitApparentPower L |  | 0.1kWh | ApparentPower |
| 1066. |  | / |  |  |  | / | / | / | reserved |
|  | Ups information (offline) |  |  |  |  |  |  |  |  |
| 1067. |  | EPS Fac |  |  |  | UPSfrequency | 5000/6000 | 0.01Hz |  |
| 1068. |  | EPS Vac1 |  |  |  | UPS phase R output voltage | 2300 | 0.1V |  |
| 1069. |  | EPS Iac1 |  |  |  | UPS phase R output current |  | 0.1A |  |
| 1070. |  | EPS Pac1 H |  |  |  | UPS phase R output power (H) |  | 0.1VA |  |
| 1071. |  | EPS Pac1 L |  |  |  | UPS phase R output power (L) |  | 0.1VA |  |
| 1072. |  | EPS Vac2 |  |  |  | UPS phase S output voltage |  | 0.1V |  |
| 1073. |  | EPS Iac2 |  |  |  | UPS phase S output current |  | 0.1A | No use |
| 1074. |  | EPS Pac2 H |  |  |  | UPS phase S output power (H) |  | 0.1VA |  |
| 1075. |  | EPS Pac2 L |  |  |  | UPS phase S output power (L) |  | 0.1VA |  |
| 1076. |  | EPS Vac3 |  |  |  | UPS phase T output voltage |  | 0.1V |  |
| 1077. |  | EPS Iac3 |  |  |  | UPS phase T output current |  | 0.1A | No use |
| 1078. |  | EPS Pac3 H |  |  |  | UPS phase T output power (H) |  | 0.1VA |  |
| 1079. |  | EPS Pac3 L |  |  |  | UPS phase T output power (L) |  | 0.1VA |  |
| 1080. |  | Loadpercent |  |  |  | Load percent of UPS ouput | 0-100 | 1% |  |
| 1081. |  | PF |  |  |  | Power factor | 0-2 | 0.1 | Primary Value+1 |
|  | BMS Infomation |  |  |  |  |  |  |  |  |
| 1082. |  |  | BMS_StatusOld |  |  | StatusOld from BMS | Detail information, refer to document:GrowattxxSxx P ESS Protocol; |  |  |
| 1083. |  |  | BMS_Status |  |  | Status from BMS |  |  | W/R |
| 1084. |  |  | BMS_ErrorOld |  |  | Error info Old from BMS |  |  |  |
| 1085. |  |  | BMS_Error |  |  | Errorinfomation from BMS |  |  |  |
| 1086. |  |  | BMS_SOC |  |  | SOC from BMS |  |  | R SPH6K |
| 1087. |  |  | BMS_BatteryVo t |  | l | Battery voltage from BMS |  |  | R SPH6K |
| 1088. |  |  | BMS_BatteryCu r |  | r | Battery current from BMS |  |  |  |
| 1089. |  |  | BMS_BatteryTe mp |  |  | Battery temperature from BMS |  |  |  |
| 1090. |  |  | BMS_MaxCurr |  |  | Max. charge/discharge current from BMS (pylon) |  |  |  |
| 1091. |  |  | BMS_GaugeRM |  |  | Gauge RM from BMS |  |  |  |
| 1092. |  |  | BMS_GaugeFCC |  |  | Gauge FCC from BMS |  |  |  |
| 1093. |  |  | BMS_FW |  |  |  |  |  |  |

| 1094. | BMS_DeltaVolt | Delta V from BMS |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1095. | BMS_CycleCnt | Cycle Count from BMS |  |  |  |
| 1096. | BMS_SOH | SOH from BMS |  |  |  |
| 1097. | BMS_ConstantV olt | CV voltage from BMS |  |  |  |
| 1098. | BMS_WarnInfoO ld | Warning info old from BMS |  |  |  |
| 1099. | BMS_WarnInfo | Warning info from BMS |  |  |  |
| 1100. | BMS_GaugeICCu rr | Gauge IC current from BMS |  |  |  |
| 1101. | BMS_MCUVersi on | MCU Software version from BMS |  |  |  |
| 1102. | BMS_GaugeVers ion | Gauge Version from BMS |  |  |  |
| 1103. | BMS_wGaugeFR Version_ L | Gauge FR Version L16 from BMS |  |  |  |
| 1104. | BMS_wGaugeFR Version_H | Gauge FR Version H16 from BMS |  |  |  |
| 1105. | BMS_BMSInfo | BMSInformation from BMS |  |  |  |
| 1106. | BMS_PackInfo | Pack Information from BMS |  |  |  |
| 1107. | BMS_UsingCap | Using Cap from BMS |  |  |  |
| 1108. | BMS_ Cell1_Volt | Cell1_Voltage from BMS |  |  |  |
| 1109. | BMS_ Cell2_Volt | Cell_Voltage from BMS |  |  |  |
| … |  |  |  |  |  |
| 1123 | BMS_ Cell16_Volt | Cell16_Voltage from BMS |  |  |  |
| 1124 | AC Charge Energy Today H | AC Charge Energy today | kwh |  | Energy today |
| Ninth group reserved for storage power |  |  |  |  |  |
| 1125. | ACCharge Energy TodayL | AC Charge Energy today | kwh |  |  |
| 1126. | AC Charge Energy Total H |  |  |  | Energy total |
| 1127. | ACCharge Energy Total L |  |  |  |  |
| 1128. | AC Charge Power H | AC Charge Power | W |  |  |
| 1129. | AC Charge Power L | AC Charge Power | w |  |  |
| 1130. | 70% INV Power adjust | uwGridPower_70_AdjEE_SP | W |  |  |
| 1131. | Extra AC Power to grid_H | Extra inverte AC Power to grid High | For SPA connect inverter |  | SPA used |
| 1132. | Extra AC Power to grid_L | Extrainverte AC Power to grid Low |  |  | SPA used |
| 1133. | Eextra_today H | Extra inverter PowerTOUser_Extra today (high) | R | 0.1kWh | SPA used |
| 1134. | Eextra_today L | Extra inverter PowerTOUser_Extra today (low) | R | 0.1kWh | SPA used |
| 1135. | Eextra_total H | Extra inverter PowerTOUser_Extra total(high) |  | 0.1kWh | SPA used |
| 1136. | Eextra_total L | Extra inverter PowerTOUser_Extra total(low) |  | 0.1kWh | SPA used |
| 1137. | Esystem_today H | System electric energy today H |  | 0.1kWh | SPA used System electric energy today H |
| 1138. | Esystem_ today L | System electric energy today L |  | 0.1kWh | SPA used System electric energy today L |
| 1139. | Esystem_total H | System electric energy total H |  | 0.1kWh | SPA used System electric energy total H |
| 1140. | Esystem_ total L | System electric energy total L |  | 0.1kWh | SPA used System electric energy total L |
| …… | / | / | / | / | reversed |
| 1249. | / | / | / | / | reversed |

|  | thirteen group for Storage power’s SPA |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2000 |  | Inverter Status | Inverter run state |  | 0:waiting, 1:normal, 3:fault |  | SPA |
| …… |  | reversed |  |  |  |  |  |
| 2035 |  | Pac H | Output power (high) |  |  | 0.1W | SPA |
| 2036 |  | Pac L | Output power (low) |  |  | 0.1W | SPA |
| 2037 |  | Fac | Grid frequency |  |  | 0.01Hz | SPA |
| 2038 |  | Vac1 | Three/single phase grid voltage |  |  | 0.1V | SPA |
| 2039 |  | Iac1 | Three/single phase grid output current |  |  | 0.1A | SPA |
| 2040 |  | Pac1 H | Three/single phase grid output watt VA (high) |  |  | 0.1VA | SPA |
| 2041 |  | Pac1 L | Three/single phase grid output watt |  |  | 0.1VA | SPA |

|  |  | VA(low) |  |  |  |
| --- | --- | --- | --- | --- | --- |
| …… | reversed |  |  |  |  |
| 2053 | Eac today H | Today generate energy (high) |  | 0.1kWH | SPA |
| 2054 | Eac today L | Today generate energy (low) |  | 0.1kWH | SPA |
| 2055 | Eac total H | Total generate energy (high) |  | 0.1kWH | SPA |
| 2056 | Eac total L | Total generate energy (low) |  | 0.1kWH | SPA |
| 2057 | Time total H | Work time total (high) |  | 0.5s | SPA |
| 2058 | Time total L | Work time total (low) |  | 0.5s | SPA |
| …… | reversed |  |  |  |  |
| 2093 | Temp1 | Inverter temperature |  | 0.1C | SPA |
| 2094 | Temp2 | The inside IPM in inverter Temperature |  | 0.1C | SPA |
| 2095 | Temp3 | Boost temperature |  | 0.1C | SPA |
| 2096 | Temp4 |  |  |  | reserved |
| 2097 | uwBatVolt_DSP | BatVolt_DSP |  | 0.1V | BatVolt(DSP) |
| 2098 | P Bus Voltage | P Bus inside Voltage |  | 0.1V | SPA |
| 2099 | N Bus Voltage | N Bus inside Voltage |  | 0.1V | SPA |
| 2100 | RemoteCtrlEn | / | 0.Load First 1.BatFirst 2.Grid | / | Remote setup enable |
| 2101 | RemoteCtrlPow er | / |  | / | Remotely set power |
| 2102 | Extra AC Power to grid_H | Extra inverte AC Power to grid High | For SPA connect inverter |  | SPA used |
| 2103 | Extra AC Power to grid_L | Extrainverte AC Power to grid Low |  |  | SPA used |
| 2104 | Eextra_today H | Extra inverter PowerTOUser_Extra today (high) | R | 0.1kWh | SPA used |
| 2105 | Eextra_today L | Extra inverter PowerTOUser_Extra today (low) | R | 0.1kWh | SPA used |
| 2106 | Eextra_total H | Extra inverter PowerTOUser_Extratotal(high) |  | 0.1kWh | SPA used |
| 2107 | Eextra_total L | Extra inverter PowerTOUser_Extra total(low) |  | 0.1kWh | SPA used |
| 2108 | Esystem_today H | System electric energy today H |  | 0.1kWh | SPA used System electric energy today H |
| 2109 | Esystem_ today L | System electric energy today L |  | 0.1kWh | SPA used System electric |

|  |  |  |  |  |  | energy today L |
| --- | --- | --- | --- | --- | --- | --- |
| 2110 | Esystem_total H | System electric energy total H |  | 0.1kWh |  | SPA used System electric energy total H |
| 2111 | Esystem_ total L | System electric energy total L |  | 0.1kWh |  | SPA used System electric energy total L |
| 2112 | EACharge_Today _H | ACCharge energy today |  | 0.1kwh |  | Storage Power |
| 2113 | EACharge_Today _L | ACCharge energy today |  | 0.1kwh |  | Storage Power |
| 2114 | EACharge_Total _H | ACCharge energy total |  | 0.1kwh |  | Storage Power |
| 2115 | EACharge_Total _L | ACCharge energy total |  | 0.1kwh |  | Storage Power |
| 2116 | AC charge Power_H | Grid power to local load |  | 0.1kwh |  | Storage Power |
| 2117 | AC charge Power_L | Grid power to local load |  | 0.1kwh |  | Storage Power |
| 2118 | Priority | 0:Load First 1:Battery First 2:Grid First |  |  |  | Storage Power |
| 2119 | Battery Type | 0：Lead-acid 1：Lithium battery |  |  |  | Storage Power |
| 2120 | AutoProofreadC MD | Aging mode |  |  |  | Storage Power |
| … | reserved |  |  |  |  | reserved |
| 2124. | reserved |  |  |  |  | reserved |
| Use for TL-X and TL-XH |  |  |  |  |  |  |
| 3000 | Inverter Status | Inverter run state High 8 bits mode (specific mode) 0: Waiting module 1: Self-test mode, optional 2: Reserved |  |  |  |  |

|  |  | 3：SysFault module 4: Flash module 5：PVBATOnline module: 6：BatOnline module 7：PVOfflineMode 8：BatOfflineMode The lower 8 bits indicate the machine status (web page display) 0: StandbyStatus; 1: NormalStatus; 3: FaultStatus 4：FlashStatus; |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 3001 | Ppv H | PV total power |  | 0.1W |  |
| 3002 | Ppv L |  |  |  |  |
| 3003 | Vpv1 | PV1 voltage |  | 0.1V |  |
| 3004 | Ipv1 | PV1 input current |  | 0.1A |  |
| 3005 | Ppv1 H | PV1 power |  | 0.1W |  |
| 3006 | Ppv1 L |  |  |  |  |
| 3007 | Vpv2 | PV2 voltage |  | 0.1V |  |
| 3008 | Ipv2 | PV2 input current |  | 0.1A |  |
| 3009 | Ppv2 H | PV2 power |  | 0.1W |  |
| 3010 | Ppv2 L |  |  |  |  |
| 3011 | Vpv3 | PV3 voltage |  | 0.1V |  |
| 3012 | Ipv3 | PV3 input current |  | 0.1A |  |
| 3013 | Ppv3 H | PV3 power |  | 0.1W |  |
| 3014 | Ppv3 L |  |  |  |  |
| 3015 | Vpv4 | PV4 voltage |  |  |  |
| 3016 | Ipv4 | PV4 input current |  |  |  |
| 3017 | Ppv4H | PV4 power |  |  |  |
| 3018 | Ppv4L |  |  |  |  |
| 3019 | Reserved |  |  |  |  |
| 3020 | Reserved |  |  |  |  |
| 3021 | Reserved |  |  |  |  |
| 3022 | Reserved |  |  |  |  |
| 3023 | Pac H | Output power |  | 0.1W | Output power |
| 3024 | Pac L |  |  |  |  |
| 3025 | Fac | Grid frequency |  | 0.01Hz | Grid frequency |
| 3026 | Vac1 | Three/single phase grid voltage |  | 0.1V | Three/single phase grid |

|  |  |  |  |  | voltage |
| --- | --- | --- | --- | --- | --- |
| 3027 | Iac1 | Three/single phase grid output current |  | 0.1A | Three/single phase grid output current |
| 3028 | Pac1 H | Three/single phase grid output watt VA |  | 0.1VA | Three/single phase grid output watt VA |
| 3029 | Pac1 L |  |  |  |  |
| 3030 | Vac2 | Three phase grid voltage |  | 0.1V | Three phase grid voltage |
| 3031 | Iac2 | Three phase grid output current |  | 0.1A | Three phase grid output current |
| 3032 | Pac2 H | Three phase grid output power |  | 0.1VA | Three phase grid output power |
| 3033 | Pac2 L |  |  |  |  |
| 3034 | Vac3 | Three phase grid voltage |  | 0.1V | Three phase grid voltage |
| 3035 | Iac3 | Three phase grid output current |  | 0.1A | Three phase grid output current |
| 3036 | Pac3 H | Three phase grid output power |  | 0.1VA | Three phase grid output power |
| 3037 | Pac3 L |  |  |  |  |
| 3038 | Vac_RS | Three phase grid voltage |  | 0.1V |  |
| 3039 | Vac_ST | Three phase grid voltage |  | 0.1V |  |
| 3040 | Vac_TR | Three phase grid voltage |  | 0.1V |  |
| 3041 | Ptouser total H | Total forward power |  | 0.1W | Total forward power |
| 3042 | Ptouser total L |  |  |  |  |
| 3043 | Ptogrid total H | Total reverse power |  | 0.1W | Total reverse power |
| 3044 | Ptogrid total L |  |  |  |  |
| 3045 | Ptoload total H | Total load power |  | 0.1W | Total load power |
| 3046 | Ptoload total L |  |  |  |  |
| 3047 | Time total H | Work time total |  | 0.5s |  |
| 3048 | Time total L |  |  |  |  |
| 3049 | Eac today H | Today generate energy |  | 0.1kWh | Today generate energy |
| 3050 | Eac today L |  |  |  |  |

| 3051 | Eac total H | Total generate energy |  | 0.1kWh | Total generate energy |
| --- | --- | --- | --- | --- | --- |
| 3052 | Eac total L |  |  |  |  |
| 3053 | Epv_total H | PV energy total |  | 0.1kWh | PV energy total |
| 3054 | Epv_total L |  |  |  |  |
| 3055 | Epv1_today H | PV1 energy today |  | 0.1kWh |  |
| 3056 | Epv1_today L |  |  |  |  |
| 3057 | Epv1_total H | PV1 energy total |  | 0.1kWh |  |
| 3058 | Epv1_total L |  |  |  |  |
| 3059 | Epv2_today H | PV2 energy today |  | 0.1kWh |  |
| 3060 | Epv2_today L |  |  |  |  |
| 3061 | Epv2_total H | PV2 energy total |  | 0.1kWh |  |
| 3062 | Epv2_total L |  |  |  |  |
| 3063 | Epv3_today H | PV3 energy today |  | 0.1kWh |  |
| 3064 | Epv3_today L |  |  |  |  |
| 3065 | Epv3_total H | PV3 energy total |  | 0.1kWh |  |
| 3066 | Epv3_total L |  |  |  |  |
| 3067 | Etouser_today H | Today energy to user |  | 0.1kWh | Today energy to user |
| 3068 | Etouser_today L |  |  |  |  |
| 3069 | Etouser_total H | Total energy to user |  | 0.1kWh | Total energy to user |
| 3070 | Etouser_total L |  |  |  |  |
| 3071 | Etogrid_today H | Today energy to grid |  | 0.1kWh | Today energy to grid |
| 3072 | Etogrid_today L |  |  |  |  |
| 3073 | Etogrid_total H | Total energy to grid |  | 0.1kWh | Total energy to grid |
| 3074 | Etogrid_total L |  |  |  |  |
| 3075 | Eload_today H | Today energy of user load |  | 0.1kWh | Today energy of user load |
| 3076 | Eload_today L |  |  |  |  |
| 3077 | Eload_total H | Total energy of user load |  | 0.1kWh | Total energy of user load |
| 3078 | Eload_total L |  |  |  |  |
| 3079 | Reserved |  |  |  |  |
| 3080 | Reserved |  |  |  |  |
| 3081 | Reserved |  |  |  |  |
| 3082 | Reserved |  |  |  |  |
| 3083 | Reserved |  |  |  |  |
| 3084 | Reserved |  |  |  |  |

| 3085 | Reserved |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 3086 | DeratingMode | DeratingMode |  |  | 0:cNOTDerate 1:cPVHighDer ate 2: cPowerCon stantDerate 3: cGridVHigh Derate 4:cFreqHighD erate 5:cDcSoureM odeDerate 6:cInvTemprD erate 7:cActivePow erOrder 8:cLoadSpeed Process 9:cOverBack byTime 10:cInternalT emprDerate 11:cOutTemp rDerate 12:cLineImpe CalcDerate 13: cParallelA ntiBackflowD erate 14:cLocalAnti BackflowDera te 15:cBdcLoadP riDerate 16:cChkCTErr Derate |
| 3087 | ISO | PV ISO value |  | 1KΩ |  |
| 3088 | DCI_R | R DCI Curr |  | 0.1mA |  |
| 3089 | DCI_S | S DCI Curr |  | 0.1mA |  |
| 3090 | DCI_T | T DCI Curr |  | 0.1mA |  |
| 3091 | GFCI | GFCI Curr |  | 1mA |  |
| 3092 | Reserved |  |  |  |  |

| 3093 | Temp1 | Inverter temperature |  | 0.1℃ |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3094 | Temp2 | The inside IPM in inverter temperature |  | 0.1℃ |  |  |
| 3095 | Temp3 | Boost temperature |  | 0.1℃ |  |  |
| 3096 | Temp4 | Reserved |  | 0.1℃ |  |  |
| 3097 | Temp5 | Commmunication broad temperature |  | 0.1℃ |  |  |
| 3098 | P Bus Voltage | P Bus inside Voltage |  | 0.1V |  |  |
| 3099 | N Bus Voltage | N Bus inside Voltage |  | 0.1V |  |  |
| 3100 | IPF | Inverter output PF now |  |  | 0-20000 |  |
| 3101 | RealOPPercent | Real Output power Percent |  | 1% | 1~100 |  |
| 3102 | OPFullwatt H | Output Maxpower Limited |  | 0.1W | Output Maxpower Limited |  |
| 3103 | OPFullwatt L |  |  |  |  |  |
| 3104 | StandbyFlag | Inverter standby flag |  | bitfield | bit0:turn off Order； bit1:PV Low； bit2:AC Volt/Freq out of scope； bit3~bit7 ： Reserved |  |
| 3105 | Fault code | Inverter fault code |  |  |  |  |
| 3106 | Warning code | Inverter Warning code |  |  |  |  |
| 3107 | Systemfault word0 | System fault word0 |  | bitfield |  |  |
| 3108 | Systemfault word1 | System fault word1 |  | bitfield |  |  |
| 3109 | Systemfault word2 | System fault word2 |  | bitfield |  |  |
| 3110 | Systemfault word3 | System fault word3 |  | bitfield |  |  |
| 3111 | Systemfault word4 | System fault word4 |  | bitfield |  |  |
| 3112 | Systemfault word5 | System fault word5 |  | bitfield |  |  |
| 3113 | Systemfault word6 | System fault word6 |  | bitfield |  |  |
| 3114 | Systemfault word7 | System fault word7 |  | bitfield |  |  |
| 3115 | inv start delay time | inv start delay time |  | 1S | inv start delay time |  |
| 3116 | Reserved |  |  |  |  |  |
| 3117 | Reserved |  |  |  |  |  |

| 3118 | BDC_OnOffState | BDC connect state |  |  | 0:No BDC Connect 1:BDC1 Connect 2:BDC2 Connect 3:BDC1+BDC2 Connect |
| --- | --- | --- | --- | --- | --- |
| 3119 | DryContactState | Current status of DryContact |  |  | Current status of DryContact 0: turn off; 1: turn on; |
| 3120 | Reserved |  |  |  |  |
| 3121 | Reserved |  |  |  |  |
| 3122 | Reserved |  |  |  |  |
| 3123 | Reserved |  |  |  |  |
| 3124 | Reserved |  |  |  |  |
| 3125 | Edischr_today H | Today discharge energy |  | 0.1kWh | Today discharge energy |
| 3126 | Edischr_today L |  |  |  |  |
| 3127 | Edischr_total H | Total discharge energy |  | 0.1kWh | Total discharge energy |
| 3128 | Edischr_total L |  |  |  |  |
| 3129 | Echr_today H | Charge energy today |  | 0.1kWh | Charge energy today |
| 3130 | Echr_today L |  |  |  |  |
| 3131 | Echr_total H | Charge energy total |  | 0.1kWh | Charge energy total |
| 3132 | Echr_total L |  |  |  |  |
| 3133 | Eacchr_today H | Today energy of AC charge |  | 0.1kWh | Today energy of AC charge |
| 3134 | Eacchr_today L |  |  |  |  |
| 3135 | Eacchr_total H | Total energy of AC charge |  | 0.1kWh | Total energy of AC charge |
| 3136 | Eacchr_total L |  |  |  |  |
| 3137 | Reserved |  |  |  |  |
| 3138 | Reserved |  |  |  |  |
| 3139 | Reserved |  |  |  |  |
| 3140 | Reserved |  |  |  |  |
| 3141 | Reserved |  |  |  |  |
| 3142 | Reserved |  |  |  |  |
| 3143 | Reserved |  |  |  |  |
| 3144 | Priority | Word Mode |  |  | 0 LoadFirst 1 |

|  |  |  |  |  | BatteryFirs t 2 GridFirst |
| --- | --- | --- | --- | --- | --- |
| 3145 | EPS Fac | UPS frequency |  | 0.01Hz |  |
| 3146 | EPS Vac1 | UPS phase R output voltage |  | 0.1V |  |
| 3147 | EPS Iac1 | UPS phase R output current |  | 0.1A |  |
| 3148 | EPS Pac1 H | UPS phase R output power |  | 0.1VA |  |
| 3149 | EPS Pac1 L |  |  |  |  |
| 3150 | EPS Vac2 | UPS phase S output voltage |  | 0.1V |  |
| 3151 | EPS Iac2 | UPS phase S output current |  | 0.1A |  |
| 3152 | EPS Pac2 H | UPS phase S output power |  | 0.1VA |  |
| 3153 | EPS Pac2 L |  |  |  |  |
| 3154 | EPS Vac3 | UPS phase T output voltage |  | 0.1V |  |
| 3155 | EPS Iac3 | UPS phase T output current |  | 0.1A |  |
| 3156 | EPS Pac3 H | UPS phase T output power |  | 0.1VA |  |
| 3157 | EPS Pac3 L |  |  |  |  |
| 3158 | EPS Pac H | UPS output power |  | 0.1VA |  |
| 3159 | EPS Pac L |  |  |  |  |
| 3160 | Loadpercent | Load percent of UPS ouput |  | 0.10% |  |
| 3161 | PF | Power factor |  | 0.1 |  |
| 3162 | DCV | DC voltage |  | 1mV |  |
| 3163 | Reserved |  |  |  |  |
| 3164 | Reserved |  |  |  |  |
| 3165 | Reserved |  |  |  |  |
| 3166 | SysState_Mode | System work State and mode 高 8 位表示模式； 0：No charge and discharge； 1：charge； 2：Discharge； 低 8 位表示状态； 0: StandbyStatus; 1: NormalStatus; 2: FaultStatus 3：FlashStatus; |  |  | BDC1 |
| 3167 | FaultCode | Storge device fault code |  |  |  |
| 3168 | WarnCode | Storge device warning code |  |  |  |
| 3169 | Vbat | Battery voltage |  | 0.01V |  |
| 3170 | Ibat | Battery current |  | 0.1A |  |
| 3171 | SOC | State of charge Capacity |  | 1% |  |
| 3172 | Vbus1 | BUS1 voltage |  | 0.1V |  |

| 3173 | Vbus2 | BUS2 voltage |  | 0.1V |  |
| --- | --- | --- | --- | --- | --- |
| 3174 | Ibb | BUCK-BOOST Current |  | 0.1A |  |
| 3175 | Illc | LLC Current |  | 0.1A |  |
| 3176 | TempA | Temperture A |  | 0.1℃ |  |
| 3177 | TempB | Temperture B |  | 0.1℃ |  |
| 3178 | Pdischr H | Discharge power |  | 0.1W |  |
| 3179 | Pdischr L |  |  |  |  |
| 3180 | Pchr H | Charge power |  | 0.1W |  |
| 3181 | Pchr L |  |  |  |  |
| 3182 | Edischr_total H | Discharge total energy of storge device |  | 0.1kWh |  |
| 3183 | Edischr_total L |  |  |  |  |
| 3184 | Echr_total H | Charge total energy of storge device |  | 0.1kWh |  |
| 3185 | Echr_total L |  |  |  |  |
| 3186 | Reserved | Reserved |  |  |  |
| 3187 | BDC1_Flag | BDC mark (charge and discharge, fault alarm code) Bit0: ChargeEn; BDC allows charging Bit1: DischargeEn; BDC allows discharge Bit2~7: Resvd; reserved Bit8~11: WarnSubCode; BDC sub-warning code Bit12~15: FaultSubCode; BDC sub-error code |  |  |  |
| 3188 | Reserved |  |  |  |  |
| 3189 | SysState_Mode | System work State and mode 高 8 位表示模式； 0：No charge and discharge； 1：charge； 2：Discharge； 低 8 位表示状态； 0: StandbyStatus; 1: NormalStatus; 2: FaultStatus 3：FlashStatus； |  |  |  |
| 3190 | FaultCode | Storge device fault code |  |  | BDC2 |
| 3191 | WarnCode | Storge device warning code |  |  |  |
| 3192 | Vbat | Battery voltage |  | 0.01V |  |
| 3193 | Ibat | Battery current |  | 0.1A |  |
| 3194 | SOC | State of charge Capacity |  | 1% |  |

| 3195 | Vbus1 | BUS1 voltage |  | 0.1V |  |
| --- | --- | --- | --- | --- | --- |
| 3196 | Vbus2 | BUS2 voltage |  | 0.1V |  |
| 3197 | Ibb | BUCK-BOOST Current |  | 0.1A |  |
| 3198 | Illc | LLC Current |  | 0.1A |  |
| 3199 | TempA | Temperture A |  | 0.1℃ |  |
| 3200 | TempB | Temperture B |  | 0.1℃ |  |
| 3201 | Pdischr H | Discharge power |  | 0.1W |  |
| 3202 | Pdischr L |  |  |  |  |
| 3203 | Pchr H | Charge power |  | 0.1W |  |
| 3204 | Pchr L |  |  |  |  |
| 3205 | Edischr_total H | Discharge total energy of storge device |  | 0.1kWh |  |
| 3206 | Edischr_total L |  |  |  |  |
| 3207 | Echr_total H | Charge total energy of storge device |  | 0.1kWh |  |
| 3208 | Echr_total L |  |  |  |  |
| 3209 | reserved | reserved |  |  |  |
| 3210 | BDC2_Flag | BDC mark (charge and discharge, fault alarm code) Bit0: ChargeEn; BDC allows charging Bit1: DischargeEn; BDC allows discharge Bit2~7: Resvd; reserved Bit8~11: WarnSubCode; BDC sub-warning code Bit12~15: FaultSubCode; BDC sub-error code |  |  |  |
| 3211 | Reserved |  |  |  |  |
| 3212 | BMS_Status | Status from BMS | R | 1 |  |
| 3213 | BMS_Error | Error information from BMS | R | 1 |  |
| 3214 | BMS_WarnInfo | Warning information from BMS | R | 1 |  |
| 3215 | BMS_SOC | SOC from BMS | R | 1% |  |
| 3216 | BMS_BatteryVol t | Battery voltage from BMS | R | 0.01V |  |
| 3217 | BMS_BatteryCur r | Battery current from BMS | R | 0.01A |  |
| 3218 | BMS_BatteryTe mp | Battery temperature from BMS | R | 0.1℃ |  |
| 3219 | BMS_MaxCurr | Max. charge/discharge current from BMS (pylon) | R | 0.01A |  |
| 3220 | BMS_DeltaVolt | Delta V from BMS | R | 0.01A |  |
| 3221 | BMS_CycleCnt | Cycle Count from BMS | R | 1 |  |
| 3222 | BMS_SOH | SOH from BMS | R | 1 |  |
| 3223 | BMS_ConstantV olt | CV voltage from BMS | R | 0.01V |  |
| 3224 | BMS_BMSInfo | BMSInformation from BMS | R | 1 |  |
| 3225 | BMS_PackInfo | Pack Information from BMS | R | 1 |  |
| 3226 | BMS_UsingCap | Using Cap from BMS | R | 1 |  |
| 3227 | BMS_FW |  | R | 1 |  |
| 3228 | BMS_MCUVersi on | MCU Software version from BMS | R | 1 |  |
| 3229 | BMSCommType | BMS Communication Type |  |  | BMS Communicati on Type 0: RS485; 1: CAN; |
| 3230 ~ 3233 | Reserved |  |  |  |  |
| 3234 ~ 3249 | Debug data | Debug data |  |  |  |

&*1:  Inverter fault code Bit:

| Fault type value | Means(The message showed on the inverter when the inverter has fault) |
| --- | --- |
| 1~23 | " Error: 99+x ", |
| 24 | "Auto Test Failed", |
| 25 | "No AC Connection", |
| 26 | "PV Isolation Low", |
| 27 | " Residual I High", |
| 28 | " Output High DCI", |
| 29 | " PV Voltage High", |
| 30 | " AC V Outrange ", |
| 31 | " AC F Outrange ", |
| 32 | " Module Hot " |

&*2:  The value is 0.1V when the fault is the voltage, is 0.01Hz when the fault is the frequency; &*3:

| High byte value |  | Means |  |  |  | low byte value |  | Means |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 0 |  | Auto test stop |  |  |  | 0 |  | No test |  |  |
|  |  | 1 |  | Auto test starting |  |  |  | 1 |  | Testing grid volt high pro |  |  |
|  |  | 2 |  | Auto testing |  |  |  | 2 |  | Testing grid volt low pro |  |  |
|  |  |  |  |  |  |  |  | 3 |  | Testing grid frequency high pro |  |  |
|  |  |  |  |  |  |  |  | 4 |  | Testing grid frequency low pro |  |  |

&*4: The variable “wAutoTestResult” and “cTestStepStop”: wAutoTestResult is the step test time  counter, when it reach cTestStepStop, this step test will stop and fail.

&*5: Inverter Model: A , could be show: “A1 B0 D0 T0 PF U1 M5 S1” or “1000F151”

Ax=(A&0XF00000000)>>28

Bx=(A&0XF0000000)>>24

Dx=(A&0XF000000)>>20

Tx=(A&0XF00000)>>16

Px=(A&0x00F000)>>12

Ux=(A&0x000F00)>>8

Mx=(A&0x0000F0)>>4

Sx=(A&0x00000F)

&*6: DTC(Device type code)

| Code No. | Device type | Note |
| --- | --- | --- |
| 001xx | Inverter | 1 tracker and 1phase Grid connect PV inverter TL |
| 002xx | Inverter | 2 tracker and 1phase Grid connect PV inverter TL |
| 003xx | Inverter | 1 tracker and 1phase Grid connect PV inverter HF |
| 004xx | Inverter | 2 tracker and 1phase Grid connect PV inverter HF |
| 005xx | Inverter | 1 tracker and 1phase Grid connect PV inverter LF |
| 006xx | Inverter | 2 tracker and 1phase Grid connect PV inverter LF |
| 007xx | Inverter | 1 tracker and 3phase Grid connect PV inverter TL |
| 008xx | Inverter | 2 tracker and 3phase Grid connect PV inverter TL |
| 009xx | Inverter | 1 tracker and 3phase Grid connect PV inverter LF |
| 010xx | Inverter | 2 tracker and 3phase Grid connect PV inverter LF |
| …… |  |  |
| 10001 | Data logger | RF-ShineVersion |
| 10002 | Data logger | Web-ShinePano |
| 10003 | Data logger | Web-ShineWebBox |
| 10004 | Data logger | WL-WIFI Module |
| …… |  |  |
| 11001 | Confluence box | Confluence box 1 |
| …… |  |  |

&*7: Grid network power control command password:

Inverter is in lock state after power on; change the power control by network command should unlock   	inverter first; default pw is XXXXXX;

Unlock: send 0 to 3-135, then send password to 3-136~138; inverter will auto lock in 5min after    	 	 	unlocked;

Change PW: unlock first, then send 1 to 3-135, then send new password to 3-136~138;  	 	Lock: send 0 or 2 to 3-135;

&*8: Inverter fault code and warning code

| Fault code |  |  |  | Warning code |
| --- | --- | --- | --- | --- |
| 0x00000001 | \ |  | 0x0001 | Fan warning |
| 0x00000002 | Communication error |  | 0x0002 | String communication abnormal |
| 0x00000004 | \ |  | 0x0004 | StrPIDconfig Warning |
| 0x00000008 | StrReverse or StrShort fault |  | 0x0008 | \ |
| 0x00000010 | Model Init fault |  | 0x0010 | DSP and COM firmware unmatch |
| 0x00000020 | Grid Volt Sample diffirent |  | 0x0020 | \ |
| 0x00000040 | ISO Sample diffirent |  | 0x0040 | SPD abnormal |
| 0x00000080 | GFCI Sample diffirent |  | 0x0080 | GND and N connect abnormal |
| 0x00000100 | \ |  | 0x0100 | PV1 or PV2 circuit short |
| 0x00000200 | \ |  | 0x0200 | PV1 or PV2 boost driver broken |
| 0x00000400 | \ |  | 0x0400 | \ |
| 0x00000800 | \ |  | 0x0800 | \ |
| 0x00001000 | AFCI Fault |  | 0x1000 | \ |
| 0x00002000 | \ |  | 0x2000 | \ |
| 0x00004000 | AFCI Module fault |  | 0x4000 | \ |
| 0x00008000 | \ |  | 0x8000 | \ |
| 0x00010000 | \ |  |  |  |
| 0x00020000 | Relay check fault |  |  |  |
| 0x00040000 | \ |  |  |  |
| 0x00080000 | \ |  |  |  |
| 0x00100000 | \ |  |  |  |
| 0x00200000 | Communication error |  |  |  |
| 0x00400000 | Bus Voltage error |  |  |  |
| 0x00800000 | AutoTest fail |  |  |  |
| 0x01000000 | No Utility |  |  |  |
| 0x02000000 | PV Isolation Low |  |  |  |
| 0x04000000 | Residual I High |  |  |  |
| 0x08000000 | Output High DCI |  |  |  |
| 0x10000000 | PV Voltage high |  |  |  |
| 0x20000000 | AC V Outrange |  |  |  |
| 0x40000000 | AC F Outrange |  |  |  |
| 0x80000000 | TempratureHigh |  |  |  |

&*9 Warning Value

|  | Warning Value 1 | Warning Value 2 | Warning Value 3 |
| --- | --- | --- | --- |
| 0x0001 | String1abnormal | PV1ShortCircuit | AC SPD abnormal |
| 0x0002 | String2abnormal | PV2ShortCircuit | DC SPD abnormal |
| 0x0004 | String3abnormal | PV3ShortCircuit |  |
| 0x0008 | String4abnormal | PV4ShortCircuit |  |
| 0x0010 | String5abnormal | PV5ShortCircuit |  |
| 0x0020 | String6abnormal | PV6ShortCircuit |  |
| 0x0040 | String7abnormal | PV7ShortCircuit |  |
| 0x0080 | String8abnormal | PV8ShortCircuit |  |
| 0x0100 | String9abnormal | BT1DriverFault |  |
| 0x0200 | String10abnormal | BT2DriverFault |  |
| 0x0400 | String11abnormal | BT3DriverFault |  |
| 0x0800 | String12abnormal | BT4DriverFault |  |
| 0x1000 | String13abnormal | BT5DriverFault |  |
| 0x2000 | String14abnormal | BT6DriverFault |  |
| 0x4000 | String15abnormal | BT7DriverFault |  |
| 0x8000 | String16abnormal | BT8DriverFault |  |

&*11: Inverter Model: A , could be show: “S0A D01 B01 T06 P0F U01 M03E8” or

“0A0101060F0103E8”

Sx=(A&0XFF00000000000000)>>56

Dx=(A&0X00FF000000000000)>>48

Bx=(A&0X0000FF0000000000)>>40

Tx=(A&0X000000FF00000000)>>32 Px=(A&0x00000000FF000000)>>24

Ux=(A&0x0000000000FF0000)>>16

Mx=(A&0x000000000000FFFF)

HybridAbnoram/Fault/warning bit definition

(Abnormal:record 	event 	for 	debug,continueworking;fault:record 	event 	and 	show 	for

debug,stopworking;Warning:record event and show,continue working)

| Word definition |  | Bit definition |  | comment |
| --- | --- | --- | --- | --- |
| System fault word0 | Byte0 | MasterForceINVFault | 0. | M3 on/off control |
|  |  | MasterForceSPFault | 1. |  |
|  |  | BusVoltHigh_TZ | 2. | restart PWM |
|  |  | BusVoltHigh_ISR | 3. | restartPWM |
|  |  | reserved | 4. |  |
|  |  | reserved | 5. |  |
|  |  | reserved | 6. |  |

|  |  | reserved | 7. |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Byte1 | GridZClossFault | 8. | Grid side abnormal |  |
|  |  | reserved | 9. |  |  |
|  |  | reserved | 10. |  |  |
|  |  | GFCIHigh | 11. |  |  |
|  |  | GridR_VFault | 12. |  |  |
|  |  | GridS_VFault | 13. |  |  |
|  |  | GridT_VFault | 14. |  |  |
|  |  | GridFFault | 15. |  |  |
| System fault word1 | Byte2 | RelayFault | 0. | Grid side abnormal |  |
|  |  | GFCIDamage | 1. |  |  |
|  |  | GridR_VLowFault | 2. |  |  |
|  |  | GridR_VHighFault | 3. |  |  |
|  |  | GridS_VLowFault | 4. |  |  |
|  |  | GridS_VHighFault | 5. |  |  |
|  |  | GridT_VLowFault | 6. |  |  |
|  |  | GridT_VHighFault | 7. |  |  |
|  | Byte3 | INVCurrOCP_ISR | 8. | Grid side abnormal |  |
|  |  | INVCurrOCP_TZ | 9. |  |  |
|  |  | DCIHigh | 10. |  |  |
|  |  | reserved | 11. |  |  |
|  |  | INVR_CurrOCP_Rms | 12. |  |  |
|  |  | INVS_CurrOCP_Rms | 13. |  |  |
|  |  | INVT_CurrOCP_Rms | 14. |  |  |
|  |  | NoUtility | 15. |  |  |
| System fault word2 | Byte4 | GridFLowFault | 0. | Grid side abnormal |  |
|  |  | GridFHighFault | 1. |  |  |
|  |  | GridVolt_Unbalance_Fault | 2. |  |  |
|  |  | AC_PLL_Fault | 3. |  |  |
|  |  | OverLoadFault | 4. |  |  |
|  |  | reserved | 5. |  |  |
|  |  | reserved | 6. |  |  |
|  |  | reserved | 7. |  |  |
|  | Byte5 | EPS_LineVoltR_Loss | 8. | EPS side abnormal |  |
|  |  | EPS_LineVoltS_Loss | 9. |  |  |
|  |  | EPS_LineVoltT_Loss | 10. |  |  |
|  |  | reserved | 11. |  |  |
|  |  | reserved | 12. |  |  |
|  |  | reserved | 13. |  |  |
|  |  | reserved | 14. |  |  |
|  |  | reserved | 15. |  |  |

| System fault word3 | Byte6 | BatTerminalReversed | 0. | BAT Side abnormal |  |
| --- | --- | --- | --- | --- | --- |
|  |  | BatTerminalOpen BMS Battery Open | 1. |  |  |
|  |  | BatteryVoltageLow | 2. |  |  |
|  |  | BatteryVoltageHigh | 3. |  |  |
|  |  | reserved | 4. |  |  |
|  |  | reserved | 5. |  |  |
|  |  | reserved | 6. |  |  |
|  |  | reserved | 7. |  |  |
|  | Byte7 | reserved | 8. | BAT Side abnormal |  |
|  |  | reserved | 9. |  |  |
|  |  | reserved | 10. |  |  |
|  |  | reserved | 11. |  |  |
|  |  | reserved | 12. |  |  |
|  |  | reserved | 13. |  |  |
|  |  | reserved | 14. |  |  |
|  |  | reserved | 15. |  |  |
| System fault word4 | Byte8 | reserved | 0. | PV Side Abnormal |  |
|  |  | reserved | 1. |  |  |
|  |  | reserved | 2. |  |  |
|  |  | reserved | 3. |  |  |
|  |  | reserved | 4. |  |  |
|  |  | PV1_VoltLowWarn | 5. |  |  |
|  |  | PV2-VoltLowWarn | 6. |  |  |
|  |  | reserved | 7. |  |  |
|  | Byte9 |  | 8. | PV Side Abnormal |  |
|  |  |  | 9. |  |  |
|  |  |  | 10. |  |  |
|  |  | reserved | 11. |  |  |
|  |  | reserved | 12. |  |  |
|  |  | reserved | 13. |  |  |
|  |  | reserved | 14. |  |  |
|  |  | reserved | 15. |  |  |
| System fault word5 | Byte10 | NEDetectFault | 0. | Sytem fault |  |
|  |  | PVISOFault | 1. |  |  |
|  |  | reserved | 2. |  |  |
|  |  | BusVoltHighFault_ISR | 3. |  |  |
|  |  | BusSampleFault | 4. |  |  |
|  |  | UHCTFault | 5. |  |  |
|  |  | AComFault | 6. |  |  |
|  |  | BComFault | 7. |  |  |

|  | Byte11 | BusVoltHighFault_TZ | 8. | Sytem fault |  |
| --- | --- | --- | --- | --- | --- |
|  |  | AuotTestFault | 9. |  |  |
|  |  | DCIHigh | 10. |  |  |
|  |  | NTCOpenFault | 11. |  |  |
|  |  | reserved | 12. |  |  |
|  |  | BBHeatsink_TempOver | 13. |  |  |
|  |  | BBOCP_FaultISR | 14. |  |  |
|  |  | BBOCP_FaultTZ | 15. |  |  |
| System fault word6 | Byte12 | PV1_VoltHighFault | 0. | Sytem fault |  |
|  |  | PV2_VoltHighFault | 1. |  |  |
|  |  | BTHeatsink_Overtemp | 2. |  |  |
|  |  | INVHeatsink_Overtemp | 3. |  |  |
|  |  | reserved | 4. |  |  |
|  |  | reserved | 5. |  |  |
|  |  | reserved | 6. |  |  |
|  |  | reserved | 7. |  |  |
|  | Byte13 | BoostDriver1Warn | 8. | System warning |  |
|  |  | BoostDriver2Warn | 9. |  |  |
|  |  | WARN104 | 10. |  |  |
|  |  | PV1_ShortFault | 11. |  |  |
|  |  | PV2_ShortFault | 12. |  |  |
|  |  | Meter Comm Loss | 13. |  |  |
|  |  | PairingTimeOut | 14. |  |  |
|  |  | CT LN Reversed | 15. |  |  |
| System fault word6 | Byte14 | BMS COM Fault | 0. |  |  |
|  |  | BMS Error: xxx | 1. |  |  |
|  |  | Battery reversed | 2. |  |  |
|  |  | BAT NTC Open | 3. |  |  |
|  |  | SS Timeout | 4. |  |  |
|  |  | Bat voltage low | 5. |  |  |
|  |  | Bat T Outrange | 6. |  |  |
|  |  | BATOutput_Overload | 7. |  |  |
|  | Byte15 | reserved | 8. |  |  |
|  |  | reserved | 9. |  |  |
|  |  | reserved | 10. |  |  |
|  |  | reserved | 11. |  |  |
|  |  | reserved | 12. |  |  |
|  |  | reserved | 13. |  |  |
|  |  | reserved | 14. |  |  |
|  |  | reserved | 15. |  |  |
| System fault word7 |  | reserved |  |  |  |

# Set address

Refer to the Inverter user manual.  Always is :

Knock the pv inverter to let the lcd display to the “COM Addr: xxx”, then double knock, if displays “Move”, you should another double knock, until it displays a address number, then you can give a single knock to change the address, this address will be remembered when the lcd backlight off.

# Notice

- It can drive mostly 32 pv inverters for one rs485 comport.

- There are only read input and hold registers commands even the newest version.

- App user could only care the input register.

- App user could not care the holding registers.

- Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing the other registers;