## Sheet1
Growatt Inverter Modbus RTU Protocol_II
V1.05
2018-04-19
Growatt New Energy CO.,LTD
No. | Version | Date | Notice | Signature
1 | V1.00 | 2017-03-27 | The first version | May
2 | V1.01 | 2017-04-28 | Modify max data length to 125 words. | May
Add Input reg50-52 for line voltage
3 | V1.02 | 2017-07-18 | Add SP storage and offline inverter message | May
Modify Input reg. First and Second group sequence
Modify Holding register First group sequence
Modigy stringPID fault code and warning code
Modify fifth and sixth group for Gridfault record
4 | V1.03 | 2017-08-02 | Modify Hybrid Abnoram/Fault/warning bit definition | Ericxiong
5 | V1.04 | 2018-03-29 | Add Inputing178,179,180,181 for Warning Value1,Warning Value2,Warning Value3 and
FaultCode
Add Holding240 for aging Check Step
Add Inputing112 for INV warn code
Add Inputing113 for real Power Percent
Add Inputing114 for inv start delay time
Add Inputing115 for INV All Fault Code
Add holding267-298 for DSP debugdata address
Add Inputing182-197 for DSP debugdata value
Add Inputing198 for USB Aging Test OK flag
Add Inputing199 for USB Flash Aging Test OK flag
Add Inputing200 for ISO check value
Add holding299 for Active Over load Enable
Add Inputing 201-203 for R、S、T DCI Current
Add Inputing204 for PID Bus Volt
Add Inputing205 for GFCI Curr
Add Inputing 206-227 for APF/SVG information
Add holding 300 for SVG/APF mode
6 | V1.05 | 2018-06-28 | Add InputingReg 525~529 for Setting up GPRS IP Address | huo.zhao
Add HodlingReg 90 as the step to set up GPRS IP
Address
7 | V1.06 | 2018.7.5 | Add HoldingReg 301 for BDEW LVRT K Factor | Yimin.Yang
V1.00 2017-03-17:
First version
V1.01 2017-4-28
Modify max data length to 125 words. Add Inputreg 50-52 for line voltage
V1.05 2018-6-28
Add InputingReg 525~529 for Setting up GPRS IP Address
Add HodlingReg 90 as the step to set up GPRS IP Address
catalog
1 Data format ............................................................................................................................ 4
2 Command Format ................................................................................................................... 4
3 Device Message Transmission Mode / Framing ..................................................................... 7
4 Register map ........................................................................................................................... 8
4.1 Holding Reg ...................................................................................................................... 8
4.2
Input Reg ....................................................................................................................... 25
5 Set address ........................................................................................................................... 54
6 Notice ................................................................................................................................... 55
1 Data format
Valid slave device addresses are in the range of 0 – 254 decimal.
The individual slave devices are assigned addresses in the range of 1 – 254.
0 is the broadcast address
It is 16bits (two bytes) unsigned integer for each holding and input register;
2 Command Format
Function 3 Read holding register
Response Error:
11 0x80¦0x03 Errornum CRC (Errornum as a byte)
Function 4 Read input register
Response Error:
11 0x80¦0x04 Errornum CRC (Errornum as a byte)
Function 6 Preset single register
Response Error:
11 0x80¦0x06 Errornum CRC (Errornum as a byte)
Function 16 Preset multiple register
Response Error:
11 0x80¦0x10 Errornum CRC (Errornum as a byte)
3 Device Message Transmission Mode / Framing
RTU Mode
When controllers are setup to communicate on a Modbus network using RTU (Remote Terminal Unit) mode, each 8–bit byte in a message contains two 4–bit hexadecimal characters. Each message must be transmitted in a continuous stream.
The format for each byte in RTU mode is:
Coding System: 8–bit binary, hexadecimal 0–9, A–F
Two hexadecimal characters contained in each
8–bit field of the message
Bits per Byte:
1 start bit
8 data bits, least significant bit sent first
None parity
1 stop bit
Error Check Field: Cyclical Redundancy Check (CRC)
The baud rate of the transmission is:
Default Baud Rate: 9600 bps
Can be set through hold register 22
Minimum CMD period (RS485 Time out): 850ms.
Wait for minimum 850ms to send a new CMD after last CMD. Suggestion is 1s;
Maximum Data Length Define:
Maximum read data length is 125 words in read command;
Maximum update data length is 125 words in preset command;
Note:
Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing other registers;
9 | Fw version H | Firmware version (high) |  |  | ASCII
10 | Fw version M | Firmware version
(middle)
11 | Fw version L | Firmware version (low)
12 | Fw version2 | Control Firmware version (high) |  |  | ASCII
H
13 | Fw version2 | Control Firmware version (middle)
M
14 | Fw version2 L | Control Firmware version (low)
15 | LCD language | LCD language | W | 0-5
16 | CountrySelec ted | Country Selected or not | W | 0: need to select;
1: have
selected
17 | Vpv start | Input start voltage | W |  | 0.1V
18 | Time start | Start time | W |  | 1s
19 | RestartDelay | Restart Delay Time after fault back; | W |  | 1s
Time
20 | wPowerStart | Power start slope | W | 1-1000 | 0.1%
Slope
21 | wPowerResta rtSlopeEE | Power restart slope | W | 1-1000 | 0.1%
22 | wSelectBaud | Select communication baudrate 0: 9600bps | W | 0-1 |  | 0
| rate | 1:38400bps
23 | Serial NO. 5 | Serial number 5 |  |  | ASCII
24 | Serial No. 4 | Serial number 4
25 | Serial No. 3 | Serial number 3
26 | Serial No. 2 | Serial number 2
27 | Serial No. 1 | Serial number 1
28 | Module H | Inverter Module (high) |  | &*5
29 | Module L | Inverter Module (low) |  | &*5
30 | Com Address | Communicate address | W | 1-254 |  | 1
31 | FlashStart | Update firmware | W | 1
32 | Reset User | Reset User Information | W | 0x0001
Info
33 | Reset to | Reset to factory | W | 0x0001
factory
34 | Manufacture | Manufacturer information (high) |  |  | ASCII
r Info 8
35 | Manufacture | Manufacturer information (middle)
r Info 7
36 | Manufacture | Manufacturer information (low)
r Info 6
37 | Manufacture | Manufacturer information (high)
r Info 5
38 | Manufacture | Manufacturer information (middle)
r Info 4
39 | Manufacture | Manufacturer information (low)
r Info3
40 | Manufacture | Manufacturer information (low)
r Info 2
41 | Manufacture | Manufacturer information (high)
r Info 1
42 | reserved | [5 empty] | reserved
43 | DTC | Device Type Code |  | &*6
44 | TP | Input tracker num and output phase num |  | Eg:0x0203 is two
MPPT and 3ph output
45 | Sys Year | System time-year | W | Year offset is 0 |  |  | Local time
46 | Sys Month | System time- Month | W
47 | Sys Day | System time- Day | W
48 | Sys Hour | System time- Hour | W
49 | Sys Min | System time- Min | W
50 | Sys Sec | System time- Second | W
51 | Sys Weekly | System Weekly | W | 0-6
52 | Vac low | Grid voltage low limit protect | W |  | 0.1V
53 | Vac high | Grid voltage high limit protect | W |  | 0.1V
54 | Fac low | Grid frequency low limit protect | W |  | 0.01
Hz
55 | Fac high | Grid high frequency limit protect | W |  | 0.01
Hz
56 | Vac low 2 | Grid voltage low limit protect 2 | W |  | 0.1V
57 | Vac high 2 | Grid voltage high limit protect 2 | W |  | 0.1V
58 | Fac low 2 | Grid frequency low limit | W |  | 0.01
|  |  | protect 2 |  |  | Hz
59 | Fac high 2 |  | Grid high frequency limit protect 2 | W |  | 0.01
Hz
60 | Vac low 3 |  | Grid voltage low limit protect 3 | W |  | 0.1V
61 | Vac high 3 |  | Grid voltage high limit protect 3 | W |  | 0.1V
62 | Fac low 3 |  | Grid frequency low limit protect 3 | W |  | 0.01Hz
63 | Fac high 3 |  | Grid frequency high | W |  | 0.01Hz
limit protect 3
64 | Vac low C |  | Grid low voltage limit connect to Grid | W |  | 0.1V
65 | Vac high C |  | Grid high voltage limit connect to Grid | W |  | 0.1V
66 | Fac low C |  | Grid low frequency limit connect to Grid | W |  | 0.01
Hz
67 | Fac high C |  | Grid high frequency limit connect to Grid | W |  | 0.01
Hz
68 | Vac time | low1 | Grid voltage low limit protect time 1 | W |  | Cycle
69 | Vac time | high1 | Grid voltage high limit protect time 1 | W |  | Cycle
70 | Vac time | low2 | Grid voltage low limit protect time 2 | W |  | Cycle
71 | Vac time | high2 | Grid voltage high limit protect time 2 | W |  | Cycle
72 | Fac time | low1 | Grid frequency low limit protect time 1 | W |  | Cycle
73 | Fac time | high1 | Grid frequency high | W |  | Cycle
limit protect time 1
74 | Fac time | low2 | Grid frequency low limit protect time 2 | W |  | Cycle
75 | Fac time | high2 | Grid frequency high | W |  | Cycle
limit protect time 2
76 | Vac time | low3 | Grid voltage low limit protect time 3 | W |  | Cycle
77 | Vac time | high3 | Grid voltage high limit protect time 3 | W |  | Cycle
78 | Fac time | low3 | Grid frequency low limit protect time 3 | W |  | Cycle
79 | Fac | high3 | Grid frequency high | W |  | Cycle
| time | limit protect time 3
80 | U10min | Volt protection for 10 min | W |  | 0.1V | 1.1Vn
81 | PV Voltage | PV Voltage High Fault | W |  | 0.1V
High Fault
82 | FW Build No. | FW Build version |  |  | ASCII
5
83 | FW Build No. | FW Build version |  |  | ASCII
4
84 | FW Build No. | DSP1 FW Build No. |  |  | ASCII
3
85 | FW Build No. | DSP2 FW Build No. |  |  | ASCII
2
86 | FW Build No. | M3 FW Build No. |  |  | ASCII
1
87 | FW Build No. | CPLD FW Build No. |  |  | ASCII
0
88 | ModbusVersi on | Modbus Version |  | Eg：207 is | Int(16b
|  |  |  | V2.07 | its)
89 | PFModel | Set PF function Model | W
0: PF=1
1: PF by set
2: default PF line
3: User PF line
4: UnderExcited (Inda)
Reactive Power
5: OverExcited(Capa)
Reactive Power
6：Q(v)model
90 | GPRS IP Flag | read:1;Set GPRS IP | W | write:2 read:0~3
Successed
Write:2;Read GPRS IP
Successed
91 | FreqDerateSt | Frequency derating start point | W |  | 0.01HZ
art
92 | FLrate | Frequency – load limit rate | W | 0-100 | 10time
s
93 | V1S | CEI021 V1S Q(v) | W | V1S<V2S | 0.1V
94 | V2S | CEI021 V2S Q(v) | W |  | 0.1V
95 | V1L | CEI021 V1L Q(v) | W | V1L<V1S | 0.1V
96 | V2L | CEI021 V2L Q(v) | W | V2L<V1L | 0.1V
97 | Qlockinpowe | Q(v) lock in active power of CEI021 | W | 0-100 | Percen
| r |  |  |  | t
98 | QlockOutpo wer | Q(v) lock Out active power of CEI021 | W | 0-100 | Percen
t
99 | LIGridV | Lock in gird volt of | W | nVn | 0.1V
CEI021 PF line
100 | LOGridV | Lock out gird volt of | W | nVn | 0.1V
CEI021 PF line
101 | PFAdj1 | PF adjust value 1 |  | 4096 is 1
102 | PFAdj2 | PF adjust value 2 |  | 4096 is 1
103 | PFAdj3 | PF adjust value 3 |  | 4096 is 1
104 | PFAdj4 | PF adjust value 4 |  | 4096 is 1
105 | PFAdj5 | PF adjust value 5 |  | 4096 is 1
106 | PFAdj6 | PF adjust value 6 |  | 4096 is 1
107 | QVRPDelayTi meEE | QV Reactive Power | W | 0-30 | 1S | 3S
delaytime
108 | OverFDeratD elayTimeEE | Overfrequency deratin g delaytime | W | 0-20 | 50ms | 0
109 | QpercentMa | Qmax for Q(V) curve | W | 0-1000 | 0.1%
x
110 | PFLineP1_LP | PF limit line point 1 load percent | W | 0-255 | percen |  | 255 means no this point
t
111 | PFLineP1_PF | PF limit line point 1 power factor | W | 0-20000
112 | PFLineP2_LP | PF limit line point 2 load percent | W | 0-255 | percen |  | 255 means no this point
t
113 | PFLineP2_PF | PF limit line point | W | 0-20000
2power factor
114 | PFLineP3_LP | PF limit line point 3 load percent | W | 0-255 | percen |  | 255 means no this point
t
115 | PFLineP3_PF | PF limit line point 3 power factor | W | 0-20000
116 | PFLineP4_LP | PF limit line point 4 load percent | W | 0-255 | percen |  | 255 means no this point
t
117 | PFLineP4_PF | PF limit line point 4 power factor | W | 0-20000
118 | BLVersion1 | Boot loader version1 | R |  |  |  | Reserved
119 | BLVersion2 | Boot loader version2 | R |  |  |  | Reserved
120 | BLVersion3 | Boot loader version3 | R |  |  |  | Reserved
121 | BLVersion4 | Boot loader version4 | R |  |  |  | Reserved
122 | INV-Lng | Inverter Longitude | W
123 | INV-Lat | Inverter Latitude | W
124 | TrakerModel | 2 Traker Model | W | 0,1,2 | 0:Inde pende
nt
1:DC
Source
2:Paral
lel
Second group
125 | INV Type-1 | Inverter type-1 | R |  | ASCII |  | Reserved
126 | INV Type-2 | Inverter type-2 | R |  | ASCII
127 | INV Type-3 | Inverter type-3 | R |  | ASCII
128 | INV Type-4 | Inverter type-4 | R |  | ASCII
129 | INV Type-5 | Inverter type-5 | R |  | ASCII
130 | INV Type-6 | Inverter type-6 | R |  | ASCII
131 | INV Type-7 | Inverter type-7 | R |  | ASCII
132 | INV Type-8 | Inverter type-8 | R |  | ASCII
…… | [6 empty] | Reserved
200 | [6 empty] | Reserved
201 | PID Working | PID Working Model | W | 0:Automa
| Model |  |  | tic 1:
Continual 2:
Overnight
202 | PID On/Off | PID On/Off Control | W | 0:On 1:Off
Ctrl
203 | PID Volt | PID Output Voltage | W | 300~1000 | V
| Option | Option
…… | [6 empty] | Reserved
229 | [6 empty] | Reserved
230~249 for growatt debug setting
230 | Island | Island Disable or not. | W | 0,1 |  | 0
| Disable | 1:disable 0:Enable
231 | Fan Check | Start Fan Check | W | 1
232 | EnableNLine | Enable N Line of grid | W | 1 |  | 0
233 | wCheckHard ware | wCheckHardware
Bit0: GFCIBreak;
Bit1:SPSDamage
Bit8:EepromReadWarnin g
Bit9:EEWriteWarning
……
234 | wCheckHard ware2 | [5 empty] | reserved
235 | ubNToGNDD | Dis/enable N to GND | W | 1:enable |  | 1
| etect | detect function |  | 0:disable
236 | NonStdVacEn able | Enable/Disable | W | 0-1; |  | 0 | 0:Disable;
|  | Nonstandard |  |  |  |  | 1:Enable;
Grid voltage range
237 | uwEnableSpe | Disablse/enable appointed spec setting | W | 1:enable | Binary | 0x000 | Bit 0: Hungary
| cSet |  |  | 0:disable |  | 0
238 | Fast MPPT | About Fast mppt |  | 0,1,2 |  | 0 | Reserved
enable
…
240 | Check Step |  | W
…… | [6 empty] | Reserved
249 | [6 empty] | Reserved
250 | Curve analysis | Enable a curve analysis of a road | W | 0~1 | 0
251 | Faultrecorder | Preset Record | W | 1001~199 | 1001
| Wave1 | Waveform Number |  | 9
252 | Faultrecorder | Preset Record | W | 1001~199 | 1002
| Wave2 | Waveform Number |  | 9
253 | Faultrecorder | Preset Record | W | 1001~199 | 1003
| Wave3 | Waveform Number |  | 9
254 | Faultrecorder | Preset Record | W | 1001~199 | 1004
| Wave4 | Waveform Number |  | 9
255 | Faultrecorder | Preset Record | W | 1~999 | 1
| Wave5 | Waveform Number
256 | Faultrecorder | Preset Record | W | 1~999 | 2
| Wave6 | Waveform Number
257 | Faultrecorder | Preset Record | W | 1~999 | 3
| Wave7 | Waveform Number
258 | Faultrecorder | Preset Record | W | 1~999 | 4
| Wave8 | Waveform Number
259 | FaultRecorde rEnable | FaultRecorderEnable | W | 1~100 | 0
260 | recorderWav e1 | Preset Record | W | 1~1999 | 1
Waveform Number
261 | recorderWav e2 | Preset Record | W | 1~1999 | 2
Waveform Number
262 | recorderWav e3 | Preset Record | W | 1~1999 | 3
Waveform Number
263 | recorderWav e4 | Preset Record | W | 1~1999 | 4
Waveform Number
264 | WaveRecord erEnable | Real-time waveform | W | 0~1 | 0
recording
265 | Harmonic | Harmonic Check Enable | W | 0~1 | 0
Check Enable
266 | Impedance | Impedance Enable | W | 0~1 | 0
Enable
267 | 067 Debug 1 | 067 Debug 1 _H
_H
268 | 67 | 067 Debug1_L
Debug1_L
269 | 067 Debug2_H | 067 Debug2_H
270 | 67 | 067 Debug2_L
Debug2_L
271 | 067 Debug3_H | 067 Debug3_H
272 | 67 | 067 Debug3_L
Debug3_L
273 | 067 Debug4_H | 067 Debug4_H
274 | 67 | 067 Debug4_L
Debug4_L
275 | 067 Debug5_H | 067 Debug5_H
276 | 67 | 067 Debug5_L
Debug5_L
277 | 067 Debug6_H | 067 Debug6_H
278 | 67 | 067 Debug6_L
Debug6_L
279 | 067 Debug7_H | 067 Debug7_H
280 | 67 | 067 Debug7_L
Debug7_L
281 | 067 Debug8_H | 067 Debug8_H
282 | 67 | 067 Debug8_L
Debug8_L
283 | 075 Debug 1 | 075 Debug 1 _H
_H
284 | 75 | 075 Debug1_L
Debug1_L
285 | 075 Debug2_H | 075 Debug2_H
286 | 75 | 075 Debug2_L
Debug2_L
287 | 075 Debug3_H | 075 Debug3_H
288 | 75 | 075 Debug3_L
Debug3_L
289 | 075 Debug4_H | 075 Debug4_H
290 | 75 | 075 Debug4_L
Debug4_L
291 | 075 Debug5_H | 075 Debug5_H
292 | 75 | 075 Debug5_L
Debug5_L
293 | 075 Debug6_H | 075 Debug6_H
294 | 75 | 075 Debug6_L
Debug6_L
295 | 075 Debug7_H | 075 Debug7_H
296 | 75 | 075 Debug7_L
Debug7_L
297 | 075 Debug8_H | 075 Debug8_H
298 | 75 | 075 Debug8_L
Debug8_L
299 | bActiveOverl oadEnable | Active Over load Enable
300 | bSvgApfMod | Svg Apf Mode |  | 低4位：0：
| e |  |  | SVG/APF，
1 ：
APF/SVG,
2：SVG, 3： APF
高 4 位：0：全天模式 1：夜间模
式
301 |  | bBdewLvrtKF actor | [8 empty] | BDEW LVRT K Factor | [8 empty] | 0-4
待确定部分
360 |  | 232T485Ena | [8 empty] | 232T485Enable | [6 empty] | W |  | 0: Disable;
|  | ble | [17 empty] | 1: Enable
361 |  | Decrease | [8 empty] | Decrease output watt | [7 empty] | W
Power H
362 |  | Decrease | [8 empty] | Decrease output watt | [6 empty] | W | [5 empty] | 0.1W
Power L
363 |  | Increase | [8 empty] | Increase output watt | [6 empty] | W
Power H
364 |  | Increase | [8 empty] | Increase output watt | [6 empty] | W | [5 empty] | 0.1W
Power L
365 |  | Factory | [8 empty] | The ODM Info code
366 |  | Vac start b | [7 empty] | y | Vac start adjust by pf | [6 empty] | W | [5 empty] | 0.1V
pf
367 |  | PF of va | [7 empty] | c | Max pf of adjust Vac | [6 empty] | W | [7 empty] | 10000
limit
368 |  | LCMDTest | [8 empty] | Local command test | [7 empty] | W | 1 to test
369 |  | ReactiveRate | [8 empty] | Reactive Rate in LVFRT | [7 empty] | W | 0-100 | [5 empty] | 2
370 |  | LVFRT_LV1 | [8 empty] | LVFRT low fault value 1 | [7 empty] | W |  |  |  |  | 0.1V
371 |  | LVFRT_LT1 | [8 empty] | LVFRT low fault time |  |  |  |  | 1 |  |  | W |  |  |  |  | 1ms
372 |  | LVFRT_LV2 | [8 empty] | LVFRT low fault value 2 | [7 empty] | W |  |  |  |  | 0.1V
373 |  | LVFRT_LT2 | [8 empty] | LVFRT low fault time |  |  |  |  | 2 |  |  | W |  |  |  |  | 1ms
374 |  | LVFRT_LV3 | [8 empty] | LVFRT low fault value 3 | [7 empty] | W |  |  |  |  | 0.1V
375 |  | LVFRT_LT3 | [8 empty] | LVFRT low fault time |  |  |  |  | 3 |  |  | W |  |  |  |  | 1ms
376 |  | LVFRT_LV4 | [8 empty] | LVFRT low fault value 4 | [7 empty] | W |  |  |  |  | 0.1V
377 |  | LVFRT_LT4 | [8 empty] | LVFRT low fault time |  |  |  |  | 4 |  |  | W |  |  |  |  | 1ms
378 |  | LVFRT_HV1 | [8 empty] | LVFRT high fault value 1 | [7 empty] | W |  |  |  |  | 0.1V
379 |  | LVFRT_HT1 | [8 empty] | LVFRT high fault time 1 | [7 empty] | W |  |  |  |  | 1ms
380 |  | wLoadDerate | [8 empty] | Load derate start ac | [8 empty] | 1.05Vn~1. |  |  |  | 0.1V
|  | StartVolt | [8 empty] | voltage | [8 empty] | 2Vn
381 |  | SpecPasswor | [8 empty] | Unlock or set | [7 empty] | W | 0:unlock , | [5 empty] | 2
|  | dType | [8 empty] | Specpassword | [8 empty] | auto loc |  |  | k
in 5
minute;
1:change
pw
(should
unlock
first)，
[20 empty] | 2：lock |  |  | ,
&*7
382 |  | SpecPasswor | [6 empty] | SpecPassword3 | [8 empty] | W |  | For the |  |  |  |  | ASCII | XX
|  | d3 | [17 empty] | spec
setting
change
383 |  | SpecPasswor | [6 empty] | SpecPassword2 | [8 empty] | W |  | .. |  |  |  |  | ASCII | XX
d2
384 |  | SpecPasswor | [6 empty] | SpecPassword1 | [9 empty] | W | .. |  |  |  |  | ASCII | XX
d1
385 |  | DCIshift | [6 empty] | DCI offset | [10 empty] | Center is | [6 empty] | Reserved
30000
386 |  | DCIAdj | [6 empty] | DCI adjust | [10 empty] | Center is | [6 empty] | Reserved
2000
387 |  | IniEEPROM | [6 empty] | IniEEPROM | [9 empty] | W | 0xFF | [6 empty] | Reserved
388 |  | Balance 1 | [6 empty] | Phaseflag¦ErrorCode | [9 empty] | W | [7 empty] | Reserved
389 |  | Balance 2 | [6 empty] | Power H | [9 empty] | W | [7 empty] | Reserved
390 |  | Balance 3 | [6 empty] | Power L | [9 empty] | W | [7 empty] | Reserved
391 |  | bHighACVDe | [5 empty] | r | High ac voltage | [7 empty] | load |  | W | 20 |  |  |  |  | 0-100
|  | ateSlope | [6 empty] | derating slope
392 |  | BlaneceMod | [6 empty] | BlaneceModel | [8 empty] | W |  | 2023-03-01
el
393 |  | BalencePhas | [6 empty] | BalencePhase | [8 empty] | W |  | 2023-03-01
e
394 |  | DCIshift |  |  | 2 |  |  |  | DCI offset 2 | [8 empty] | W |  | Center is | [6 empty] | Reserved
30000
395 |  | DCIshift |  |  | 3 |  |  |  | DCI offset 3 | [9 empty] | W | Center is | [6 empty] | Reserved
30000
396 |  | EnergyLimitE | [6 empty] | Output Energy L | [7 empty] | imit | R |  | 1 is | [6 empty] | Reserved
|  | nable | [6 empty] | Enable | [10 empty] | enable
397 |  | EnergyRemai | [6 empty] | Output Energy L | [7 empty] | imit | W |  | 0.1kWh | [6 empty] | Reserved
|  | n H | [6 empty] | value High
398 |  | EnergyRemai | [6 empty] | Output Energy L | [7 empty] | imit | W |  | 0.1kWh | [6 empty] | Reserved
|  | n L | [6 empty] | value low
399 |  | TrakerModel | [6 empty] | 2 Traker Model | [9 empty] | W | 0,1,2 | [6 empty] | Reserved
400 |  | PMchec |  |  | k |  |  |  | Growatt Resaved | [9 empty] | W | [7 empty] | Reserved
401 |  | INVWorkMo | [6 empty] | INV work mode set | [9 empty] | W | 0:default | [5 empty] | 0
|  | de | [17 empty] | 1:CV
Mode
2:CC
Mode
3:CP
Mode
402 |  | PV1VoltSet | [5 empty] | pv1 voltage set when CV |  |  |  |  | W |  | StartPVVo
[8 empty] | Mode was chosed | [6 empty] | lt-HighPV
Volt
403 |  | PV2VoltSet | [5 empty] | Pv2 voltage set when CV | [5 empty] | W | StartPVVo
[8 empty] | Mode was chosed | [6 empty] | lt-HighPV
Volt
404 |  | BT1CurrRefS | [5 empty] | BT1 current set when CC | [5 empty] | W | 0-MaxBTC
|  | et | [5 empty] | Mode was chosed | [6 empty] | urrent
405 |  | BT2CurrRefS | [5 empty] | BT2current set when CC | [5 empty] | W | 0-MaxBTC
|  | et | [5 empty] | Mode was chosed | [6 empty] | urrent
406 |  | WattACVRec | [5 empty] | Delay time for powe |  |  |  | r c |  | W | 3-90S
|  | overDelayT |  |  |  | i |  | recovering when a
|  | me | [5 empty] | voltage getting normal
407 |  | TxDataInterv | [5 empty] | TxDataInterval | [5 empty] | W | 1~600 |  |  | 0.1
[21 empty] | 50 | 5mins
|  | al | [15 empty] | mins
408 |  | ChkCode | [5 empty] | Datalogger Check Code |  |  |  |  | R |  |  |  |  | ASCII
|  | NO.1 | [5 empty] | 1
409 |  | ChkCode | [5 empty] | Datalogger Check Code |  |  |  |  | R |  |  |  |  | ASCII
|  | NO.2 | [5 empty] | 2
500 |  | ChkCode | [5 empty] | Datalogger Check Code |  |  |  |  | R |  |  |  |  | ASCII
|  | NO.3 | [5 empty] | 3
501 |  | bISLDShiftDel | [5 empty] | Growatt Resaved |  |  |  |  | W | [8 empty] | Reserved
taEE
502 |  | bLowPointer | [5 empty] | Growatt Resaved | [5 empty] | W | [7 empty] | Reserved
505 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.1 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
506 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.2 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
507 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.3 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
508 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.4 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
509 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.5 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
510 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.6 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
511 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.7 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
512 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.8 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
513 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.9 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
514 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.10 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
515 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.11 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
516 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.12 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
517 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.13 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
518 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.14 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
519 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.15 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
520 |  | GPRSIP Addr | [5 empty] | GPRSIP Addr No.16 |  |  |  |  | W |  | 0~65536 |  |  | ASCII
521 | GPRSIP Addr | GPRSIP Addr No.17 |  | W | 0~65536 | ASCII
522 | GPRSIP Addr | GPRSIP Addr No.18 |  | W | 0~65536 | ASCII
523 | GPRSIP Addr | GPRSIP Addr No.19 |  | W | 0~65536 | ASCII
524 | GPRSIP Addr | GPRSIP Addr No.20 |  | W | 0~65536 | ASCII
525 | GPRSIP Addr | GPRSIP Addr No.21 |  | W | 0~65536 | ASCII
526 | GPRSIP Addr | GPRSIP Addr No.22 |  | W | 0~65536 | ASCII
527 | GPRSIP Addr | GPRSIP Addr No.23 |  | W | 0~65536 | ASCII
528 | GPRSIP Addr | GPRSIP Addr No.24 |  | W | 0~65536 | ASCII
529 | GPRSIP Addr | GPRSIP Addr No.25 |  | W | 0~65536 | ASCII
Six group for Storage Power
Register NO. | Variable | Description |  | Write or not | Value | Unit | Initial | Note
| Name | [5 empty] | value
1000 | Float charge current limit | When charge current battery need is lower than this value, enter into float charge |  | W |  | 0.1A | 600 | CC current
1001 | PF CMD | Set the following 19-22 CMD will be memory or not(1/0), if not, these settings are the initial value. |  | W | 0or1, |  | 0 | Means these settings will be acting or not when next power on
memory
state
1002 | VbatWarning | LoadPercent(only lead-Acid): |  | W |  | 0.1V | <20%
|  | <20% |  |  |  |  | 48.0VD
|  | 20%~50% |  |  |  |  | C
|  | >50% |  |  |  |  | [20%,5
0%]
47.0VD
C
>50%
45.0V
1003 | VbatWarnClr | LoadPercent(only lead-Acid): |  | W |  | 0.1V | <20%
|  | <20% |  |  |  |  | 49.0VD
|  | 20%~50% |  |  |  |  | C
|  | >50% |  |  |  |  | [20%,5
0%]
48.0VD
C
>50%
45.5V
1004 | Vbat stop for discharge | Should stop discharge when lower than this voltage(only lead-Acid): |  | W |  | 0.01V | <20%
46.0VD
C
|  | <20% |  |  |  | [20%,5
|  | 20%~50% |  |  |  | 0%]
|  | >50% |  |  |  | 44.8VD
C
>50%
44.2V
1005 | Vbat stop for charge | Should stop charge when higher than this voltage | W |  | 0.01V | 5800
1006 | Vbat start for discharge | Should not discharge when lower than this voltage | W |  | 0.01V | 4800
1007 | Vbat start for charge | Should charge when lower than this voltage | W |  | 0.01V | 5300 | reserved
1008 | FlashStart | Update firmware | W | 0x0001:o wn 0X0100: TIC2000
1009 | Bat temp | Battery temperature lower limit for discharge | W | 0-200:0-2 | 0.1℃ | 1170
| lower limit d |  |  | 0℃
1000-140
0：-40-0℃
1010 | Bat temp | Battery temperature upper limit for discharge | W | 200-1000 | 0.1℃ | 420
upper limit d
1011 | Bat temp | Battery temperature lower limit for charge | W | 0-200:0-2 | 0.1℃ | 30
| lower limit c |  |  | 0℃
1000-140
0：-40-0℃
1012 | Bat temp | Battery temperature upper limit for charge | W | 200-1000 | 0.1℃ | 370
upper limit c
1013 | ForcedDischa | time- Min | W | 0-60 | 1 | 0
rge Min
Start1
1014 | ForcedDischa | time- Hour | W | 0-24 | 1 | 0
rge Hour
Start1
1015 | ForcedDischa | time- Min | W | 0-60 | 1 | 0
rge Min
Start2
1016 | ForcedDischa | time- Hour | W | 0-24 | 1 | 0
rge Hour
Start2
1017 | ForcedDischa | time- Min | W | 0-60 | 1 | 0
rge Min
Start3
1018 | ForcedDischa | time- Hour | W | 0-24 | 1 | 0
rge Hour
Start3
1019 | ForcedDischa | time- Min | W | 0-60 |  | 0
rge Min
Stop1
1020 | ForcedDischa | time- Hour | W | 0-24 |  | 0
rge Hour
Stop1
1021 | ForcedDischa | time- Min | W | 0-60 |  | 0
rge Min
Stop2
1022 | ForcedDischa | time- Hour | W | 0-24 |  | 0
rge Hour
Stop2
1023 | ForcedDischa | time- Min | W | 0-60 |  | 0
rge Min
Stop3
1024 | ForcedDischa | time- Hour | W | 0-24 |  | 0
rge Hour
Stop3
1025 | ForcedCharg e Min Start1 | time- Min | W | 0-60 | 1 | 0
1026 | ForcedCharg e Hour Start1 | time- Hour | W | 0-24 | 1 | 0
1027 | ForcedCharg e Min Start2 | time- Min | W | 0-60 | 1 | 0
1028 | ForcedCharg e Hour Start2 | time- Hour | W | 0-24 | 1 | 0
1029 | ForcedCharg e Min Start3 | time- Min | W | 0-60 | 1 | 0
1030 | ForcedCharg e Hour Start3 | time- Hour | W | 0-24 | 1 | 0
1031 | ForcedCharg e Min Stop1 | time- Min | W | 0-60 | 1 | 0
1032 | ForcedCharg e Hour Stop1 | time- Hour | W | 0-24 | 1 | 0
1033 | ForcedCharg e Min Stop2 | time- Min | W | 0-60 | 1 | 0
1034 | ForcedCharg e Hour Stop2 | time- Hour | W | 0-24 | 1 | 0
1035 | ForcedCharg e Min Stop3 | time- Min | W | 0-60 | 1 | 0
1036 | ForcedCharg e Hour Stop3 | time- Hour | W | 0-24 | 1 | 0
1037 |  | Use the CTMode to Choose RFCT \ Cable | W | 2:METER 1:cWirele ssCT |  | 0
| bCTMode | CT\METER |  | 0:cWiredC
T
1038 | bCTAdjust | CTAdjust enable | W | 0:disable |  | 0
1:enable
1039 | wDisChargeS OCLowLimit1 | Stop soc1 when discharge | W | 0-10 | 1% | 5 | Load first Mode
1040 | wDisChargeS OCLowLimit2 | Stop soc2 when discharge | W | 0-10 | 1% | 5 | grid first Mode
1041 | wChargeSOC | Stop soc1 when charge | W | 50-100 | 1% | 100 | Load first Mode
LowLimit1
1042 | wChargeSOC | Stop soc2 when charge | W | 50-100 | 1% | 100 | battery first Mode
LowLimit2
1043 | AC Charge | AC Charge Enable | W/R | 0:disable |  | 0
| Enable |  |  | 1:enable
1044 | Priority choose | Load(default)/Battery/G | W/R | 0:Load |  | 0
|  | rid |  | 1:Battery
2:Grid
1045 | ChargePower | Free Mode Charging | 0~100 | 1% |  | 100
| Command | Power Percent
1046 | DisChargePo werComman | Free Mode DisCharging | 0~100 | 1% |  | 100
| d | Power Percent
1047 | bAgingTestSt ep | Command for aging test |  | 0: default
1: charge 2:
discharge
26 / 55
13 | Ppv3 H | PV3 input power (high) |  | 0.1W
14 | Ppv3 L | PV3 input power (low) |  | 0.1W
15 | Vpv4 | PV4 voltage |  | 0.1V
16 | PV4Curr | PV4 input current |  | 0.1A
17 | Ppv4 H | PV4 input power (high) |  | 0.1W
18 | Ppv4 L | PV4 input power (low) |  | 0.1W
19 | Vpv5 | PV5 voltage |  | 0.1V
20 | PV5Curr | PV5 input current |  | 0.1A
21 | Ppv5H | PV5 input power(high) |  | 0.1W
22 | Ppv5 L | PV5 input power(low) |  | 0.1W
23 | Vpv6 | PV6 voltage |  | 0.1V
24 | PV6Curr | PV6 input current |  | 0.1A
25 | Ppv6 H | PV6 input power (high) |  | 0.1W
26 | Ppv6 L | PV6 input power (low) |  | 0.1W
27 | Vpv7 | PV7 voltage |  | 0.1V
28 | PV7Curr | PV7 input current |  | 0.1A
29 | Ppv7 H | PV7 input power (high) |  | 0.1W
30 | Ppv7 L | PV7 input power (low) |  | 0.1W
31 | Vpv8 | PV8 voltage |  | 0.1V
32 | PV8Curr | PV8 input current |  | 0.1A
33 | Ppv8 H | PV8 input power (high) |  | 0.1W
34 | Ppv8 L | PV8 input power (low) |  | 0.1W
35 | Pac H | Output power (high) |  | 0.1W
36 | Pac L | Output power (low) |  | 0.1W
37 | Fac | Grid frequency |  | 0.01Hz
38 | Vac1 | Three/single phase grid voltage |  | 0.1V
39 | Iac1 | Three/single phase grid output current |  | 0.1A
40 | Pac1 H | Three/single phase grid output watt |  | 0.1VA
(high)
41 | Pac1 L | Three/single phase grid output watt |  | 0.1VA
(low)
42 | Vac2 | Three phase grid voltage |  | 0.1V
43 | Iac2 | Three phase grid output current |  | 0.1A
44 | Pac2 H | Three phase grid output power (high) |  | 0.1VA
45 | Pac2 L | Three phase grid output power (low) |  | 0.1VA
46 | Vac3 | Three phase grid voltage |  | 0.1V
47 | Iac3 | Three phase grid output current |  | 0.1A
48 | Pac3 H | Three phase grid output power (high) |  | 0.1VA
49 | Pac3 L | Three phase grid output power (low) |  | 0.1VA
50 | Vac_RS | Three phase grid voltage |  | 0.1V | Line volt | age
51 | Vac_ST | Three phase grid voltage |  | 0.1V | Line volt | age
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
27 / 55
52 | Vac_TR | Three phase grid voltage |  | 0.1V | Line volt | age
53 | Eac today H | Today generate energy (high) |  | 0.1kWH
54 | Eac today L | Today generate energy (low) |  | 0.1kWH
55 | Eac total H | Total generate energy (high) |  | 0.1kWH
56 | Eac total L | Total generate energy (low) |  | 0.1kWH
57 | Time total H | Work time total (high) |  | 0.5s
58 | Time total L | Work time total (low) |  | 0.5s
59 | Epv1_today H | PV1 Energy today (high) |  | 0.1kWh
60 | Epv1_today L | PV1 Energy today (low) |  | 0.1kWh
61 | Epv1_total H | PV1 Energy total (high) |  | 0.1kWh
62 | Epv1_total L | PV1 Energy total (low) |  | 0.1kWh
63 | Epv2_today H | PV2 Energy today (high) |  | 0.1kWh
64 | Epv2_today L | PV2 Energy today (low) |  | 0.1kWh
65 | Epv2_total H | PV2 Energy total (high) |  | 0.1kWh
66 | Epv2_total L | PV2 Energy total (low) |  | 0.1kWh
67 | Epv3_today H | PV3 Energy today (high) |  | 0.1kWh
68 | Epv3_today L | PV3 Energy today (low) |  | 0.1kWh
69 | Epv3_total H | PV3 Energy total (high) |  | 0.1kWh
70 | Epv3_total L | PV3 Energy total (low) |  | 0.1kWh
71 | Epv4_today H | PV4 Energy today (high) |  | 0.1kWh
72 | Epv4_today L | PV4 Energy today (low) |  | 0.1kWh
73 | Epv4_total H | PV4 Energy total (high) |  | 0.1kWh
74 | Epv4_total L | PV4 Energy total (low) |  | 0.1kWh
75 | Epv5_today H | PV5 Energy today (high) |  | 0.1kWh
76 | Epv5_today L | PV5 Energy today (low) |  | 0.1kWh
77 | Epv5_total H | PV5 Energy total (high) |  | 0.1kWh
78 | Epv5_total L | PV5 Energy total (low) |  | 0.1kWh
79 | Epv6_today H | PV6 Energy today (high) |  | 0.1kWh
80 | Epv6_today L | PV6Energy today (low) |  | 0.1kWh
81 | Epv6_total H | PV6 Energy total (high) |  | 0.1kWh
82 | Epv6_total L | PV6 Energy total (low) |  | 0.1kWh
83 | Epv7_today H | PV7 Energy today (high) |  | 0.1kWh
84 | Epv7_today L | PV7 Energy today (low) |  | 0.1kWh
85 | Epv7_total H | PV7 Energy total (high) |  | 0.1kWh
86 | Epv7_total L | PV7 Energy total (low) |  | 0.1kWh
87 | Epv8_today H | PV8 Energy today (high) |  | 0.1kWh
88 | Epv8_today L | PV8Energy today (low) |  | 0.1kWh
89 | Epv8_total H | PV8 Energy total (high) |  | 0.1kWh
90 | Epv8_total L | PV8 Energy total (low) |  | 0.1kWh
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
28 / 55
91 | Epv_total H | PV Energy total (high) |  | 0.1kWh
92 | Epv_total L | PV Energy total (low) |  | 0.1kWh
93 | Temp1 | Inverter temperature |  | 0.1C
94 | Temp2 | The inside IPM in inverter Temperature |  | 0.1C
95 | Temp3 | Boost temperature |  | 0.1C
96 | Temp4 |  |  |  | reserved
97 | Temp5 |  |  |  | reserved
98 | P Bus Voltage | P Bus inside Voltage |  | 0.1V
99 | N Bus Voltage | N Bus inside Voltage |  | 0.1V
100 | IPF | Inverter output PF now | 0-20000
101 | RealOPPercent | Real Output power Percent |  | 1%
102 | OPFullwatt H | Output Maxpower Limited high
103 | OPFullwatt L | Output Maxpower Limited low |  | 0.1W
104 | DeratingMode | DeratingMode | 0:no derate; |  | “*”is Res | erved
1:PV;
2:*;
3:Vac;
4:Fac;
5:Tboost;
6:Tinv;
7:Control;
8:*;
9:*OverBack
ByTime;
105 | Fault code | Inverter fault code | &*1
106 | Fault Bitcode H | Inverter fault code high | &*8
107 | Fault Bitcode L | Inverter fault code low
108 | Fault Bit_II H | Inverter fault code_II high | --预留 mix，待定义
109 | Fault Bit_II L | Inverter fault code_II low
110 | Warning bit H | Warning bit H | &*8
111 | Warning bit L | Warning bit L
112 | bINVWarnCode | bINVWarnCode
113 | real Power | real Power Percent | 0-100 | %
Percent
114 | inv start delay time | inv start delay time
115 | bINVAllFaultCod e | bINVAllFaultCode
… | reserved |  |  |  | reserved
124 | reserved |  |  |  | reserved
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
29 / 55
Second group
125 | PID PV1+ Voltage | PID PV1PE Volt | 0~1000V | 0.1V
126 | PID PV1+ Current | PID PV1PE Curr | -10~10mA | 0.1mA
127 | PID PV2+ Voltage | PID PV2PE Volt | 0~1000V | 0.1V
128 | PID PV2+ Current | PID PV2PE Curr | -10~10mA | 0.1mA
129 | PID PV3+ Voltage | PID PV3PE Volt | 0~1000V | 0.1V
130 | PID PV3+ Current | PID PV3PE Curr | -10~10mA | 0.1mA
131 | PID PV4+ Voltage | PID PV4PE Volt | 0~1000V | 0.1V
132 | PID PV4+ Current | PID PV4PE Curr | -10~10mA | 0.1mA
133 | PID PV5+ Voltage | PID PV5PE Volt | 0~1000V | 0.1V
134 | PID PV5+ Current | PID PV5PE Curr | -10~10mA | 0.1mA
135 | PID PV6+ Voltage | PID PV6PE Volt | 0~1000V | 0.1V
136 | PID PV6+ Current | PID PV6PE Curr | -10~10mA | 0.1mA
137 | PID PV7+ Voltage | PID PV7PE Volt | 0~1000V | 0.1V
138 | PID PV7+ Current | PID PV7PE Curr | -10~10mA | 0.1mA
139 | PID PV8+ Voltage | PID PV8PE Volt | 0~1000V | 0.1V
140 | PID PV8+ Current | PID PV8PE Curr | -10~10mA | 0.1mA
141 | PID Status | Bit0~7:PID Working Status | 0~3
1:Wait Status
2:Normal Status
3:Fault Status
Bit8~15:Reversed
142 | V _String1 | PV String1 voltage |  | 0.1V
143 | Curr _String1 | PV String1 current | -15~15A | 0.1A
144 | V _String2 | PV String2 voltage |  | 0.1V
145 | Curr _String2 | PV String2 current | -15~15A | 0.1A
146 | V _String3 | PV String3 voltage |  | 0.1V
147 | Curr _String3 | PV String3 current | -15~15A | 0.1A
148 | V _String4 | PV String4 voltage |  | 0.1V
149 | Curr _String4 | PV String4 current | -15~15A | 0.1A
150 | V _String5 | PV String5 voltage |  | 0.1V
151 | Curr _String5 | PV String5 current | -15~15A | 0.1A
152 | V _String6 | PV String6 voltage |  | 0.1V
153 | Curr _String6 | PV String6 current | -15~15A | 0.1A
154 | V _String7 | PV String7 voltage |  | 0.1V
155 | Curr _String7 | PV String7 current | -15~15A | 0.1A
156 | V _String8 | PV String8 voltage |  | 0.1V
157 | Curr _String8 | PV String8 current | -15A~15A | 0.1A
158 | V _String9 | PV String9 voltage |  | 0.1V
159 | Curr _String9 | PV String9 current | -15A~15A | 0.1A
160 | V _String10 | PV String10 voltage |  | 0.1V
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
30 / 55
161 | Curr _String10 |  | PV String10 current | -15~15A | 0.1A
162 | V _String11 |  | PV String11 voltage |  | 0.1V
163 | Curr _String11 |  | PV String11 current | -15~15A | 0.1A
164 | V _String12 |  | PV String12 voltage |  | 0.1V
165 | Curr _String12 |  | PV String12 current | -15~15A | 0.1A
166 | V _String13 |  | PV String13 voltage |  | 0.1V
167 | Curr _String13 |  | PV String13 current | -15A~15A | 0.1A
168 | V _String14 |  | PV String14 voltage |  | 0.1V
169 | Curr _String14 |  | PV String14 current | -15~15A | 0.1A
170 | V _String15 |  | PV String15 voltage |  | 0.1V
171 | Curr _String15 |  | PV String15 current | -15~15A | 0.1A
172 | V _String16 |  | PV String16 voltage |  | 0.1V
173 | Curr _String16 |  | PV String16 current | -15~15A | 0.1A
174 | StrUnmatch |  | Bit0~15: String1~16 unmatch |  |  | suggestiv | e
175 | StrCurrentUnblan ce |  | Bit0~15: String1~16 current unblance |  |  | suggestiv | e
176 | StrDisconnect |  | Bit0~15: String1~16 disconnect |  |  | suggestiv | e
177 | PIDFaultCode |  | Bit0:Output over voltage
Bit1: ISO fault
Bit2: BUS voltage abnormal
Bit3~15:reserved
178 | String Prompt |  | String Prompt
Bit0: String Unmatch
Bit1: StrDisconnect
Bit2:StrCurrentUnblance
Bit3~15:reserved
179 | PV Warning Value |  | PV Warning Value
180 | DSP075 | Warning | DSP075 Warning Value
Value
181 | DSP075 | Fault | DSP075 Fault Value
Value
182 | DSP067 | Debug | DSP067 Debug Data1
Data1
183 | DSP067 | Debug | DSP067 Debug Data2
Data2
184 | DSP067 | Debug | DSP067 Debug Data3
Data3
185 | DSP067 | Debug | DSP067 Debug Data4
Data4
186 | DSP067 | Debug | DSP067 Debug Data5
Data5
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
31 / 55
187 | DSP067 | Debug | DSP067 Debug Data6
Data6
188 | DSP067 | Debug | DSP067 Debug Data7
Data7
189 | DSP067 | Debug | DSP067 Debug Data8
Data8
190 | DSP075 | Debug | DSP075 Debug Data1
Data1
191 | DSP075 | Debug | DSP075 Debug Data2
Data2
192 | DSP075 | Debug | DSP075 Debug Data3
Data3
193 | DSP075 | Debug | DSP075 Debug Data4
Data4
194 | DSP075 | Debug | DSP075 Debug Data5
Data55
195 | DSP075 | Debug | DSP075 Debug Data6
Data6
196 | DSP075 | Debug | DSP075 Debug Data7
Data7
197 | DSP075 | Debug | DSP075 Debug Data8
Data8
198 | bUSBAgingTestOk |  | USB Aging Test Ok Flag | 0-1
Flag
199 | bFlashEraseAging |  | Flash Erase Aging Ok Flag | 0-1
OkFlag
200 | PV ISO |  | PV ISO Value |  | KΩ
201 | R_DCI |  | R DCI Curr |  | 0.1mA
202 | S_DCI |  | S DCI Curr |  | 0.1mA
203 | T_DCI |  | T DCI Curr |  | 0.1mA
204 | PID_Bus |  | PID Bus Volt |  | 0.1V
205 | GFCI |  | GFCI Curr |  | mA
206 | SVG/APF Status |  | SVG/APF Status | 0-3
207 | CT_I _R |  | R phase load side current for SVG |  | 0.1A
208 | CT_I _S |  | S phase load side current for SVG |  | 0.1A
209 | CT_I _T |  | T phase load side current for SVG |  | 0.1A
210 | CT_Q _R H |  | R phase load side output reactive power for SVG(High) |  | 0.1Var
211 | CT_Q _R L |  | R phase load side output reactive power for SVG(low) |  | 0.1Var
212 | CT_Q _S H |  | S phase load side output reactive power for SVG(High) |  | 0.1Var
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
33 / 55
| – year¦ month |  | 2000
257 | Grid Fault record 2 | Grid Fault record 2 – day¦ hour
– day¦ hour
258 | Grid Fault record 2 | Grid Fault record 2 – min¦ sec
– min¦ sec
259 | Grid Fault record | Grid Fault record 2-value
2-value
260 | Grid Fault record 3 | Grid Fault record 3 – code
– code
261 | Grid Fault record 3 | Grid Fault record 3 – year¦ month | Year offset is
| – year¦ month |  | 2000
262 | Grid Fault record 3 | Grid Fault record 3 – day¦ hour
– day¦ hour
263 | Grid Fault record 3 | Grid Fault record 3 – min¦ sec
– min¦ sec
264 | Grid Fault record | Grid Fault record 3-value
3-value
265 | Grid Fault record 4 | Grid Fault record 4 – code
– code
266 | Grid Fault record 4 | Grid Fault record 4 – year¦ month | Year offset is
| – year¦ month |  | 2000
267 | Grid Fault record 4 | Grid Fault record 4 – day¦ hour
– day¦ hour
268 | Grid Fault record 4 | Grid Fault record 4 – min¦ sec
– min¦ sec
269 | Grid Fault record | Grid Fault record 4-value
4-value
270 | Grid Fault record 5 | Grid Fault record 5 – code
– code
271 | Grid Fault record 5 | Grid Fault record 5 – year¦ month | Year offset is
| – year¦ month |  | 2000
272 | Grid Fault record 5 | Grid Fault record 5 – day¦ hour
– day¦ hour
273 | Grid Fault record 5 | Grid Fault record 5 – min¦ sec
– min¦ sec
274 | Grid Fault record | Grid Fault record 5-value
5-value
275 | bTestProcess<<8 ¦ bAutoTestStep | Auto test process or auto test step | &*3
276 | wAutoTestResult | Auto test result | &*4
277 | cTestStepStop | Auto test stop step | &*4
278 | Value Limit | Safety voltage/frequency limit value |  | 0.1V
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
34 / 55
279 | Time Limit | Safety time limit value |  | 1ms
280 | Real value | Real voltage/frequency value |  | 0.1V
281 | Test value | Auto testing voltage/frequency value |  | 0.1V
282 | Test treat value | Auto test voltage/frequency treat value |  | 0.1V
283 | Test treat time | Auto test treat time |  | 1ms
284 | E_hour0 H | Energy hourly of this day
285 | E_hour0 L | Energy hourly of this day
286 | E_hour1 H | Energy hourly of this day
287 | E_hour1 L | Energy hourly of this day
… | E_hour | …
… | E_hour | …
330 | E_hour23 H | Energy hourly of this day
331 | E_hour23 L | Energy hourly of this day
332 | E_ day0 H | Energy of latest day
333 | E_day0 L | Energy of latest day
334 | E_ day1 H | Energy of latest 1st day
335 | E_ day1 L | Energy of latest 1st day
… | E_ day | …
… | E_ day | …
344 | E_ day 6 H | Energy of latest 6th day
345 | E_ day 6L | Energy of latest 6th day
346 | E_ month0 H | Energy of latest month
347 | E_ month0 L | Energy of latest month
| E_ month1 H | Energy of latest 1st month
| E_ month1 L | Energy of latest 1st month
… | E_ month | …
… | E_ month | …
368 | E_ month11 H | Energy of latest 11th month
369 | E_ month11L | Energy of latest 11th month
… |  |  |  |  | reserved
374 |  |  |  |  | reserved
Fouth group
375 | E_ year0 H | Energy of latest year
376 | E_ year 0 L | Energy of latest year
377 | E_ year 1 H | Energy of latest 1st year
378 | E_ year 1 L | Energy of latest 1st year
… | E_ year | …
… | E_ year | …
413 | E_ year 18 H | Energy of latest 18th year
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
35 / 55
414 | E_ year18 L |  | Energy of latest 18th year
…
499 | [5 empty] | reserved
Fifth group and sixth
500 |  | Inverter Error record 1 – code | Inverter Error record 1 – code
501 |  | Inverter Error record 1 – year¦ month | Inverter Error record 1 – year¦ month | Year offset is
2000
502 |  | Inverter Error record 1 – day¦ hour | Inverter Error record 1 – day¦ hour
503 |  | Inverter Error record 1 – min¦ sec | Inverter Error record 1 – min¦ sec
504 |  | Inverter Error record 1-value | Inverter Error record 1-value
505 |  | Inverter Error record 2 – code | Inverter Error record 2 – code
506 |  | Inverter Error record 2 – year¦ month | Inverter Error record 2 – year¦ month | Year offset is
2000
507 |  | Inverter Error record 2 – day¦ hour | Inverter Error record 2 – day¦ hour
508 |  | Inverter Error record 2 – min¦ sec | Inverter Error record 2 – min¦ sec
509 |  | Inverter Error record 2-value | Inverter Error record 2-value
510 |  | Inverter Error record 2 – code | Inverter Error record 2 – code
… |  | Inverter Error record…… | Inverter Error record……
740 |  | Inverter Error record49 – code | Inverter Error record 49- code
741 |  | Inverter Error record49 – | Inverter Error record49 – year¦ month | Year offset is
|  | year¦ month |  | 2000
742 |  | Inverter Error record49 – day¦ hour | Inverter Error record49 – day¦ hour
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
36 / 55
743 | Inverter Error record49 – min¦ sec | Inverter Error record49 – min¦ sec
744 | Inverter Error record49-value | Inverter Error record49-value
745 | Inverter Error record50 – code | Inverter Error record 50- code
746 | Inverter Error record50 – | Inverter Error record50 – year¦ month | Year offset is
| year¦ month |  | 2000
747 | Inverter Error record50 – day¦ hour | Inverter Error record50 – day¦ hour
748 | Inverter Error record50 – min¦ sec | Inverter Error record50 – min¦ sec
749 | Inverter Error record50-value | Inverter Error record50-value
Seventh group for debug
750 | ISO fault Value | ISO Fault value |  | 0.1V
751 | GFCI fault Value | GFCI fault Value |  | 1mA
752 | DCI fault Value | DCI fault Value |  | 0.01A
753 | Vpv fault Value | PV voltage fault value |  | 0.1V
754 | Vac fault Value | AC voltage fault value |  | 0.1V
755 | Fac fault Value | AC frequency fault value |  | 0.01 Hz
756 | Temperature fault Value | Temperature fault value |  | 0.1C
757 | WarningValue1 | Warning Value1 of slave CPU | &*9
758 | WarningValue2 | Warning Value2 of slave CPU | &*9
759 | WarningValue3 | Warning Value3 of main CPU or STM32 | &*9
760 | FaultValue | Inverter fault value | &*10
...
799
800 | Debug Reserved | Debug Reserved |  |  | Reserved
……
874 | Debug Reserved | Debug Reserved |  |  | Reserved
Eighth group for reserved
……
999 |  |  |  |  | Reserved
Ninth group for Storage power
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
37 / 55
| uwSysWorkMod | System work mode | 0x00:等待模式 0x01: 自 检 模式，可选 |  | 监控层 | 给客户
1000 | e |  | 0x02 : 保留 0x03：SysFault |  | 显示的式为： | 工作模
|  |  | 模式 |  | 0x00:等待 | 模式模式模式中
|  |  | 0x04: Flash 模式 |  | 0x01:自检 | ¦0x07 常模式
|  |  | 0x05 ： |  | 0x03:故障
|  |  | PVBATOnline 模式: |  | 0x04:升级
|  |  | 0x06 ： |  | 0x05¦0x06
|  |  | BatOnline 模式 |  | ¦0x08:正
0x07 ：
PVOfflineMod
e 模式
0x08 ：
BatOfflineMo
de 模式
1001 |  | System fault word0 |  |  | 详见一障说明 | 体机故
1002 |  | System fault word1
1003 |  | System fault word2
1004 |  | System fault word3
1005 |  | System fault word4
1006 |  | System fault word5
1007 |  | System fault word6
1008 |  | System fault word7
1009 | Pdischarge1 H | Discharge power(high) |  | 0.1W
1010 | Pdischarge1 L | Discharge power (low) |  | 0.1W
1011 | Pcharge1 H | Charge power(high) |  | 0.1W
1012 | Pcharge1 L | Charge power (low) |  | 0.1W
1013 | Vbat | Battery voltage |  | 0.1V
1014 | SOC | State of charge Capacity | 0-100 | 1%
1015 | Pactouser R | AC power to user H |  | 0.1w
H
1016 | Pactouser R L | AC power to user L |  | 0.1w
1017 | Pactouser S |  |  | 0.1w
H
1018 | Pactouser S L |  |  | 0.1w
1019 | Pactouser T |  |  | 0.1w
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
42 / 55
1303 | Ed_ month1 L | Energy Disharge of latest 1st month |  | 0.1kwh
… | Ed_ month | … |  | 0.1kwh
… | Ed_ month | … |  | 0.1kwh
| Ed_ month11 H | Energy Disharge of latest 11th month |  | 0.1kwh
1322
1323 | Ed_ month11L | Energy Disharge of latest 11th month |  | 0.1kwh
1324 | Ed_ year0 H | Energy Disharge of latest year |  | 0.1kwh
1325 | Ed_ year 0 L | Energy Disharge of latest year |  | 0.1kwh
1326 | Eg_ day0 H | Energy to grid of latest day |  | 0.1kwh
1327 | Eg_day0 L | Energy to grid of latest day |  | 0.1kwh
1328 | Eg_ day1 H | Energy to grid of latest 1st day |  | 0.1kwh
1329 | Eg_ day1 L | Energy to grid of latest 1st day |  | 0.1kwh
… | Eg_ day | … |  | 0.1kwh
… | Eg_ day | … |  | 0.1kwh
1337 | Eg_ day 6 H | Energy to grid of latest 6th day |  | 0.1kwh
1338 | Eg_ day 6L | Energy to grid of latest 6th day |  | 0.1kwh
1339 | Eg_ month0 H | Energy to grid of latest month |  | 0.1kwh
1340 | Eg_ month0 L | Energy to grid of latest month |  | 0.1kwh
1341 | Eg_ month1 H | Energy to grid of latest 1st month |  | 0.1kwh
1342 | Eg_ month1 L | Energy to grid of latest 1st month |  | 0.1kwh
… | Eg_ month | … |  | 0.1kwh
… | Eg_ month | … |  | 0.1kwh
1361 | Eg_ month11 H | Energy to grid of latest 11th month |  | 0.1kwh
1362 | Eg_ month11L | Energy to grid of latest 11th month |  | 0.1kwh
1363 | Eg_ year0 H | Energy to grid of latest year |  | 0.1kwh
1364 | Eg_ year 0 L | Energy to grid of latest year |  | 0.1kwh
1365 | Eu_ day0 H | Energy to user of latest day |  | 0.1kwh
1366 | Eu_day0 L | Energy to user of latest day |  | 0.1kwh
1367 | Eu_ day1 H | Energy to user of latest 1st day |  | 0.1kwh
1368 | Eu_ day1 L | Energy to user of latest 1st day |  | 0.1kwh
… | Eu_ day | … |  | 0.1kwh
… | Eu_ day | … |  | 0.1kwh
Eleventh group for Storage power
1375 | Eu_ day 6 H | Energy to user of latest 6th day |  | 0.1kwh
1376 | Eu_ day 6L | Energy to user of latest 6th day |  | 0.1kwh
1377 | Eu_ month0 H | Energy to user of latest month |  | 0.1kwh
1378 | Eu_ month0 L | Energy to user of latest month |  | 0.1kwh
1379 | Eu_ month1 H | Energy to user of latest 1st month |  | 0.1kwh
1380 | Eu_ month1 L | Energy to user of latest 1st month |  | 0.1kwh
… | Eu_ month | … |  | 0.1kwh
… | Eu_ month | … |  | 0.1kwh
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
43 / 55
1399 | Eu_ month11 H | Energy to user of latest 11th month |  |  | 0.1kwh
1400 | Eu_ month11L | Energy to user of latest 11th month |  |  | 0.1kwh
1401 | Eu_ year0 H | Energy to user of latest year |  |  | 0.1kwh
1402 | Eu_ year 0 L | Energy to user of latest year |  |  | 0.1kwh
Twelfth group for buck-boost debug
1500 | CurrentRecord_0x | OCD Date & Time(L) |  | 0-5:Second
| 22 | R |  | 6-11:minute
12-16:hour
17-21:day
22-25:month
26-31:year
1501 | CurrentRecord_0x | OCD Date & Time(H) | R
23
1502 | CurrentRecord_0x | Current SCD Protection | R | 0-65534
| 24 | Counts in Discharge
1503 | CurrentRecord_0x | SCD Date & Time(L) | R | 0-5:Second
| 25 |  |  | 6-11:minute
12-16:hour
17-21:day
22-25:month
26-31:year
1504 | CurrentRecord_0x | SCD Date & Time(H) | R
26
1505 | CurrentRecordUp date |  | R | 0:00
unrefreshed 1: refreshed
1506 | CurrentRecord_0x |  | R | reversed
28
1507 | CurrentRecord_0x |  | R | reversed
29
1508 | CurrentRecord_0x |  | R | reversed
2A
1509 | CurrentRecord_0x |  | R | reversed
2B
1510 | CurrentRecord_0x |  | R | reversed
2C
1511 | CurrentRecord_0x |  | R | reversed
2D
1512 | CurrentRecord_0x |  | R | reversed
2E
1513 | CurrentRecord_0x |  | R | reversed
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
44 / 55
2F
1514 | VoltageRecord_0x | High Voltage | R
| 31 | Protection Counts in
Charge
1515 | VoltageRecord_0x | High Voltage | R
| 32 | Protection Counts in
Discharge
1516 | VoltageRecord_0x | OVC Date & Time(L) | R
33
1517 | VoltageRecord_0x | OVC Date & Time(H) | R
34
1518 | VoltageRecord_0x | OVD Date & Time(L)
35
1519 | VoltageRecord_0x | OVD Date & Time(H)
36
1520 | VoltageRecord_0x | Low Voltage Protection
| 37 | Counts in Charge
1521 | VoltageRecord_0x | Low Voltage Protection
| 38 | Counts in Discharge
1522 | VoltageRecord_0x | UVC Date & Time(L)
39
1523 | VoltageRecord_0x | UVC Date & Time(H)
3A
1524 | VoltageRecord_0x | UVD Date & Time(L)
3B
1525 | VoltageRecord_0x | UVD Date & Time(H)
3C
1526 | VoltageRecordUpd ate |  |  | 0:00
unrefreshed 1: refreshed
1527 | VoltageRecord_0x |  |  | reversed
3E
1528 | VoltageRecord_0x |  |  | reversed
3F
1529 | TemperatureRecor d_0x41 | High Temperature
Protection Counts in
Charge
1530 | TemperatureRecor d_0x42 | High Temperature
Protection Counts in
Discharge
1531 | TemperatureRecor d_0x43 | OTC Date & Time(L)
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
45 / 55
1532 | TemperatureRecor d_0x44 | OTC Date & Time(H)
1533 | TemperatureRecor d_0x45 | OTD Date & Time(L)
1534 | TemperatureRecor d_0x46 | OTD Date & Time(H)
1535 | TemperatureRecor d_0x47 | Low Temperature
Protection Counts in
Charge
1536 | TemperatureRecor d_0x48 | Low Temperature
Protection Counts in
Discharge
1537 | TemperatureRecor d_0x49 | UTC Date & Time(L)
1538 | TemperatureRecor d_0x4A | UTC Date & Time(H)
1539 | TemperatureRecor d_0x4B | UTD Date & Time(L)
1540 | TemperatureRecor d_0x4C | UTD Date & Time(H)
1541 | TemperatureRecor dUpdate |  |  | reversed | 0:00
unrefresh ed
1:00
refreshed
1542 | TemperatureRecor d_0x4E |  |  | reversed
1543 | TemperatureRecor d_0x4F |  |  | reversed
1544 | ChargeRecordUpd ate |  | W/R | 0:00 | default:0
unrefreshed 1: refreshed
1545 | ChargeRecord_0x | Charge Counts (more than 60s) |  | 0~65534
51
1546 | ChargeRecord_0x | Last charge Date &
| 52 | Time(L)
1547 | ChargeRecord_0x | Last charge Date &
| 53 | Time(H)
1548 | ChargeRecord_0x | Full Charge Counts |  | 0~65534
54
1549 | ChargeRecord_0x | Last full charge Date &
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
46 / 55
| 55 | Time(L)
1550 | ChargeRecord_0x | Last full charge Date &
| 56 | Time(H)
1551 | ChargeRecord_0x | 2nd Protection Active
| 57 | Date & Time(L)
1552 | ChargeRecord_0x | 2nd Protection Active
| 58 | Date & Time(H)
1553 | ChargeRecord_0x |  |  | reversed
59
1554 | ChargeRecord_0x |  |  | reversed
5A
1555 | StatusInfo_0x11 | Date&Time(L)
1556 | StatusInfo_0x12 | Date&Time(H)
1557 | StatusInfo_0x13 | status |  | bit0-1:00-pre -charge;
01-standby;
10-charging; 11-dischargi ng bit2: 0-no
error; 1-error bit3:
0-unbalanc; 1-balance bit4: 0-wake; 1-sleep bit5:
0-mosfet off; 1-mosfet on bit6-8:revers ed
1558 | StatusInfo_0x14 | Error code |  | bit0: OCD bit1: SCD bit2: OV bit3: UV bit4: OTD bit5: OTC bit6: UTD bit7: UTC
Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888
#28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com
District, Shenzhen, P.R. China. 社区光明路28号
P.C. 518000
|  |  |  | 4 | Testing grid frequency low pro
&*4: The variable “wAutoTestResult” and “cTestStepStop”: wAutoTestResult is the step test time counter, when it reach cTestStepStop, this step test will stop and fail.
&*5: Inverter Model: A , could be show: “A1 B0 D0 T0 PF U1 M5 S1” or “1000F151”
Ax=(A&0XF00000000)>>28
Bx=(A&0XF0000000)>>24
Dx=(A&0XF000000)>>20
Tx=(A&0XF00000)>>16
Px=(A&0x00F000)>>12
Ux=(A&0x000F00)>>8
Mx=(A&0x0000F0)>>4
Sx=(A&0x00000F)
&*6: DTC(Device type code)
Code No. | Device type | Note
001xx | Inverter | 1 tracker and 1phase Grid connect PV inverter TL
002xx | Inverter | 2 tracker and 1phase Grid connect PV inverter TL
003xx | Inverter | 1 tracker and 1phase Grid connect PV inverter HF
004xx | Inverter | 2 tracker and 1phase Grid connect PV inverter HF
005xx | Inverter | 1 tracker and 1phase Grid connect PV inverter LF
006xx | Inverter | 2 tracker and 1phase Grid connect PV inverter LF
007xx | Inverter | 1 tracker and 3phase Grid connect PV inverter TL
008xx | Inverter | 2 tracker and 3phase Grid connect PV inverter TL
009xx | Inverter | 1 tracker and 3phase Grid connect PV inverter LF
010xx | Inverter | 2 tracker and 3phase Grid connect PV inverter LF
……
10001 | Data logger | RF-ShineVersion
10002 | Data logger | Web-ShinePano
10003 | Data logger | Web-ShineWebBox
10004 | Data logger | WL-WIFI Module
……
11001 | Confluence box | Confluence box 1
……
&*7: Grid network power control command password:
Inverter is in lock state after power on; change the power control by network command should unlock | inverter first; default pw is XXXXXX;
Unlock: send 0 to 3-135, then send password to 3-136~138; inverter will auto lock in 5min after
unlocked;
Change PW: unlock first, then send 1 to 3-135, then send new password to 3-136~138;
Lock: send 0 or 2 to 3-135;
&*8: Inverter fault code and warning code
Fault code |  |  |  | Warning code
0x00000001 | \ |  | 0x0001 | Fan warning
0x00000002 | Communication error |  | 0x0002 | String communication abnormal
0x00000004 | \ |  | 0x0004 | StrPID config Warning
0x00000008 | StrReverse or StrShort fault |  | 0x0008 | \
0x00000010 | Model Init fault |  | 0x0010 | DSP and COM firmware unmatch
0x00000020 | Grid Volt Sample diffirent |  | 0x0020 | \
0x00000040 | ISO Sample diffirent |  | 0x0040 | SPD abnormal
0x00000080 | GFCI Sample diffirent |  | 0x0080 | GND and N connect abnormal
0x00000100 | \ |  | 0x0100 | PV1 or PV2 circuit short
0x00000200 | \ |  | 0x0200 | PV1 or PV2 boost driver broken
0x00000400 | \ |  | 0x0400 | \
0x00000800 | \ |  | 0x0800 | \
0x00001000 | AFCI Fault |  | 0x1000 | \
0x00002000 | \ |  | 0x2000 | \
0x00004000 | AFCI Module fault |  | 0x4000 | \
0x00008000 | \ |  | 0x8000 | \
0x00010000 | \
0x00020000 | Relay check fault
0x00040000 | \
0x00080000 | \
0x00100000 | \
0x00200000 | Communication error
0x00400000 | Bus Voltage error
0x00800000 | AutoTest fail
0x01000000 | No Utility
0x02000000 | PV Isolation Low
0x04000000 | Residual I High
0x08000000 | Output High DCI
0x10000000 | PV Voltage high
0x20000000 | AC V Outrange
0x40000000 | AC F Outrange
0x80000000 | TempratureHigh
&*9 Warning Value
| Warning Value 1 | Warning Value 2 | Warning Value 3
0x0001 | String1abnormal | PV1ShortCircuit | AC SPD abnormal
0x0002 | String2abnormal | PV2ShortCircuit | DC SPD abnormal
6 Notice
1) It can drive mostly 32 pv inverters for one rs485 comport.
2) There are only read input and hold registers commands even the newest version.
3) App user could only care the input register.
4) App user could not care the holding registers.
5) Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing the other registers;