## Sheet1
Growatt Inverter Modbus RTU Protocol
V1.20
Make： weiwei.shi
Check： qixing.ren
Authorize： liangcai.wu
Effective date：
Change Record
Index | Version | Change Content | Make | Make date
1 | 0 | First Republic | Weiwei.shi | 2020.4.28
Instruction：Register range for various types of inverter TL-X（MIN Type）：03 register range：0~124,3000~3124；04 register range：3000~3124,3125~3249
TL3-X(MAX、MID、MAC Type)：03 register range：0~124,125~249；
04 register range：0~124,125~249
Storage(MIX Type)：03 register range：0~124,1000~1124；04 register range：0~124,1000~1124
Storage(SPA Type)：03 register range：0~124,1000~1124；04 register range：1000~1124,2000~2124
Storage(SPH Type)：03 register range：0~124,1000~1124；04 register range：0~124,1000~1124
catalog
1 Data format | 5
2 Command Format | 5
3 Device Message Transmission Mode / Framing | 8
4 Register map | 9
4.1 Holding Reg | 9
4.2 Input Reg | 33
5 Set address | 65
6 Notice | 65
1 Data format
Valid slave device addresses are in the range of 0 – 254 decimal.
The individual slave devices are assigned addresses in the range of 1 – 254.
0 is the broadcast address
It is 16bits (two bytes) unsigned integer for each holding and input register;
2 Command Format
Function 3 Read holding register
Response Error:
11 0x80¦0x03 ErrornumCRC(Errornum as a byte)
Function 4 Read input register
Response Error:
11 0x80¦0x04 ErrornumCRC (Errornum as a byte)
Function 6 Preset single register
Response Error:
11 0x80¦0x06 ErrornumCRC (Errornum as a byte)
Function 16 Preset multiple register
Response Error:
11 0x80¦0x10 ErrornumCRC (Errornum as a byte)
3 Device Message Transmission Mode / Framing
RTU Mode
When controllers are setup to communicate on a Modbus network using RTU (Remote Terminal Unit) mode, each 8–bit byte in a message contains two 4–bit hexadecimal characters. Each message must be transmitted in a continuous stream.
The format for each byte in RTU mode is:
Coding System: 8–bit binary, hexadecimal 0–9, A–F
Two hexadecimal characters contained in each
8–bit field of the message
Bits per Byte:
1 start bit
8 data bits, least significant bit sent first
None parity
1 stop bit
Error Check Field: Cyclical Redundancy Check (CRC)
The baud rate of the transmission is:
Default Baud Rate: 9600 bps
Can be set through hold register 22
Minimum CMD period (RS485 Time out): 850ms.
Wait for minimum850ms to send a new CMD after last CMD. Suggestion is 1s;
Maximum Data Length Define:
Maximum read data length is 125 words in read command;
Maximum update data length is 125 words in preset command;
Note:
Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing other registers;
4 Register map
It is 16bits (two bytes) unsigned integer for each holding and input register;
4.1 Holding Reg
Registe r NO. | Variable | Description | Write or not | Value | Unit | Initial value | Note
Name
First group
0 | OnOff | Remote On/Off . | W | 0or1 |  | 1 | When PV restart, recover 1.
On（1）；Off（0）
1 | SaftyFuncEn | Bit0: SPI enable | W | 0:00 |  |  | SPI: system protection
|  | Bit1: AutoTestStart |  | disable 1: enable |  |  | interface
|  | Bit2: LVFRT enable |  |  |  |  | Bit0~3:for CEI0-21
|  | Bit3:FreqDerating |  |  |  |  | Bit4~6:for SAA
Enable
Bit4: Softstart enable
Bit5: DRMS enable
Bit6:PowerVoltFunc
Enable
Bit7: HVFRT enable
Bit8:ROCOF enable Bit9: Recover
FreqDeratingMode
Enable
Bit10~15:预留
2 | PF CMD memory | Set Holding register3,4,5,99 CMD will be memory or not(1/0), if not, these settings are the initial value. | W | 0or1 |  | 0 | Means these settings will be acting or not when next power on
state
3 | Active P | Inverter Max output active power percent | W | 0-100 or | % | 255 | 255: power is not be limited
| Rate |  |  | 255
4 | Reactive P | Inverter max output reactive power percent | W | -100-100 or 255 | % | 255 | 255: power is not be limited
Rate
5 | Power factor | Inverter output power factor’s 10000 times | W | 0-20000, |  | 0
0-10000
is
underexci ted, other
is
overexcit ed
6 | Pmax H | Normal power (high) |  |  | 0.1VA
7 | Pmax L | Normal power (low) |  |  | 0.1VA
8 | Vnormal | Normal work PV voltage |  |  | 0.1V
9 | Fw version H | Firmware version |  |  | ASCII
(high)
10 | Fw version | Firmware version
| M | (middle)
11 | Fw version L | Firmware version (low)
12 | Fw version2 | Control Firmware version (high) |  |  | ASCII
H
13 | Fw version2 | Control Firmware version (middle)
M
14 | Fw version2 | Control Firmware version (low)
L
15 | LCD language | LCD language | W | 0-5 |  |  | 0: Italian;
1: English;
2: German;
3: Spanish;
4: French;
5: Chinese;
6：Polish
7：Portugues
8：Hungary
16 | CountrySele cted | Country Selected or not | W | 0: need
to select;
1: have
selected
17 | Vpv start | Input start voltage | W |  | 0.1V
18 | Time start | Start time | W |  | 1s
19 | RestartDelay | Restart Delay Time after fault back; | W |  | 1s
Time
20 | wPowerStart | Power start slope | W | 1-1000 | 0.1%
Slope
21 | wPowerRest artSlopeEE | Power restart slope | W | 1-1000 | 0.1%
22 | wSelectBaud | Select | W | 0-1 |  | 0
| rate | communicationbaudrat
e
0: 9600bps
1:38400bps
23 | Serial NO | Serial number 1-2 |  |  | ASCII
24 | Serial NO | Serial number 3-4
25 | Serial NO | Serial number 5-6
26 | Serial NO | Serial number 7-8
27 | Serial NO | Serial number 9-10
28 | Module H | Inverter Module (high) |  | &*5
29 | Module L | Inverter Module (low) |  | &*5
30 | Com | Communicate address | W | 1-254 |  | 1
Address
31 | FlashStart | Update firmware | W | 1
32 | Reset User | Reset User Information | W | 0x0001
Info
33 | Reset to | Reset to factory | W | 0x0001
factory
34 | Manufacture | Manufacturer information (high) |  |  | ASCII
r Info 8
35 | Manufacture | Manufacturer information (middle)
r Info 7
36 | Manufacture | Manufacturer information (low)
r Info 6
37 | Manufacture | Manufacturer information (high)
r Info 5
38 | Manufacture | Manufacturer information (middle)
r Info 4
39 | Manufacture | Manufacturer information (low)
r Info3
40 | Manufacture | Manufacturer information (low)
r Info 2
41 | Manufacture | Manufacturer information (high)
r Info 1
42 | bfailsafeEn; | G100 fail safe | W | Enable:1 |  |  | English G100 fail safe set
Disable:0
43 | DTC | Device Type Code |  | &*6
44 | TP | Input tracker num and output phase num |  | Eg:0x020
3 is two MPPT and 3ph output
45 | Sys Year | System time-year | W | Year offset is 0 |  |  | Local time
46 | Sys Month | System time- Month | W
47 | Sys Day | System time- Day | W
48 | Sys Hour | System time- Hour | W
49 | Sys Min | System time- Min | W
50 | Sys Sec | System time- Second | W
51 | Sys Weekly | System Weekly | W | 0-6
52 | Vac low | Grid voltage low limit protect | W |  | 0.1V
53 | Vac high | Grid voltage high limit protect | W |  | 0.1V
54 | Fac low | Grid frequency low limit protect | W |  | 0.01
Hz
55 | Fac high | Grid high | W |  | 0.01
|  | frequencylimit protect |  |  | Hz
56 | Vac low 2 | Grid voltage low limit protect 2 | W |  | 0.1V
57 | Vac high 2 | Grid voltage high limit protect 2 | W |  | 0.1V
58 | Fac low 2 | Grid frequency low limit protect 2 | W |  | 0.01
Hz
59 | Fac high 2 | Grid high frequency limit protect 2 | W |  | 0.01
Hz
60 | Vac low 3 | Grid voltage low limit protect 3 | W |  | 0.1V
61 | Vac high 3 | Grid voltage high limit protect 3 | W |  | 0.1V
62 | Fac low 3 | Grid frequency low | W |  | 0.01Hz
limit protect 3
63 | Fac high 3 | Grid frequency high limit protect 3 | W |  | 0.01Hz
64 | Vac low C | Grid low voltage limit connect to Grid | W |  | 0.1V
65 | Vac high C | Grid high voltage limit connect to Grid | W |  | 0.1V
66 | Fac low C | Grid low frequency limit connect to Grid | W |  | 0.01
Hz
67 | Fac high C | Grid high frequency limit connect to Grid | W |  | 0.01
Hz
68 | Vac low1 | Grid voltage low limit protect time 1 | W |  | Cycle
time
69 | Vac time | high1 | Grid voltage high limit protect time 1 | W |  | Cycle
70 | Vac time | low2 | Grid voltage low limit protect time 2 | W |  | Cycle
71 | Vac time | high2 | Grid voltage high limit protect time 2 | W |  | Cycle
72 | Fac time | low1 | Grid frequency low | W |  | Cycle
limit protect time 1
73 | Fac time | high1 | Grid frequency high limit protect time 1 | W |  | Cycle
74 | Fac time | low2 | Grid frequency low | W |  | Cycle
limit protect time 2
75 | Fac time | high2 | Grid frequency high limit protect time 2 | W |  | Cycle
76 | Vac time | low3 | Grid voltage low limit protect time 3 | W |  | Cycle
77 | Vac time | high3 | Grid voltage high limit protect time 3 | W |  | Cycle
78 | Fac time | low3 | Grid frequency low | W |  | Cycle
limit protect time 3
79 | Fac time | high3 | Grid frequency high limit protect time 3 | W |  | Cycle
80 | U10min |  | Volt protection for 10 min | W |  | 0.1V | 1.1Vn
81 | PV Voltage |  | PV Voltage High Fault | W |  | 0.1V
High Fault
82 | FW Build No. |  | FW Build version |  |  | ASCII
5
83 | FW Build No. |  | FW Build version |  |  | ASCII
4
84 | FW Build No. |  | DSP1 FW Build No. |  |  | ASCII
3
85 | FW Build No. |  | DSP2 FW Build No. |  |  | ASCII
2
86 | FW Build No. |  | M3 FW Build No. |  |  | ASCII
1
87 | FW Build No. |  | CPLD FW Build No. |  |  | ASCII
0
88 | ModbusVers |  | Modbus Version |  | Eg：207 is | Int(16 bits)
| ion |  |  |  | V2.07
89 | PFModel |  | Set PF function Model | W
0: PF=1
1: PF by set
2: default PF line
3: User PF line
4: UnderExcited (Inda)
Reactive Power
5: OverExcited(Capa)
Reactive Power
6：Q(v)model
7：Direct Control mode
90 | GPRS IP Flag | Bit0-3:read:1;Set GPRS | W | Bit0-3:ab out GPRS
|  | IP Successed |  | IP SET Bit4-7:ab out GRPRS
|  | Write:2;Read GPRS IP |  | Status
Successed
Bit4-7:GPRS status
91 | FreqDerateS | Frequency derating start point | W |  | 0.01H
| tart |  |  |  | Z
92 | FLrate | Frequency – load limit rate | W | 0-100 | 10tim
es
93 | V1S | CEI021 V1S Q(v) | W | V1S<V2S | 0.1V
94 | V2S | CEI021 V2S Q(v) | W |  | 0.1V
95 | V1L | CEI021 V1L Q(v) | W | V1L<V1S | 0.1V
96 | V2L | CEI021 V2L Q(v) | W | V2L<V1L | 0.1V
97 | Qlockinpow | Q(v) lock in active power of CEI021 | W | 0-100 | Percen
| er |  |  |  | t
98 | QlockOutpo wer | Q(v) lock Out active power of CEI021 | W | 0-100 | Percen
t
99 | LIGridV | Lock in gird volt of | W | nVn | 0.1V
CEI021 PF line
100 | LOGridV | Lock out gird volt of | W | nVn | 0.1V
CEI021 PF line
101 | PFAdj1 | PF adjust value 1 |  | 4096 is 1
102 | PFAdj2 | PF adjust value 2 |  | 4096 is 1
103 | PFAdj3 | PF adjust value 3 |  | 4096 is 1
104 | PFAdj4 | PF adjust value 4 |  | 4096 is 1
105 | PFAdj5 | PF adjust value 5 |  | 4096 is 1
106 | PFAdj6 | PF adjust value 6 |  | 4096 is 1
107 | QVRPDelayTi meEE | QV Reactive Power | W | 0-30 | 1S | 3S
delaytime
108 | OverFDeratD | Overfrequency derati | W | 0-20 | 50ms | 0
| elayTimeEE | ngdelaytime
109 | QpercentMa | Qmax for Q(V) curve | W | 0-1000 | 0.1%
x
110 | PFLineP1_LP | PF limit line point 1 load percent | W | 0-255 | percen |  | 255 means no this point
t
111 | PFLineP1_PF | PF limit line point 1 power factor | W | 0-20000
112 | PFLineP2_LP | PF limit line point 2 load percent | W | 0-255 | percen |  | 255 means no this point
t
113 | PFLineP2_PF | PF limit line point | W | 0-20000
2power factor
114 | PFLineP3_LP | PF limit line point 3 load percent | W | 0-255 | percen |  | 255 means no this point
t
115 | PFLineP3_PF | PF limit line point 3 power factor | W | 0-20000
116 | PFLineP4_LP | PF limit line point 4 load percent | W | 0-255 | percen |  | 255 means no this point
t
117 | PFLineP4_PF | PF limit line point 4 power factor | W | 0-20000
118 | Module 4 | Inverter Module (4) |  | &*11 |  |  | SxxBxx
119 | Module 3 | Inverter Module (3) |  | &*11 |  |  | DxxTxx
120 | Module 2 | Inverter Module (2) |  | &*11 |  |  | PxxUxx
121 | Module 1 | Inverter Module (1) |  | &*11 |  |  | Mxxxx Power
122 | ExportLimit_ | ExportLimit_En/dis | R/W | 1/0 |  |  | ExportLimit enable,
| En/dis | [5 empty] | 0: Disable exportLimit;
1: Enable 485 exportLimit;
2: Enable 232 exportLimit;
3: Enable CT exportLimit;
123 | ExportLimitP owerRate | ExportLimitPowerRate | R/W | -1000~+1 | 0.1% |  | ExportLimit PowerRate
0
124 | TrakerModel | Traker Model | W | 0,1,2 |  |  | 0:Independent
1:DC Source
2:Parallel
Second group
125 | INV Type-1 | Inverter type-1 | R |  | ASCII |  | Reserved
126 | INV Type-2 | Inverter type-2 | R |  | ASCII
127 | INV Type-3 | Inverter type-3 | R |  | ASCII
128 | INV Type-4 | Inverter type-4 | R |  | ASCII
129 | INV Type-5 | Inverter type-5 | R |  | ASCII
130 | INV Type-6 | Inverter type-6 | R |  | ASCII
131 | INV Type-7 | Inverter type-7 | R |  | ASCII
132 | INV Type-8 | Inverter type-8 | R |  | ASCII
133 | BLVersion1 | Boot loader version1 | R |  |  |  | Reserved
134 | BLVersion2 | Boot loader version2 | R |  |  |  | Reserved
135 | BLVersion3 | Boot loader version3 | R |  |  |  | Reserved
136 | BLVersion4 | Boot loader version4 | R |  |  |  | Reserved
137 | Reactive P | Reactive PowerH | R/W |  | 0.1var
ValueH
138 | Reactive P | Reactive PowerL | R/W |  | 0.1var
ValueL
139 | ReactiveOut putPriorityE nable | ReactiveOutput Priority | R/W |  | 0/1 |  | 0：disable
|  | Enable |  |  |  |  | 1：enable
……
141 | SvgFunction | Svg enable on night | R/W |  | 0/1 |  | 0：disable
| Enable | [5 empty] | 1：enable
142 | uwUnderFU | UnderF Upload Point | R/W |  | 0.01H
| ploadPoint |  |  |  | Z
143 | uwOFDerate RecoverPoin | OFDerate RecoverPoint | R/W |  | 0.01H
| t |  |  |  | Z
144 | uwOFDerate RecoverDela yTime | OFDerate | R/W | 0-30000 | 50ms
RecoverDelayTime
145 | ZeroCurrent | ZeroCurrent Enable | R/W | 0-1
Enable
146 | uwZeroCurre ntStaticlowV | ZeroCurrent | R/W | 46-230V | 0.1V | 115V
| olt | StaticlowVolt
147 | uwZeroCurre ntStaticHigh | ZeroCurrent | R/W | 230-276V | 0.1V | 276V
| Volt | StaticHighVolt
148 | uwHVoltDer ateHighPoint | HVoltDerate HighPoint | R/W | 0-1000V | 0.1V
149 | uwHVoltDer ateLowPoint | HVoltDerate LowPoint | R/W | 0-1000V | 0.1V
150 | uwQVPower | QVPower Stable Time | R/W | 0-60S | 0.1S
StableTime
151 | uwUnderFU ploadStopPo | UnderF Upload | R/W |  | 0.01H
| int | StopPoint |  |  | Z
152 | fUnderFreqP | Underfrequency load | R/W | 46.00-50. | 0.01Hz | 49.8 | CEI
| oint | start point |  | 0
153 | fUnderFreqE | Underfrequency down | R/W | 46.00-50. | 0.01Hz | 49.1 | CEI
| ndPoint | load end point |  | 0
154 | fOverFreqPo | Over frequency loading start point | R/W | 50.00-52. | 0.01Hz | 50.2 | CEI
| int |  |  | 0
155 | fOverFreqEn dPoint | Over frequency loading end point | R/W | 50.00-52. | 0.01Hz | 51.5 | CEI
0
156 | fUnderVoltP oint | Undervoltage load | R/W | 160-300 | 0.1V | 220 | CEI
shedding start point
157 | fUnderVoltE ndPoint | Undervoltage derating end point | R/W | 160-300 | 0.1V | 207 | CEI
158 | fOverVoltPoi nt | Overvoltage loading | R/W | 160-300 | 0.1V | 230 | CEI
start point
159 | fOverVoltEn dPoint | Overvoltage loading end point | R/W | 160-300 | 0.1V | 245 | CEI
160 | uwNominal | NominalGridVolt Select | R/W | 0~3 |  |  | UL
GridVolt
161 | uwGridWatt | GridWatt DelayTime | R/W | 0~3000 | 20ms |  | UL
Delay
162 | uwReconnec | Reconnect StartSlope | R/W | 1~1000 | 0.1 |  | UL
tStartSlope
163 | uwLFRTEE | LFRT1 Freq | R/W | 5500~650 | 0.01Hz |  | UL
0
164 | uwLFRTTime | LFRT1 Time | R/W |  | 20ms |  | UL
EE
165 | uwLFRT2EE | LFRT2 Freq | R/W | 5500~650 | 0.01Hz |  | UL
0
166 | uwLFRTTime | LFRT2 Time | R/W |  | 20ms |  | UL
2EE
167 | uwHFRTEE | HFRT1 Freq | R/W | 5500~650 | 0.01Hz |  | UL
0
168 | uwHFRTTim | HFRT1 Time | R/W |  | 20ms |  | UL
eEE
169 | uwHFRT2EE | HFRT2 Freq | R/W | 5500~650 | 0.01Hz |  | UL
0
170 | uwHFRTTim e2EE | HFRT2 Time | R/W |  | 20ms |  | UL
171 | uwHVRTEE | HVRT1 Volt | R/W |  | 0.001 |  | UL
Un
172 | uwHVRTTim | HVRT1 Time | R/W |  | 20ms |  | UL
eEE
173 | uwHVRT2EE | HVRT2 Volt | R/W |  | 0.001 |  | UL
Un
174 | uwHVRTTim | HVRT2 Time | R/W |  | 0.001 |  | UL
| e2EE |  |  |  | Un
175 | uwUnderFU | UnderF | R/W | 0-2s | 50ms | 0s | 50549
| ploadDelayTi me | UploadDelayTime
176 | uwUnderFU | UnderF UploadRate | R/W |  |  |  | 50549
ploadRateEE
177 | uwGridResta rt_H_Freq | GridRestart HighFreq | R/W |  | 0.01Hz |  | 50549
178 | OverFDeratR esponseTim | OverFDerat | W/R | 0-500
| e | ResponseTime
179 | UnderFUplo adResponse | UnderFUpload | W/R | 0-500
| Time | ResponseTime
Intelligent control reads relevant data, used to identify the logo 180-200
180 | MeterLink | Whether to elect the meter | R/W |  |  |  | 0: Missed, 1: Received
181 | OPT Number | Number of connection optimizers | R/W | 0-64 |  |  | The total number of optimizers connected to the inverter
182 | OPT | Optimizer configuration completion flag | R/W |  |  |  | 0x00:Not configured success
| ConfigOK | [5 empty] | 0x01:Configuration is complete
Flag
183 | PvStrScan | String Num | R/W | 0、8、16、 |  |  | 0：Not support
|  |  |  | 32 |  |  | Other：PvString Num
……
200 | Reserved | [5 empty] | Reserved
201 | PID Working | PID Operating mode | W | 0:00
| Model |  |  | automati
c 1:
continuo us
2: All night
202 | PID On/Off | PID Break control | W | 0:On 1:Off
Ctrl
203 | PID Volt | PID Output voltage option | W | 300~1000 | V
Option
…… | [6 empty] | Reserved
209 | New | Serial number 1-2 |  |  | ASCII
Serial NO
210 | New | Serial number 3-4 |  |  | ASCII
Serial NO
211 | New | Serial number 5-6 |  |  | ASCII
Serial NO
212 | New | Serial number 7-8 |  |  | ASCII
Serial NO
213 | New | Serial number 9-10 |  |  | ASCII
Serial NO
214 | New | Serial number 11-12 |  |  | ASCII
Serial NO
215 | New | Serial number 13-14 |  |  | ASCII
Serial NO
216 | New | Serial number 15-16 |  |  | ASCII
Serial NO
217 | New | Serial number 17-18 |  |  | ASCII
Serial NO
218 | New | Serial number 19-20 |  |  | ASCII
Serial NO
219 | New | Serial number 21-22 |  |  | ASCII
Serial NO
220 | New | Serial number 23-24 |  |  | ASCII
Serial NO
221 | New | Serial number 25-26 |  |  | ASCII
Serial NO
222 | New | Serial number 27-28 |  |  | ASCII
Serial NO
223 | New | Serial number 29-30 |  |  | ASCII
Serial NO
…… | [6 empty] | Reserved
229 | EnergyAdjus | Power generation incremental calibration | W/R |  | 0.1% |  | 1-1000,(Percent ratio)
| t | coefficient
230~249 for growatt debug setting
230 | IslandDisabl e | Island Disable or not. | W | 0,1 |  | 0
1:disable 0:Enable
231 | FanCheck | Start Fan Check | W | 1
232 | EnableNLine | Enable N Line of grid | W | 1 |  | 0
233 | wCheckHard | wCheckHardware
| ware | Bit0: GFCIBreak;
Bit1:SPSDamage
Bit8:EepromReadWarni ng
Bit9:EEWriteWarning
……
234 | wCheckHard ware2 | [5 empty] | reserved
235 | ubNToGNDD | Dis/enable N to GND detect function | W | 1:enable |  | 1
| etect |  |  | 0:disable
236 | NonStdVacE nable | Enable/Disable | W | 0-2 |  | 0 | 0:Disable;
|  | Nonstandard |  |  |  |  | 1:Enable Voltgrade1
|  | Grid voltage range |  |  |  |  | 2:Enable Voltgrade2
237 | uwEnableSp ecSet | Disablse/enable appointed spec setting | W | 1:enable | Binary | 0x000 | Bit 0: Hungary
|  |  |  | 0:disable |  | 0
238 | Fast MPPT | About Fast mppt |  | 0,1,2 |  | 0 | Reserved
enable
239 | / | / | / | / |  | / | Reserved
240 | Check Step |  | W
241 | INV-Lng | Inverter Longitude | W |  |  |  | Longitude
242 | INV-Lat | Inverter Latitude | W |  |  |  | Latitude
…… | [6 empty] | Reserved
249 | [6 empty] | Reserved
Six group for Storage Power
Register NO. | Variable | Description | Write or not | Value | Unit | Initial value | Note
Name
1000 | Float charge current limit | When charge current battery need is lower than this value, enter into float charge | W |  | 0.1A | 600 | CC current
1001 | PF CMD | Set the following 19-22 CMD will be memory ornot(1/0), if not, these settings are the initial value. | W | 0or1, |  | 0 | Means these settings will be acting or not when next power on(02 repeat)
memory
state
1002 | VbatStartF orDischarg | LV Vbat | R/W |  | 0.1V |  | Lead-acid battery LV voltage
e
1003 | VbatlowWa | LoadPercent(only lead-Acid): | W |  | 0.1V |  | Clear battery low voltage error voltage point
rnClr
45.5V
<20%
48.0V
20%~50%
49.0V
>50
1004 | Vbatstopfo rdischarge | Should stop discharge when lower than this voltage(only lead-Acid): | W |  | 0.01V
46.0V
<20%
44.8V
20%~50%
44.2V
>50%
1005 | Vbat stop for charge | Should stop charge when higher than this voltage | W |  | 0.01V | 5800
1006 | Vbat start | Should not discharge when lower than this voltage | W |  | 0.01V | 4800
for discharge
1007 | Vbat constant charge | can charge when lower than this voltage | W |  | 0.01V | 5800 | CV voltage（acid）
1008 | EESysInfo.S ysSetEn | Bit0：Resved; | W |  |  |  | System Enable
Bit1：Resved;
Bit2：Resved;
Bit3：Resved;
Bit4：Resved;
Bit5：bDischargeEn；
Bit6：ForceDischrEn；
Bit7：ChargeEn；
Bit8：bForceChrEn；
Bit9：bBackUpEn；
Bit10：bInvLimitLoadE；
Bit11：bSpLimitLoadEn；
Bit12：bACChargeEn；
Bit13：bPVLoadLimitEn;
Bit14,15:UnUsed;
1009 | Battemp lower limit d | Battery temperature lower limit for discharge | W | 0-200:0-2 | 0.1℃ | 1170
0℃
1000-140
0：-40-0℃
1010 | Bat temp upper limit d | Battery temperature upper limit for discharge | W | 200-1000 | 0.1℃ | 420
1011 | Bat temp lower limit | Battery temperature lower limit for charge | W | 0-200:0-2 | 0.1℃ | 30 | Lower temperature limit
| c |  |  | 0℃
1000-140
0：-40-0℃
1012 | Bat temp upper limit | Battery temperature upper limit for charge | W | 200-1000 | 0.1℃ | 370 | Upper temperature limit
c
1013 | uwUnderFr eDischarge DelyTime | Under Fre Delay Time | s | 0-20 | 50ms |  | Under Fre Delay Time
1014 | BatMdlSeri alNum | Battery serial number | W | 0:00 |  |  | SPH4-11K used
1015 | BatMdlPara llNum | Battery parallel section | W | 0:00 |  |  | SPH4-11K used
1016 | / | / | / | / | / | / | Reserve
1017 | / | / | / | / | / | / | Reserve
1018 | / | / | / | / | / | / | Reserve
1019 | / | / | / | / | / | / | Reserve
1020 | / | / | / | / | / | / | Reserve
1021 | / | / | / | / | / | / | Reserve
1022 | / | / | / | / | / | / | Reserve
1023 | / | / | / | / | / | / | Reserve
1024 | / | / | / | / | / | / | Reserve
1025 | / | / | / | / | / | / | Reserve
1026 | / | / | / | / | / | / | Reserve
1027 | / | / | / | / | / | / | Reserve
1028 | / | / | / | / | / | / | Reserve
1029 | / | / | / | / | / | / | Reserve
1030 | / | / | / | / | / | / | Reserve
1031 | / | / | / | / | / | / | Reserve
1032 | / | / | / | / | / | / | Reserve
1033 | / | / | / | / | / | / | Reserve
1034 | / | / | / | / | / | / | Reserve
1035 | / | / | / | / | / | / | Reserve
1036 | / | / | / | / | / | / | Reserve
1037 |  | Use the CTMode to | W | 2:METER 1:cWirele ssCT |  | 0
| bCTMode | Choose RFCT \ Cable |  | 0:cWiredC
|  | CT\METER |  | T
1038 | CTAdjust | CTAdjust enable | W | 0:disable |  | 0
1:enable
1039 | / | / | / | / | / | / | Reserve
1040 | / | / | / | / | / | / | Reserve
1041 | / | / | / | / | / | / | Reserve
1042 | / | / | / | / | / |  | Reserve
1043 | / | / | / | / | / | / | Reserve
1044 | Priority | ForceChrEn/ForceDischr |  | R |  | 0.Load(de fault)/1.B attery/2.G rid |  |  |  |  | bForceChrEn/disbForceDischrE n/dis
En
Load first/bat first /grid first
1045 | / | / |  | / |  | / |  | / |  | / | Reserve
1046 | / | / |  | / |  | / |  | / |  | / | Reserve
1047 | AgingTestSt ep Cmd | Command for aging test |  |  |  | 0: default 1: charge 2: |  |  |  |  | Cmd for aging test
discharge
1048 | BatteryTyp e | Battery type choose of buck-boost input |  |  |  | 0:Lithium 1:Lead-aci d 2:other |  |  |  | 0 | Battery type
1049 | / | / |  | / |  | / |  | / |  |  | Reserve
1050 | / | / |  | / |  | / |  | / |  | / | Reserve
1051 | / | / |  | / |  | / |  | / |  |  | Reserve
1052 | / | / |  | / |  | / |  | / |  |  | Reserve
1053 | / | / |  | / |  | / |  | / |  |  | Reserve
1054 | / | / |  | / |  | / |  | / |  | / | Reserve
1060 | BuckUpsFunE |  | Ups function enable or |  |  |  | 0:disable
| n |  | disable |  |  |  | 1:enable
1061 | BuckUPSVoltS |  | UPS output voltage |  |  |  | 0.15972 |  |  |  | 230V
| et | [5 empty] | 0.18611
0.25
1062 | UPSFreqSet |  | UPS output frequency |  |  |  | 0:50Hz |  |  |  | 50Hz
1:60Hz
... | / |  | / |  | / |  | / |  | / |  | / | reverse
Priority set
1070 | GridFirstDisch argePowerRat | Discharge Power Rate | W | 0-100 | 1% | Discharge
| e | when Grid First |  |  |  | Power Rate when Grid
First
1071 | GridFirstStopS | Stop Discharge soc when | W | 0-100 | 1% | Stop Discharge soc when
| OC | Grid First |  |  |  | Grid First
1072… | / | / | / | / | / | / | reverse
1079
1080 | Grid First | High eight bit：hour |  | 0-23
| Start Time 1 | Low eight bit：minute |  | 0-59
1081 | Grid First Stop | High eight bit：hour |  | 0-23
| Time 1 | Low eight bit：minute |  | 0-59
1082 | Grid First Stop | Enable :1 |  | 0 or 1 |  | Grid First enable
| Switch 1 | Disable:0
1083 | Grid First | High eight bit：hour |  | 0-23
| Start Time 2 | Low eight bit：minute |  | 0-59
1084 | Grid First Stop | High eight bit：hour |  | 0-23
| Time 2 | Low eight bit：minute |  | 0-59
1085 | Grid First Stop | ForceDischarge.bSwitch&L |  | 0 or 1 |  | Grid First enable | ForceDischarge;
| Switch 2 | CD_SET_FORCE_TRUE_2)= |  |  |  |  | LCD_SET_FORCE_T
|  | #NAME? |  |  |  |  | RUE_2
1086 | Grid First | High eight bit：hour |  | 0-23
| Start Time 3 | Low eight bit：minute |  | 0-59
1087 | Grid First Stop | High eight bit：hour |  | 0-23
| Time 3 | Low eight bit：minute |  | 0-59
1088 | Grid First Stop | Enable :1 |  | 0 or 1 |  | Grid First enable
| Switch 3 | Disable:0
1089 | / | / | / | / | / | / | reserve
1090 | BatFirstPower | Charge Power Rate when | W | 0-100 | 1% | Charge
| Rate | Bat First |  |  |  | Power Rate when Bat
First
1091 | wBatFirst stop | Stop Charge soc when Bat | W | 0-100 | 1% | Stop
| SOC | First |  |  |  | Charge soc when Bat
First
1092 | AC charge | When Bat First |  | Enable:1 |  | AC Charge
| Switch | Enable:1 |  | Disable:0 |  | Enable
Disable:0
1093…
1099
1100 | Bat First Start | High eight bit：hour |  | 0-23
| Time 1 | Low eight bit：minute |  | 0-59
1101 | Bat First Stop | High eight bit：hour |  | 0-23
| Time 1 | Low eight bit：minute |  | 0-59
1102 | BatFirst on/off Switch 1 | Enable :1 |  | 0 or 1 |  | Bat First
|  | Disable:0 |  |  |  | Enable1
1103 | Bat First Start | High eight bit：hour |  | 0-23
| Time 2 | Low eight bit：minute |  | 0-59
1104 | Bat First Stop | High eight bit：hour |  | 0-23
| Time 2 | Low eight bit：minute |  | 0-59
1105 | BatFirston/off | Enable :1 |  | 0 or 1 |  | Bat First
| Switch 2 | Disable:0 |  |  |  | Enable2
1106 | Bat First Start | High eight bit：hour |  | 0-23
| Time 3 | Low eight bit：minute |  | 0-59
1107 | Bat First Stop | High eight bit：hour |  | 0-23
| Time 3 | Low eight bit：minute |  | 0-59
1108 | BatFirston/off | Enable :1 |  | 0 or 1 |  | Bat First
| Switch 3 | Disable:0 |  |  |  | Enable3
1109 | / | / | / | / | / | / | reserve
1110 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Start Time 1 | Low eight bit：minute |  | 0-59
1111 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Stop Time 1 | Low eight bit：minute |  | 0-59
1112 | Load First | Enable :1 |  | 0 or 1 |  | Load First | SPA/ reserve
| Switch 1 | Disable:0 |  |  |  | Enable
1113 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Start Time2 | Low eight bit：minute |  | 0-59
1114 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Stop Time 2 | Low eight bit：minute |  | 0-59
1115 | Load First | Enable :1 |  | 0 or 1 |  | Load First | SPA/ reserve
| Switch 2 | Disable:0 |  |  |  | Enable
1116 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Start Time 3 | Low eight bit：minute |  | 0-59
1117 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Stop Time 3 | Low eight bit：minute |  | 0-59
1118 | Load First | Enable :1 |  | 0 or 1 |  | Load First | SPA/ reserve
| Switch 3 | Disable:0 |  |  |  | Enable
1119 | / | / | / | / | / | / | reserve
1120 | BackUpEn | BackUp Enable |  |  |  |  | MIX US
1121 | SGIPEn | SGIP Enable |  |  |  |  | MIX US
……… | 1122~1124 | / | / | / | / | / | reserve
Use for TL-X and TL-XH
3000 | ExportLimitFa iledPowerRat e | The power rate when exportLimit failed | R/W |  | 0.1% |  | The power rate when exportLimit failed
3001 | New | Serial number 1-2 | R/W |  | ASCII |  | The new model uses the following registers to record the serial number; The representation is the same as the original: one register holds two characters and the new serial number is 30 characters.
Serial NO
3002 | New | Serial number 3-4 | R/W |  | ASCII
Serial NO
3003 | New | Serial number 5-6 | R/W |  | ASCII
Serial NO
3004 | New | Serial number 7-8 | R/W |  | ASCII
Serial NO
3005 | New | Serial number 9-10 | R/W |  | ASCII
Serial NO
3006 | New | Serial number 11-12 | R/W |  | ASCII
Serial NO
3007 | New | Serial number 13-14 | R/W |  | ASCII
Serial NO
3008 | New | Serial number 15-16 | R/W |  | ASCII
Serial NO
3009 | New | Serial number 17-18 | R/W |  | ASCII
Serial NO
3010 | New | Serial number 19-20 | R/W |  | ASCII
Serial NO
3011 | New | Serial number 21-22 | R/W |  | ASCII
Serial NO
3012 | New | Serial number 23-24 | R/W |  | ASCII
Serial NO
3013 | New | Serial number 25-26 | R/W |  | ASCII
Serial NO
3014 | New | Serial number 27-28 | R/W |  | ASCII
Serial NO
3015 | New | Serial number 29-30 | R/W |  | ASCII
Serial NO
3016 | DryContactFu ncEn | DryContact function enable | R/W | 0:Disable |  |  | DryContact function enable
1: Enable
3017 | DryContactOn | The power rate of | R/W | 0~1000 | 0.1% |  | The power rate of drycontact turn on
| Rate | drycontact turn on
3018 | Reserved
3019 | DryContactOf fRate | DryContactOffRate | Dry contact closure power | R/W | 0~100 | 0.1% | Dry contact closure power pe rcentage
0
3020 | BoxCtrlInvOrd er | BoxCtrlInvOrder |  | R/W
Off-net box control instruct ion
3021 | ExterCommOf | External communication setting manual off-network enable | R/W |  |  |  | 0x00: Disable;
| fGridEn | [5 empty] | （default）
0x01: Enable;
3022 | Reserved
3023 | Reserved
3024 | Float charge current limit | When charge current battery need is lower than this value, enter into float charge | R/W |  | 0.1A | 600 | CC current
3025 | VbatWarning | "Battery-low" warning setup voltage | R/W |  | 0.1V | 4800 | Lead acid battery
LV voltage
3026 | VbatlowWarn | "Battery-low" warning clear voltage | R/W |  | 0.1V |  | Clear battery low voltage error voltage point
Clr
LoadPercent(only lead-Acid):
45.5V(Load <
20%);
48.0V(20%<=Load
<=50%);
49.0V(Load >
50%);
3027 | Vbatstopfordi scharge | Battery cut off voltage | R/W |  | 0.1V |  | Should stop discharge when lower than this voltage(only lead-Acid):
46.0V(Load <
20%);
44.8V(20%<=Load
<=50%);
44.2V(Load >
50%);
3028 | Vbat stop for charge | Battery over charge voltage | R/W |  | 0.01V | 5800 | Should stop charge when higher than this voltage
3029 | Vbat start for discharge | Battery start discharge voltage | R/W |  | 0.01V | 4800 | Should not discharge when lower than this voltage
3030 | Vbat constant charge | Battery constant charge voltage | R/W |  | 0.01V | 5800 | CV voltage（acid） can charge when lower than this voltage
3031 | Battemp | Battery temperature lower limit for discharge | R/W |  | 0.1℃ | 1170 | 0-200:0-20℃
| lower limit d | [5 empty] | 1000-1400：
-40-0℃
3032 | Bat temp upper limit d | Battery temperature upper limit for discharge | R/W |  | 0.1℃ | 420
3033 | Bat temp lower limit c | Battery temperature lower limit for charge | R/W |  | 0.1℃ | 30 | Battery temperature lower
limit
0-200:0-20℃
1000-1400：
-40-0℃
3034 | Bat temp upper limit c | Battery temperature upper limit for charge | R/W |  | 0.1℃ | 370 | Battery temperature upper limit
3035 | uwUnderFreD ischargeDelyT ime | Under Fre Delay Time | R/W |  | 50ms |  | Under Fre Delay
Time
3036 | GridFirstDisch argePowerRat | Discharge Power Rate when Grid First |  |  |  | 1-255
e
3037 | GridFirstStopS | Stop Discharge soc when |  |  |  | 1-100
| OC | Grid First
3038 | Time 1(xh) | Period 1: [Start Time ~ End | R/W |  |  |  | Bit0~7: minutes;
|  | Time], [Charge/Discharge], [Disable/Enable] |  |  |  |  | Bit8~12: hour;
Bit13~14,
|  | 3038 enable, charge and discharge, start time, end |  |  |  |  | 0: load priority;
|  | time 3039 |  |  |  |  | 1: battery priority;
2: Grid priority;
Bit15,
0: prohibited; 1:
enabled;
3039 |  |  | R/W |  |  |  | Bit0~7: minutes;
Bit8~12: hour;
Bit13~15: reserved
3040 | Time 2(xh) | Time period 2: [start time ~ end time], [charge / | R/W |  |  |  | Bit0~7: minutes;
|  | discharge], [disable / enable] |  |  |  |  | Bit8~12: hour;
Bit13~14,
|  | 3040 enable, charge and discharge, start time, 3041 |  |  |  |  | 0: load priority;
|  | end time |  |  |  |  | 1: battery priority;
2: Grid priority;
Bit15,
0: prohibited; 1:
enabled;
3041 |  |  | R/W |  |  |  | Bit0~7: minutes;
Bit8~12: hour;
Bit13~15: reserved
3042 | Time 3(xh) | With Time1 | R/W |  |  |  | With Time1
3043 |  |  | R/W |  |  |  | With Time1
3044 | Time 4(xh) | With Time1 | R/W |  |  |  | With Time1
3045 |  |  | R/W |  |  |  | With Time1
3046 | Grid First Stop | Grid first time-3 enable |  |  |  |  | Enable :1
| Switch 3 | [5 empty] | Disable:0
3047 | BatFirstPower | Charge Power Rate when |  |  |  | 1-100
| Rate | Bat First
3048 | wBatFirst stop | Stop Charge soc when Bat |  |  |  | 1-100
| SOC | First
3049 | AcChargeEna | AcChargeEnable |  |  |  |  | Enable :1
| ble | [5 empty] | Disable:0
3050 | Time 5(xh) | 同 Time1 | R/W |  |  |  | With Time1
3051 |  |  | R/W |  |  |  | With Time1
3052 | Time 6(xh) | 同 Time1 | R/W |  |  |  | With Time1
3053 |  |  | R/W |  |  |  | With Time1
3054 | Time 7(xh) | 同 Time1 | R/W |  |  |  | With Time1
3055 |  |  | R/W |  |  |  | With Time1
3056 | Time 8(xh) | 同 Time1 | R/W |  |  |  | With Time1
3057 |  |  | R/W |  |  |  | With Time1
3058 | Time 9(xh) | 同 Time1 | R/W |  |  |  | With Time1
3059 |  |  | R/W |  |  |  | With Time1
3060~ | Reserved
3069
3070 | BatteryType | Battery type choose of buck-boost input | R/W |  |  |  | Battery type
0:Lithium
1:Lead-acid
2:other
3071 | BatMdlSeria/ | BatMdlSeria/ParalNum | R/W |  |  |  | BatMdlSeria/Paral
| ParalNum | [5 empty] | Num;
SPH4-11K used
The upper 8 bits indicate the number of series segments；
The lower 8 bits
indicate the number of parallel
sections;
3072 | Reserved
3073 | Reserved
3074 | Reserved
3075 | Reserved
3076 | Reserved
3077 | Reserved
3078 | Reserved
3079 | UpsFunEn | Ups function enable or disable | R/W |  |  | 0 | 0:disable
1:enable
3080 | UPSVoltSet | UPS output voltage | R/W |  |  | 0 | 0:230V
1:208V
2:240V
3081 | UPSFreqSet | UPS output frequency | R/W |  |  | 0 | 0:50Hz
1:60Hz
3082 | bLoadFirstSto pSocSet | StopSoc When LoadFirst | R/W |  |  | 13-100 | ratio
3083 | Reserved
3084 | Reserved
3085 | Com Address | Communication addr | R/W |  |  | 1 | 1 : Communication addr=1
1 ~ 254 :
Communication addr=1~254
3086 | BaudRate | Communication BaudRate | R/W |  |  | 0 | 0: 9600 bps
1: 38400 bps
3087 | Serial NO | Serial Number 1-2 | R/W |  | ASCII |  | For battery
3088 | Serial No | Serial Number 3-4 | R/W |  | ASCII
3089 | Serial No | Serial Number 5-6 | R/W |  | ASCII
3090 | Serial No | Serial Number 7-8 | R/W |  | ASCII
3091 | Serial No | Serial Number 9-10 | R/W |  | ASCII
3092 | Model H | Model H | R/W
3093 | Model L | Model L | R/W
3094 | Pdischr max H | Max Discharge Power | R |  | 0.1W
3095 | Pdischr max
L
3096 | Pchr max H | Max Charge Power | R |  | 0.1W
3097 | Pchr max L
3098 | DTC | DTC | R
3099 | FW Code1 | FW Code1 | R |  | ASCII
3100 | FW Code2 | FW Code2 | R |  | ASCII
3101 | Processor1 | Processor1 FW Vision | R |  | ASCII
FW Vision
3102 | Reset User | Reset User Info | W
Info
3103 | Reset to factory | Reset to factory | W
3104 | Reserved
~
3124
4.2 Input Reg
NO. | Variable Name |  | Description | Value | Unit | Note
First group
0 |  | Inverter Status | Inverter run state | 0:waiting,
1:normal,
3:fault
1 |  | Ppv H | Input power (high) |  | 0.1W
2 |  | Ppv L | Input power (low) |  | 0.1W
3 |  | Vpv1 | PV1 voltage |  | 0.1V
4 |  | PV1Curr | PV1 input current |  | 0.1A
5 |  | Ppv1 H | PV1 input power(high) |  | 0.1W
6 |  | Ppv1 L | PV1 input power(low) |  | 0.1W
7 |  | Vpv2 | PV2 voltage |  | 0.1V
8 |  | PV2Curr | PV2 input current |  | 0.1A
9 |  | Ppv2 H | PV2 input power (high) |  | 0.1W
10 |  | Ppv2 L | PV2 input power (low) |  | 0.1W
11 |  | Vpv3 | PV3 voltage |  | 0.1V
12 |  | PV3Curr | PV3 input current |  | 0.1A
13 |  | Ppv3 H | PV3 input power (high) |  | 0.1W
14 |  | Ppv3 L | PV3 input power (low) |  | 0.1W
15 |  | Vpv4 | PV4 voltage |  | 0.1V
16 |  | PV4Curr | PV4 input current |  | 0.1A
17 |  | Ppv4 H | PV4 input power (high) |  | 0.1W
18 |  | Ppv4 L | PV4 input power (low) |  | 0.1W
19 |  | Vpv5 | PV5 voltage |  | 0.1V
20 |  | PV5Curr | PV5 input current |  | 0.1A
21 |  | Ppv5H | PV5 input power(high) |  | 0.1W
22 | Ppv5 L | PV5 input power(low) |  | 0.1W
23 | Vpv6 | PV6 voltage |  | 0.1V
24 | PV6Curr | PV6 input current |  | 0.1A
25 | Ppv6 H | PV6 input power (high) |  | 0.1W
26 | Ppv6 L | PV6 input power (low) |  | 0.1W
27 | Vpv7 | PV7 voltage |  | 0.1V
28 | PV7Curr | PV7 input current |  | 0.1A
29 | Ppv7 H | PV7 input power (high) |  | 0.1W
30 | Ppv7 L | PV7 input power (low) |  | 0.1W
31 | Vpv8 | PV8 voltage |  | 0.1V
32 | PV8Curr | PV8 input current |  | 0.1A
33 | Ppv8 H | PV8 input power (high) |  | 0.1W
34 | Ppv8 L | PV8 input power (low) |  | 0.1W
35 | Pac H | Output power (high) |  | 0.1W
36 | Pac L | Output power (low) |  | 0.1W
37 | Fac | Grid frequency |  | 0.01Hz
38 | Vac1 | Three/single phase grid voltage |  | 0.1V
39 | Iac1 | Three/single phase grid output current |  | 0.1A
40 | Pac1 H | Three/single phase grid output watt |  | 0.1VA
VA (high)
41 | Pac1 L | Three/single phase grid output watt |  | 0.1VA
VA(low)
42 | Vac2 | Three phase grid voltage |  | 0.1V
43 | Iac2 | Three phase grid output current |  | 0.1A
44 | Pac2 H | Three phase grid output power (high) |  | 0.1VA
45 | Pac2 L | Three phase grid output power (low) |  | 0.1VA
46 | Vac3 | Three phase grid voltage |  | 0.1V
47 | Iac3 | Three phase grid output current |  | 0.1A
48 | Pac3 H | Three phase grid output power (high) |  | 0.1VA
49 | Pac3 L | Three phase grid output power (low) |  | 0.1VA
50 | Vac_RS | Three phase grid voltage |  | 0.1V | Line voltage
51 | Vac_ST | Three phase grid voltage |  | 0.1V | Line voltage
52 | Vac_TR | Three phase grid voltage |  | 0.1V | Line voltage
53 | Eactoday H | Today generate energy (high) |  | 0.1kWH
54 | Eac today L | Today generate energy (low) |  | 0.1kWH
55 | Eac total H | Total generate energy (high) |  | 0.1kWH
56 | Eac total L | Total generate energy (low) |  | 0.1kWH
57 | Time total H | Work time total (high) |  | 0.5s
58 | Time total L | Work time total (low) |  | 0.5s
59 | Epv1_today H | PV1Energy today(high) |  | 0.1kWh
60 | Epv1_today L | PV1Energy today (low) |  | 0.1kWh
61 | Epv1_total H | PV1Energy total(high) |  | 0.1kWh
62 | Epv1_total L | PV1Energy total (low) |  | 0.1kWh
63 | Epv2_today H | PV2Energy today(high) |  | 0.1kWh
64 | Epv2_today L | PV2Energy today (low) |  | 0.1kWh
65 | Epv2_total H | PV2Energy total(high) |  | 0.1kWh
66 | Epv2_total L | PV2Energy total (low) |  | 0.1kWh
67 | Epv3_today H | PV3 Energy today(high) |  | 0.1kWh
68 | Epv3_today L | PV3 Energy today (low) |  | 0.1kWh
69 | Epv3_total H | PV3 Energy total(high) |  | 0.1kWh
70 | Epv3_total L | PV3 Energy total (low) |  | 0.1kWh
71 | Epv4_today H | PV4Energy today(high) |  | 0.1kWh
72 | Epv4_today L | PV4Energy today (low) |  | 0.1kWh
73 | Epv4_total H | PV4Energy total(high) |  | 0.1kWh
74 | Epv4_total L | PV4Energy total (low) |  | 0.1kWh
75 | Epv5_today H | PV5Energy today(high) |  | 0.1kWh
76 | Epv5_today L | PV5Energy today (low) |  | 0.1kWh
77 | Epv5_total H | PV5Energy total(high) |  | 0.1kWh
78 | Epv5_total L | PV5Energy total (low) |  | 0.1kWh
79 | Epv6_today H | PV6Energy today(high) |  | 0.1kWh
80 | Epv6_today L | PV6Energy today (low) |  | 0.1kWh
81 | Epv6_total H | PV6Energy total(high) |  | 0.1kWh
82 | Epv6_total L | PV6Energy total (low) |  | 0.1kWh
83 | Epv7_today H | PV7Energy today(high) |  | 0.1kWh
84 | Epv7_today L | PV7Energy today (low) |  | 0.1kWh
85 | Epv7_total H | PV7 Energy total(high) |  | 0.1kWh
86 | Epv7_total L | PV7Energy total (low) |  | 0.1kWh
87 | Epv8_today H | PV8Energy today(high) |  | 0.1kWh
88 | Epv8_today L | PV8Energy today (low) |  | 0.1kWh
89 | Epv8_total H | PV8Energy total(high) |  | 0.1kWh
90 | Epv8_total L | PV8Energy total (low) |  | 0.1kWh
91 | Epv_total H | PV Energy total(high) |  | 0.1kWh
92 | Epv_total L | PV Energy total (low) |  | 0.1kWh
93 | Temp1 | Inverter temperature |  | 0.1C
94 | Temp2 | The inside IPM in inverter Temperature |  | 0.1C
95 | Temp3 | Boost temperature |  | 0.1C
96 | Temp4 |  |  |  | reserved
97 | uwBatVolt_DSP | BatVolt_DSP |  | 0.1V | BatVolt(DSP)
98 | P Bus Voltage | P Bus inside Voltage |  | 0.1V
99 | N Bus Voltage | N Bus inside Voltage |  | 0.1V
100 | IPF | Inverter output PF now | 0-20000
101 | RealOPPercent | Real Output power Percent |  | 1%
102 | OPFullwatt H | Output Maxpower Limited high
103 | OPFullwatt L | Output Maxpower Limited low |  | 0.1W
104 | DeratingMode | DeratingMode | 0:no derate;
1:PV;
2:*;
3:Vac;
4:Fac;
5:Tboost;
6:Tinv;
7:Control;
8:*;
9:*OverBack
ByTime;
105 | Fault code | Inverter fault code | &*1 |  | MAX
106 | Fault Bitcode H | Inverter fault code high | &*8 |  | MAX
107 | Fault Bitcode L | Inverter fault code low
108 | RemoteCtrlEn | / | 0.Load First | / | StoragePow
|  |  | 1.BatFirst |  | er (SPA)
109 | RemoteCtrlPow | / | 2.Grid | / | StoragePow
| er |  |  |  | er (SPA)
110 | Warning bit H | Warning bit H | &*8
111 | Warning bit L | Warning bit L
112 | bINVWarnCode | bINVWarnCode |  |  | MAX
| EACharge_Today | ACCharge energy today |  | 0.1kwh | Storage
| _H |  |  |  | Power
113 | real Power | real Power Percent | 0-100 | % | MAX
Percent
| EACharge_Today | ACCharge energy today |  | 0.1kwh | Storage
| _L |  |  |  | Power
114 | inv start delay time | inv start delay time |  |  | MAX
| EACharge_Total | ACCharge energy total |  | 0.1kwh | Storage
| _H |  |  |  | Power
115 | bINVAllFaultCod e | bINVAllFaultCode |  |  | MAX
| EACharge_Total | ACCharge energy total |  | 0.1kwh | Storage
| _L |  |  |  | Power
116 | AC charge | Grid power to local load |  | 0.1kwh | Storage
| Power_H |  |  |  | Power
117 | AC charge | Grid power to local load |  |  | 0.1kwh | Storage
| Power_L |  |  |  |  | Power
118 | Priority | 0:Load First |  |  |  | Storage
|  | 1:Battery First |  |  |  | Power
2:Grid First
119 | Battery Type | 0：Lead-acid |  |  |  | Storage
|  | 1：Lithium battery |  |  |  | Power
120 | AutoProofreadC | Aging mode 自动校准命令 |  |  |  | Storage
| MD |  |  |  |  | Power
… | reserved |  |  |  |  | reserved
124 | reserved |  |  |  |  | reserved
Second group
125 | PID PV1+ Voltage |  | PID PV1PE Volt | 0~1000V | 0.1V
126 | PID PV1+ Current |  | PID PV1PE Curr | -10~10mA | 0.1mA
127 | PID PV2+ Voltage |  | PID PV2PE Volt | 0~1000V | 0.1V
128 | PID PV2+ Current |  | PID PV2PE Curr | -10~10mA | 0.1mA
129 | PID PV3+ Voltage |  | PID PV3PE Volt | 0~1000V | 0.1V
130 | PID PV3+ Current |  | PID PV3PE Curr | -10~10mA | 0.1mA
131 | PID PV4+ Voltage |  | PID PV4PE Volt | 0~1000V | 0.1V
132 | PID PV4+ Current |  | PID PV4PE Curr | -10~10mA | 0.1mA
133 | PID PV5+ Voltage |  | PID PV5PE Volt | 0~1000V | 0.1V
134 | PID PV5+ Current |  | PID PV5PE Curr | -10~10mA | 0.1mA
135 | PID PV6+ Voltage |  | PID PV6PE Volt | 0~1000V | 0.1V
136 | PID PV6+ Current |  | PID PV6PE Curr | -10~10mA | 0.1mA
137 | PID PV7+ Voltage |  | PID PV7PE Volt | 0~1000V | 0.1V
138 | PID PV7+ Current |  | PID PV7PE Curr | -10~10mA | 0.1mA
139 | PID PV8+ Voltage |  | PID PV8PE Volt | 0~1000V | 0.1V
140 | PID PV8+ Current |  | PID PV8PE Curr | -10~10mA | 0.1mA
141 | PID Status |  | Bit0~7:PID Working Status | 0~3
1:Wait Status
2:Normal Status
3:Fault Status
Bit8~15:Reversed
142 | V _String1 |  | PV String1 voltage |  | 0.1V
143 | Curr _String1 |  | PV String1 current | -15~15A | 0.1A
144 | V _String2 |  | PV String2 voltage |  | 0.1V
145 | Curr _String2 |  | PV String2 current | -15~15A | 0.1A
146 | V _String3 |  | PV String3 voltage |  | 0.1V
147 | Curr _String3 |  | PV String3 current | -15~15A | 0.1A
148 | V _String4 |  | PV String4 voltage |  | 0.1V
149 | Curr _String4 | PV String4 current | -15~15A | 0.1A
150 | V _String5 | PV String5 voltage |  | 0.1V
151 | Curr _String5 | PV String5 current | -15~15A | 0.1A
152 | V _String6 | PV String6 voltage |  | 0.1V
153 | Curr _String6 | PV String6 current | -15~15A | 0.1A
154 | V _String7 | PV String7 voltage |  | 0.1V
155 | Curr _String7 | PV String7 current | -15~15A | 0.1A
156 | V _String8 | PV String8 voltage |  | 0.1V
157 | Curr _String8 | PV String8 current | -15A~15A | 0.1A
158 | V _String9 | PV String9 voltage |  | 0.1V
159 | Curr _String9 | PV String9 current | -15A~15A | 0.1A
160 | V _String10 | PV String10 voltage |  | 0.1V
161 | Curr _String10 | PV String10 current | -15~15A | 0.1A
162 | V _String11 | PV String11 voltage |  | 0.1V
163 | Curr _String11 | PV String11 current | -15~15A | 0.1A
164 | V _String12 | PV String12 voltage |  | 0.1V
165 | Curr _String12 | PV String12 current | -15~15A | 0.1A
166 | V _String13 | PV String13 voltage |  | 0.1V
167 | Curr _String13 | PV String13 current | -15A~15A | 0.1A
168 | V _String14 | PV String14 voltage |  | 0.1V
169 | Curr _String14 | PV String14 current | -15~15A | 0.1A
170 | V _String15 | PV String15 voltage |  | 0.1V
171 | Curr _String15 | PV String15 current | -15~15A | 0.1A
172 | V _String16 | PV String16 voltage |  | 0.1V
173 | Curr _String16 | PV String16 current | -15~15A | 0.1A
174 | StrUnmatch | Bit0~15: String1~16 unmatch |  |  | suggestive
175 | StrCurrentUnblan ce | Bit0~15: String1~16 current unblance |  |  | suggestive
176 | StrDisconnect | Bit0~15: String1~16 disconnect |  |  | suggestive
177 | PIDFaultCode | Bit0:Output over voltage
Bit1: ISO fault
Bit2: BUS voltage abnormal
Bit3~15:reserved
178 | String Prompt | String Prompt
Bit0:String Unmatch
Bit1:StrDisconnect
Bit2:StrCurrentUnblance
Bit3~15:reserved
179 | PV Warning Value | PV Warning Value
180 | DSP075 Warning | DSP075 Warning Value
Value
181 | DSP075 | Fault | DSP075 Fault Value
Value
182 | DSP067 | Debug | DSP067 Debug Data1
Data1
183 | DSP067 | Debug | DSP067 Debug Data2
Data2
184 | DSP067 | Debug | DSP067 Debug Data3
Data3
185 | DSP067 | Debug | DSP067 Debug Data4
Data4
186 | DSP067 | Debug | DSP067 Debug Data5
Data5
187 | DSP067 | Debug | DSP067 Debug Data6
Data6
188 | DSP067 | Debug | DSP067 Debug Data7
Data7
189 | DSP067 | Debug | DSP067 Debug Data8
Data8
190 | DSP075 | Debug | DSP075 Debug Data1
Data1
191 | DSP075 | Debug | DSP075 Debug Data2
Data2
192 | DSP075 | Debug | DSP075 Debug Data3
Data3
193 | DSP075 | Debug | DSP075 Debug Data4
Data4
194 | DSP075 | Debug | DSP075 Debug Data5
Data55
195 | DSP075 | Debug | DSP075 Debug Data6
Data6
196 | DSP075 | Debug | DSP075 Debug Data7
Data7
197 | DSP075 | Debug | DSP075 Debug Data8
Data8
198 | bUSBAgingTestOk |  | USBAgingTestOkFlag | 0-1
Flag
199 | bFlashEraseAging |  | FlashEraseAgingOkFlag | 0-1
OkFlag
200 | PVISO |  | PVISOValue |  | KΩ
201 | R_DCI |  | R DCI Curr |  | 0.1mA
202 | S_DCI |  | S DCI Curr |  | 0.1mA
203 | T_DCI |  | T DCI Curr |  | 0.1mA
204 | PID_Bus | PIDBusVolt |  | 0.1V
205 | GFCI | GFCI Curr |  | mA
206 | SVG/APF | SVG/APF Status+SVGAPFEqualRatio | High 8 bit： SVGAPFEqua lRatio
| Status+SVGAPFEq ualRatio |  | Low 8 bit：
SVG/APF
Status
0:None
1:SVG Run
2:APF Run
3:SVG/APF
Run
207 | CT_I _R | R phase load side current for SVG |  | 0.1A
208 | CT_I _S | S phase load side current for SVG |  | 0.1A
209 | CT_I _T | T phase load side current for SVG |  | 0.1A
210 | CT_Q _R H | R phase load side output reactive power for SVG(High) |  | 0.1Var
211 | CT_Q _R L | R phase load side output reactive power for SVG(low) |  | 0.1Var
212 | CT_Q _S H | S phase load side output reactive power for SVG(High) |  | 0.1Var
213 | CT_Q _S L | S phase load side output reactive power for SVG(low) |  | 0.1Var
214 | CT_Q _T H | T phase load side output reactive power for SVG(High) |  | 0.1Var
215 | CT_Q _T L | T phase load side output reactive power for SVG(low) |  | 0.1Var
216 | CT HAR_I_R | R phase load side harmonic |  | 0.1A
217 | CT HAR_I_S | S phase load side harmonic |  | 0.1A
218 | CT HAR_I_T | T phase load side harmonic |  | 0.1A
219 | COMP_Q _R H | R phase compensate reactive power for SVG(High) |  | 0.1Var
220 | COMP_Q _R L | R phase compensate reactive power for SVG(low) |  | 0.1Var
221 | COMP_Q _S H | S phase compensate reactive power for SVG(High) |  | 0.1Var
222 | COMP_Q _S L | S phase compensate reactive power for SVG(low) |  | 0.1Var
223 | COMP_Q _T H | T phase compensate reactive power for SVG(High) |  | 0.1Var
224 | COMP_Q _T L | T phase compensate reactive power |  | 0.1Var
for SVG(low)
225 | COMP HAR_I_R | R phase compensate harmonic for |  |  |  |  | 0.1A
SVG
226 | COMP HAR_I_S | S phase compensate harmonic for |  |  |  |  | 0.1A
SVG
227 | COMP HAR_I_T | T phase compensate harmonic for |  |  |  |  | 0.1A
SVG
228 | bRS232AgingTest | RS232AgingTestOkFlag |  |  | 0-1
OkFlag
229 | bFanFaultBit | Bit0: Fan 1 fault bit Bit1: Fan 2 fault bit
Bit2: Fan 3 fault bit
Bit3: Fan 4 fault bit
Bit4-7: Reserved
230 | Sac H | Output apparent power H |  |  |  |  | 0.1W
231 | Sac L | Output apparent power L |  |  |  |  | 0.1W
232 | ReActPowerH | Real Output Reactive Power H |  |  | Int32 |  | 0.1W
233 | ReActPowerL | Real Output Reactive Power L
234 | ReActPowerMaxH | Nominal Output Reactive Power H |  |  |  |  | 0.1var
235 | ReActPowerMaxL | Nominal Output Reactive Power L
236 | ReActPower_Total | Reactive power generation |  |  |  |  | 0.1kwh
H
237 | ReActPower_Total | Reactive power generation
L
… | 238~249 | [7 empty] | reserved
Ninth group for Storage power
1000 | uwSysWorkMode |  | System work mode | 0x00:waiting module |  |  |  | Theworkingmode displayed by the monitoring to the customer is：
|  |  |  | 0x01: Self-test mode, optional |  |  |  | 0x00: waiting module
|  |  |  | 0x02 : |  |  |  | 0x01: Self-test mode,
|  |  |  | Reserved 0x03：SysFault module 0x04: Flash module |  |  |  | 0x03:fault module
|  |  |  | 0x05 ： |  |  |  | 0x04:flash module
|  |  |  | PVBATOnline module, |  |  |  | 0x05¦0x06¦0x07¦0 x08:normal module
0x06 ：
BatOnline
module,
0x07 ：
PVOfflineMod e module,
0x08 ：
BatOfflineMo de module,
1001 | Systemfault word0 | System fault word0 |  |  | Please refer to thefault description | of
Hybrid
1002 | Systemfault word1 | System fault word1
1003 | Systemfault word2 | System fault word2
1004 | Systemfault word3 | System fault word3
1005 | Systemfault word4 | System fault word4
1006 | Systemfault word5 | System fault word5
1007 | Systemfault word6 | System fault word6
1008 | Systemfault word7 | System fault word7
1009 | Pdischarge1 H | Discharge power(high) |  | 0.1W
1010 | Pdischarge1 L | Discharge power (low) |  | 0.1W
1011 | Pcharge1 H | Charge power(high) |  | 0.1W
1012 | Pcharge1 L | Charge power (low) |  | 0.1W
1013 | Vbat | Battery voltage |  | 0.1V
1014 | SOC | State of charge Capacity | 0-100 | 1% | lith/leadacid
1015 | Pactouser R H | AC power to user H |  | 0.1w
1016 | Pactouser R L | AC power to user L |  | 0.1w
1017 | Pactouser S H | Pactouser S H |  | 0.1w
1018 | Pactouser S L | Pactouser S L |  | 0.1w
1019 | Pactouser T H | Pactouser T H |  | 0.1w
1020 | Pactouser T L | Pactouser T H |  | 0.1w
1021 | PactouserTotal H | AC power to user total H |  | 0.1w
1022 | PactouserTotal L | AC power to user total L |  | 0.1w
1023 | Pac to grid R H | AC power to grid H |  | 0.1w | Ac output
1024 | Pac to grid R L | AC power to grid L |  | 0.1w
1025 | Pactogrid S H |  |  | 0.1w
1026 | Pactogrid S L |  |  | 0.1w
1027 | Pactogrid T H |  |  | 0.1w
1028 | Pactogrid T L |  |  | 0.1w
1029 | Pactogrid total H | AC power to grid total H |  | 0.1w
1030 | Pactogrid total L | AC power to grid total L |  | 0.1w
1031 | PLocalLoad R H | INV power to local load H |  | 0.1w
1032 |  | PLocalLoad R L |  | INV power to local load L |  |  | 0.1w
1033 |  | PLocalLoad S H |  |  |  |  | 0.1w
1034 |  | PLocalLoad S L |  |  |  |  | 0.1w
1035 |  | PLocalLoadT H |  |  |  |  | 0.1w
1036 |  | PLocalLoadT L |  |  |  |  | 0.1w
1037 |  | PLocalLoad total H |  | INV power to local load total H |  |  | 0.1w
1038 |  | PLocalLoad total L |  | INV power to local load total |  |  | 0.1w
L
1039 |  | IPM Temperature |  | REC Temperature |  |  | 0.1℃ | No use
1040 |  | Battery |  | Battery Temperature |  |  | 0.1℃ | Lead acid/lithium battery temp
Temperature
1041 |  | SP DSP Status |  | SP state |  |  |  | CHG/DisCHG
1042 |  | SP Bus Volt |  | SP BUS2 Volt |  |  | 0.1V
1043
发电量数据
1044 | Etouser_today H |  | Energy to user today high |  |  | 0.1kWh
1045 | Etouser_today L |  | Energy to user today low |  |  | 0.1kWh
1046 | Etouser_total H |  | Energy to user total high |  |  | 0.1kWh
1047 | Etouser_ total L |  | Energy to user total high |  |  | 0.1kWh
1048 | Etogrid_today H |  | Energy to grid today high |  |  | 0.1kWh
1049 | Etogrid _today L |  | Energy to grid today low |  |  | 0.1kWh
1050 | Etogrid _total H |  | Energy to grid total high |  |  | 0.1kWh
1051 | Etogrid _ total L |  | Energy to grid total high |  |  | 0.1kWh
1052 | Edischarge1_toda y H |  | Discharge energy1 today |  |  | 0.1kWh
1053 | Edischarge1_toda y L |  | Discharge energy1 today |  |  | 0.1kWh
1054 | Edischarge1_total |  | Total discharge energy1 (high) |  |  | 0.1kWh
H
1055 | Edischarge1_total |  | Total discharge energy1 (low) |  |  | 0.1kWh
L
1056 | Echarge1_today H |  | Charge1 energy today |  |  | 0.1kWh
1057 | Echarge1_today |  | Charge1 energy today |  |  | 0.1kWh
L
1058 | Echarge1_total H |  | Charge1 energy total |  |  | 0.1kWh
1059 | Echarge1_total L |  | Charge1 energy total |  |  | 0.1kWh
1060 | ELocalLoad_Today |  | Local load energy today |  |  | 0.1kWh
H
1061 | ELocalLoad_Today |  | Local load energy today |  |  | 0.1kWh
L
1062 | ELocalLoad_Total |  | Local load energy total |  |  | 0.1kWh
H
1063 |  | ELocalLoad_Total |  |  |  | Local load energy total |  | 0.1kWh
L
1064 |  | dwExportLimitAp |  |  |  | ExportLimitApparentPower H |  | 0.1kWh | ApparentPower
parentPower
1065 |  | dwExportLimitAp |  |  |  | ExportLimitApparentPower L |  | 0.1kWh | ApparentPower
parentPower
1066 |  | / |  |  |  | / | / | / | reserved
Ups information (offline)
1067 |  | EPS Fac |  |  |  | UPSfrequency | 5000/6000 | 0.01Hz
1068 |  | EPS Vac1 |  |  |  | UPS phase R output voltage | 2300 | 0.1V
1069 |  | EPS Iac1 |  |  |  | UPS phase R output current |  | 0.1A
1070 |  | EPS Pac1 H |  |  |  | UPS phase R output power (H) |  | 0.1VA
1071 |  | EPS Pac1 L |  |  |  | UPS phase R output power (L) |  | 0.1VA
1072 |  | EPS Vac2 |  |  |  | UPS phase S output voltage |  | 0.1V
1073 |  | EPS Iac2 |  |  |  | UPS phase S output current |  | 0.1A | No use
1074 |  | EPS Pac2 H |  |  |  | UPS phase S output power (H) |  | 0.1VA
1075 |  | EPS Pac2 L |  |  |  | UPS phase S output power (L) |  | 0.1VA
1076 |  | EPS Vac3 |  |  |  | UPS phase T output voltage |  | 0.1V
1077 |  | EPS Iac3 |  |  |  | UPS phase T output current |  | 0.1A | No use
1078 |  | EPS Pac3 H |  |  |  | UPS phase T output power (H) |  | 0.1VA
1079 |  | EPS Pac3 L |  |  |  | UPS phase T output power (L) |  | 0.1VA
1080 |  | Loadpercent |  |  |  | Load percent of UPS ouput | 0-100 | 1%
1081 |  | PF |  |  |  | Power factor | 0-2 | 0.1 | Primary Value+1
BMS Infomation
1082 |  |  | BMS_StatusOld |  |  | StatusOld from BMS | Detail information, refer to
1083 |  |  | BMS_Status |  |  | Status from BMS | document:GrowattxxSxx |  | W/R
1084 |  |  | BMS_ErrorOld |  |  | Error info Old from BMS | P ESS Protocol;
1085 |  |  | BMS_Error |  |  | Errorinfomation from BMS
1086 |  |  | BMS_SOC |  |  | SOC from BMS |  |  | R SPH6K
1087 |  |  | BMS_BatteryVo |  | l | Battery voltage from BMS |  |  | R SPH6K
t
1088 |  |  | BMS_BatteryCu |  | r | Battery current from BMS
r
1089 |  |  | BMS_BatteryTe mp |  |  | Battery temperature from BMS
1090 |  |  | BMS_MaxCurr |  |  | Max. charge/discharge current from BMS (pylon)
1091 |  |  | BMS_GaugeRM |  |  | Gauge RM from BMS
1092 |  |  | BMS_GaugeFCC |  |  | Gauge FCC from BMS
1093 |  |  | BMS_FW
1094 | BMS_DeltaVolt | Delta V from BMS
1095 | BMS_CycleCnt | Cycle Count from BMS
1096 | BMS_SOH | SOH from BMS
1097 | BMS_ConstantV | CV voltage from BMS
olt
1098 | BMS_WarnInfoO | Warning info old from BMS
ld
1099 | BMS_WarnInfo | Warning info from BMS
1100 | BMS_GaugeICCu | Gauge IC current from BMS
rr
1101 | BMS_MCUVersi on | MCU Software version from BMS
1102 | BMS_GaugeVers | Gauge Version from BMS
ion
1103 | BMS_wGaugeFR | Gauge FR Version L16 from BMS
Version_ L
1104 | BMS_wGaugeFR | Gauge FR Version H16 from BMS
Version_H
1105 | BMS_BMSInfo | BMSInformation from BMS
1106 | BMS_PackInfo | Pack Information from BMS
1107 | BMS_UsingCap | Using Cap from BMS
1108 | BMS_ Cell1_Volt | Cell1_Voltage from BMS
1109 | BMS_ Cell2_Volt | Cell_Voltage from BMS
…
1123 | BMS_ | Cell16_Voltage from BMS
Cell16_Volt
1124 | AC Charge | AC Charge Energy today | kwh |  | Energy today
Energy Today H
Ninth group reserved for storage power
1125 | ACCharge | AC Charge Energy today | kwh
Energy TodayL
1126 | AC Charge |  |  |  | Energy total
Energy Total H
1127 | ACCharge
Energy Total L
1128 | AC Charge | AC Charge Power | W
Power H
1129 | AC Charge | AC Charge Power | w
Power L
1130 | 70% INV Power | uwGridPower_70_AdjEE_SP | W
adjust
1131 | Extra AC Power to grid_H | Extra inverte AC Power to grid | For SPA connect inverter |  | SPA used
High
1132 | Extra AC Power to grid_L | Extrainverte AC Power to grid Low |  |  | SPA used
1133 | Eextra_today H | Extra inverter PowerTOUser_Extra today (high) | R | 0.1kWh | SPA used
1134 | Eextra_today L | Extra inverter PowerTOUser_Extra today (low) | R | 0.1kWh | SPA used
1135 | Eextra_total H | Extra inverter PowerTOUser_Extra total(high) |  | 0.1kWh | SPA used
1136 | Eextra_total L | Extra inverter PowerTOUser_Extra total(low) |  | 0.1kWh | SPA used
1137 | Esystem_today | System electric energy today H |  | 0.1kWh | SPA used System electric energy today H
H
1138 | Esystem_ today | System electric energy today L |  | 0.1kWh | SPA used
| L |  |  |  | System electric energy today L
1139 | Esystem_total H | System electric energy total H |  | 0.1kWh | SPA used
System electric energy total H
1140 | Esystem_ total L | System electric energy total L |  | 0.1kWh | SPA used
System electric energy total L
…… | / | / | / | / | reversed
1249 | / | / | / | / | reversed
thirteen group for Storage power’s SPA
2000 |  | Inverter Status | Inverter run state |  | 0:waiting, |  | SPA
1:normal,
3:fault
…… |  | reversed
2035 |  | Pac H | Output power (high) |  |  | 0.1W | SPA
2036 |  | Pac L | Output power (low) |  |  | 0.1W | SPA
2037 |  | Fac | Grid frequency |  |  | 0.01Hz | SPA
2038 |  | Vac1 | Three/single phase grid voltage |  |  | 0.1V | SPA
2039 |  | Iac1 | Three/single phase grid output current |  |  | 0.1A | SPA
2040 |  | Pac1 H | Three/single phase grid output watt |  |  | 0.1VA | SPA
VA (high)
2041 |  | Pac1 L | Three/single phase grid output watt |  |  | 0.1VA | SPA
VA(low)
…… | reversed
2053 | Eac today H | Today generate energy (high) |  | 0.1kWH | SPA
2054 | Eac today L | Today generate energy (low) |  | 0.1kWH | SPA
2055 | Eac total H | Total generate energy (high) |  | 0.1kWH | SPA
2056 | Eac total L | Total generate energy (low) |  | 0.1kWH | SPA
2057 | Time total H | Work time total (high) |  | 0.5s | SPA
2058 | Time total L | Work time total (low) |  | 0.5s | SPA
…… | reversed
2093 | Temp1 | Inverter temperature |  | 0.1C | SPA
2094 | Temp2 | The inside IPM in inverter Temperature |  | 0.1C | SPA
2095 | Temp3 | Boost temperature |  | 0.1C | SPA
2096 | Temp4 |  |  |  | reserved
2097 | uwBatVolt_DSP | BatVolt_DSP |  | 0.1V | BatVolt(DSP)
2098 | P Bus Voltage | P Bus inside Voltage |  | 0.1V | SPA
2099 | N Bus Voltage | N Bus inside Voltage |  | 0.1V | SPA
2100 | RemoteCtrlEn | / | 0.Load First | / | Remote setup enable
1.BatFirst
2101 | RemoteCtrlPow | / | 2.Grid | / | Remotely set power
er
2102 | Extra AC Power to grid_H | Extra inverte AC Power to grid High | For SPA connect inverter |  | SPA used
2103 | Extra AC Power to grid_L | Extrainverte AC Power to grid Low |  |  | SPA used
2104 | Eextra_today H | Extra inverter PowerTOUser_Extra today (high) | R | 0.1kWh | SPA used
2105 | Eextra_today L | Extra inverter PowerTOUser_Extra today (low) | R | 0.1kWh | SPA used
2106 | Eextra_total H | Extra inverter |  | 0.1kWh | SPA used
PowerTOUser_Extratotal(high)
2107 | Eextra_total L | Extra inverter PowerTOUser_Extra total(low) |  | 0.1kWh | SPA used
2108 | Esystem_today | System electric energy today H |  | 0.1kWh | SPA used System electric energy today H
H
2109 | Esystem_ today | System electric energy today L |  | 0.1kWh | SPA used System electric
L
energy today L
2110 | Esystem_total H | System electric energy total H |  | 0.1kWh |  | SPA used System electric energy total
H
2111 | Esystem_ total L | System electric energy total L |  | 0.1kWh |  | SPA used System electric energy total
L
2112 | EACharge_Today | ACCharge energy today |  | 0.1kwh |  | Storage
| _H |  |  |  |  | Power
2113 | EACharge_Today | ACCharge energy today |  | 0.1kwh |  | Storage
| _L |  |  |  |  | Power
2114 | EACharge_Total | ACCharge energy total |  | 0.1kwh |  | Storage
| _H |  |  |  |  | Power
2115 | EACharge_Total | ACCharge energy total |  | 0.1kwh |  | Storage
| _L |  |  |  |  | Power
2116 | AC charge | Grid power to local load |  | 0.1kwh |  | Storage
| Power_H |  |  |  |  | Power
2117 | AC charge | Grid power to local load |  | 0.1kwh |  | Storage
| Power_L |  |  |  |  | Power
2118 | Priority | 0:Load First |  |  |  | Storage
|  | 1:Battery First |  |  |  | Power
2:Grid First
2119 | Battery Type | 0：Lead-acid |  |  |  | Storage
|  | 1：Lithium battery |  |  |  | Power
2120 | AutoProofreadC | Aging mode |  |  |  | Storage
| MD |  |  |  |  | Power
… | reserved |  |  |  |  | reserved
2124 | reserved |  |  |  |  | reserved
Use for TL-X and TL-XH
3000 | Inverter Status | Inverter run state
High 8 bits mode (specific mode)
0: Waiting module
1: Self-test mode, optional
2: Reserved
3：SysFault module
4: Flash module
5：PVBATOnline module:
6：BatOnline module
7：PVOfflineMode
8：BatOfflineMode
The lower 8 bits indicate the machine status (web page display)
0: StandbyStatus;
1: NormalStatus;
3: FaultStatus
4：FlashStatus;
3001 | Ppv H | PV total power |  | 0.1W
3002 | Ppv L
3003 | Vpv1 | PV1 voltage |  | 0.1V
3004 | Ipv1 | PV1 input current |  | 0.1A
3005 | Ppv1 H | PV1 power |  | 0.1W
3006 | Ppv1 L
3007 | Vpv2 | PV2 voltage |  | 0.1V
3008 | Ipv2 | PV2 input current |  | 0.1A
3009 | Ppv2 H | PV2 power |  | 0.1W
3010 | Ppv2 L
3011 | Vpv3 | PV3 voltage |  | 0.1V
3012 | Ipv3 | PV3 input current |  | 0.1A
3013 | Ppv3 H | PV3 power |  | 0.1W
3014 | Ppv3 L
3015 | Vpv4 | PV4 voltage
3016 | Ipv4 | PV4 input current
3017 | Ppv4H | PV4 power
3018 | Ppv4L
3019 | Reserved
3020 | Reserved
3021 | Reserved
3022 | Reserved
3023 | Pac H | Output power |  | 0.1W | Output power
3024 | Pac L
3025 | Fac | Grid frequency |  | 0.01Hz | Grid frequency
3026 | Vac1 | Three/single phase grid voltage |  | 0.1V | Three/single
phase grid
voltage
3027 | Iac1 | Three/single phase grid output current |  | 0.1A | Three/single phase grid output current
3028 | Pac1 H | Three/single phase grid output watt |  | 0.1VA | Three/single phase grid output watt
3029 | Pac1 L | VA |  |  | VA
3030 | Vac2 | Three phase grid voltage |  | 0.1V | Three phase grid voltage
3031 | Iac2 | Three phase grid output current |  | 0.1A | Three phase grid output current
3032 | Pac2 H | Three phase grid output power |  | 0.1VA | Three phase grid output power
3033 | Pac2 L
3034 | Vac3 | Three phase grid voltage |  | 0.1V | Three phase grid voltage
3035 | Iac3 | Three phase grid output current |  | 0.1A | Three phase grid output current
3036 | Pac3 H | Three phase grid output power |  | 0.1VA | Three phase grid output power
3037 | Pac3 L
3038 | Vac_RS | Three phase grid voltage |  | 0.1V
3039 | Vac_ST | Three phase grid voltage |  | 0.1V
3040 | Vac_TR | Three phase grid voltage |  | 0.1V
3041 | Ptouser total H | Total forward power |  | 0.1W | Total forward power
3042 | Ptouser total L
3043 | Ptogrid total H | Total reverse power |  | 0.1W | Total reverse power
3044 | Ptogrid total L
3045 | Ptoload total H | Total load power |  | 0.1W | Total load power
3046 | Ptoload total L
3047 | Time total H | Work time total |  | 0.5s
3048 | Time total L
3049 | Eac today H | Today generate energy |  | 0.1kWh | Today generate energy
3050 | Eac today L
3051 | Eac total H | Total generate energy |  | 0.1kWh | Total generate energy
3052 | Eac total L
3053 | Epv_total H | PV energy total |  | 0.1kWh | PV energy total
3054 | Epv_total L
3055 | Epv1_today H | PV1 energy today |  | 0.1kWh
3056 | Epv1_today L
3057 | Epv1_total H | PV1 energy total |  | 0.1kWh
3058 | Epv1_total L
3059 | Epv2_today H | PV2 energy today |  | 0.1kWh
3060 | Epv2_today L
3061 | Epv2_total H | PV2 energy total |  | 0.1kWh
3062 | Epv2_total L
3063 | Epv3_today H | PV3 energy today |  | 0.1kWh
3064 | Epv3_today L
3065 | Epv3_total H | PV3 energy total |  | 0.1kWh
3066 | Epv3_total L
3067 | Etouser_today H | Today energy to user |  | 0.1kWh | Today energy to user
3068 | Etouser_today L
3069 | Etouser_total H | Total energy to user |  | 0.1kWh | Total energy to user
3070 | Etouser_total L
3071 | Etogrid_today H | Today energy to grid |  | 0.1kWh | Today energy to grid
3072 | Etogrid_today L
3073 | Etogrid_total H | Total energy to grid |  | 0.1kWh | Total energy to grid
3074 | Etogrid_total L
3075 | Eload_today H | Today energy of user load |  | 0.1kWh | Today energy of user load
3076 | Eload_today L
3077 | Eload_total H | Total energy of user load |  | 0.1kWh | Total energy of user load
3078 | Eload_total L
3079 | Reserved
3080 | Reserved
3081 | Reserved
3082 | Reserved
3083 | Reserved
3084 | Reserved
3085 | Reserved
3086 | DeratingMode | DeratingMode |  |  | 0:cNOTDerate
1:cPVHighDer
ate
2: cPowerCon stantDerate 3: cGridVHigh
Derate
4:cFreqHighD
erate
5:cDcSoureM
odeDerate
6:cInvTemprD
erate
7:cActivePow
erOrder
8:cLoadSpeed
Process 9:cOverBack
byTime 10:cInternalT emprDerate 11:cOutTemp
rDerate
12:cLineImpe
CalcDerate 13: cParallelA ntiBackflowD erate
14:cLocalAnti BackflowDera
te
15:cBdcLoadP riDerate
16:cChkCTErr
Derate
3087 | ISO | PV ISO value |  | 1KΩ
3088 | DCI_R | R DCI Curr |  | 0.1mA
3089 | DCI_S | S DCI Curr |  | 0.1mA
3090 | DCI_T | T DCI Curr |  | 0.1mA
3091 | GFCI | GFCI Curr |  | 1mA
3092 | Reserved
3093 | Temp1 | Inverter temperature |  | 0.1℃
3094 | Temp2 | The inside IPM in inverter temperature |  | 0.1℃
3095 | Temp3 | Boost temperature |  | 0.1℃
3096 | Temp4 | Reserved |  | 0.1℃
3097 | Temp5 | Commmunication broad temperature |  | 0.1℃
3098 | P Bus Voltage | P Bus inside Voltage |  | 0.1V
3099 | N Bus Voltage | N Bus inside Voltage |  | 0.1V
3100 | IPF | Inverter output PF now |  |  | 0-20000
3101 | RealOPPercent | Real Output power Percent |  | 1% | 1~100
3102 | OPFullwatt H | Output Maxpower Limited |  | 0.1W | Output
Maxpower
3103 | OPFullwatt L |  |  |  | Limited
3104 | StandbyFlag | Inverter standby flag |  | bitfield | bit0:turn off
Order； bit1:PV Low； bit2:AC Volt/Freq out of scope； bit3~bit7 ：
Reserved
3105 | Fault code | Inverter fault code
3106 | Warning code | Inverter Warning code
3107 | Systemfault word0 | System fault word0 |  | bitfield
3108 | Systemfault word1 | System fault word1 |  | bitfield
3109 | Systemfault word2 | System fault word2 |  | bitfield
3110 | Systemfault word3 | System fault word3 |  | bitfield
3111 | Systemfault word4 | System fault word4 |  | bitfield
3112 | Systemfault word5 | System fault word5 |  | bitfield
3113 | Systemfault word6 | System fault word6 |  | bitfield
3114 | Systemfault word7 | System fault word7 |  | bitfield
3115 | inv start delay time | inv start delay time |  | 1S | inv start delay time
3116 | Reserved
3117 | Reserved
3118 | BDC_OnOffState | BDC connect state |  |  | 0:No BDC
Connect
1:BDC1
Connect
2:BDC2
Connect
3:BDC1+BDC2
Connect
3119 | DryContactState | Current status of DryContact |  |  | Current
status of
DryContact
0: turn off;
1: turn on;
3120 | Reserved
3121 | Reserved
3122 | Reserved
3123 | Reserved
3124 | Reserved
3125 | Edischr_today H | Today discharge energy |  | 0.1kWh | Today discharge energy
3126 | Edischr_today L
3127 | Edischr_total H | Total discharge energy |  | 0.1kWh | Total discharge energy
3128 | Edischr_total L
3129 | Echr_today H | Charge energy today |  | 0.1kWh | Charge energy today
3130 | Echr_today L
3131 | Echr_total H | Charge energy total |  | 0.1kWh | Charge energy total
3132 | Echr_total L
3133 | Eacchr_today H | Today energy of AC charge |  | 0.1kWh | Today energy of AC charge
3134 | Eacchr_today L
3135 | Eacchr_total H | Total energy of AC charge |  | 0.1kWh | Total energy of AC charge
3136 | Eacchr_total L
3137 | Reserved
3138 | Reserved
3139 | Reserved
3140 | Reserved
3141 | Reserved
3142 | Reserved
3143 | Reserved
3144 | Priority | Word Mode |  |  | 0 LoadFirst
1
BatteryFirs t
2 GridFirst
3145 | EPS Fac | UPS frequency |  | 0.01Hz
3146 | EPS Vac1 | UPS phase R output voltage |  | 0.1V
3147 | EPS Iac1 | UPS phase R output current |  | 0.1A
3148 | EPS Pac1 H | UPS phase R output power |  | 0.1VA
3149 | EPS Pac1 L
3150 | EPS Vac2 | UPS phase S output voltage |  | 0.1V
3151 | EPS Iac2 | UPS phase S output current |  | 0.1A
3152 | EPS Pac2 H | UPS phase S output power |  | 0.1VA
3153 | EPS Pac2 L
3154 | EPS Vac3 | UPS phase T output voltage |  | 0.1V
3155 | EPS Iac3 | UPS phase T output current |  | 0.1A
3156 | EPS Pac3 H | UPS phase T output power |  | 0.1VA
3157 | EPS Pac3 L
3158 | EPS Pac H | UPS output power |  | 0.1VA
3159 | EPS Pac L
3160 | Loadpercent | Load percent of UPS ouput |  | 0.1%
3161 | PF | Power factor |  | 0.1
3162 | DCV | DC voltage |  | 1mV
3163 | Reserved
3164 | Reserved
3165 | Reserved
3166 | SysState_Mode | System work State and mode 高 8 位表示模式； |  |  | BDC1
0：No charge and discharge；
1：charge；
2：Discharge；
低 8 位表示状态；
0: StandbyStatus;
1: NormalStatus;
2: FaultStatus
3：FlashStatus;
3167 | FaultCode | Storge device fault code
3168 | WarnCode | Storge device warning code
3169 | Vbat | Battery voltage |  | 0.01V
3170 | Ibat | Battery current |  | 0.1A
3171 | SOC | State of charge Capacity |  | 1%
3172 | Vbus1 | BUS1 voltage |  | 0.1V
3173 | Vbus2 | BUS2 voltage |  | 0.1V
3174 | Ibb | BUCK-BOOST Current |  | 0.1A
3175 | Illc | LLC Current |  | 0.1A
3176 | TempA | Temperture A |  | 0.1℃
3177 | TempB | Temperture B |  | 0.1℃
3178 | Pdischr H | Discharge power |  | 0.1W
3179 | Pdischr L
3180 | Pchr H | Charge power |  | 0.1W
3181 | Pchr L
3182 | Edischr_total H | Discharge total energy of storge device |  | 0.1kWh
3183 | Edischr_total L
3184 | Echr_total H | Charge total energy of storge device |  | 0.1kWh
3185 | Echr_total L
3186 | Reserved | Reserved
3187 | BDC1_Flag | BDC mark (charge and discharge, fault alarm code)
Bit0: ChargeEn; BDC allows charging Bit1: DischargeEn; BDC allows discharge
Bit2~7: Resvd; reserved Bit8~11: WarnSubCode; BDC sub-warning code
Bit12~15: FaultSubCode; BDC sub-error code
3188 | Reserved
3189 | SysState_Mode | System work State and mode
高 8 位表示模式；
0：No charge and discharge；
1：charge；
2：Discharge；
低 8 位表示状态；
0: StandbyStatus;
1: NormalStatus;
2: FaultStatus
3：FlashStatus；
3190 | FaultCode | Storge device fault code
3191 | WarnCode | Storge device warning code |  |  | BDC2
3192 | Vbat | Battery voltage |  | 0.01V
3193 | Ibat | Battery current |  | 0.1A
3194 | SOC | State of charge Capacity |  | 1%
3195 | Vbus1 | BUS1 voltage |  | 0.1V
3196 | Vbus2 | BUS2 voltage |  | 0.1V
3197 | Ibb | BUCK-BOOST Current |  | 0.1A
3198 | Illc | LLC Current |  | 0.1A
3199 | TempA | Temperture A |  | 0.1℃
3200 | TempB | Temperture B |  | 0.1℃
3201 | Pdischr H | Discharge power |  | 0.1W
3202 | Pdischr L
3203 | Pchr H | Charge power |  | 0.1W
3204 | Pchr L
3205 | Edischr_total H | Discharge total energy of storge device |  | 0.1kWh
3206 | Edischr_total L
3207 | Echr_total H | Charge total energy of storge device |  | 0.1kWh
3208 | Echr_total L
3209 | reserved | reserved
3210 | BDC2_Flag | BDC mark (charge and discharge, fault alarm code)
Bit0: ChargeEn; BDC allows charging Bit1: DischargeEn; BDC allows discharge
Bit2~7: Resvd; reserved Bit8~11: WarnSubCode; BDC sub-warning code
Bit12~15: FaultSubCode; BDC sub-error code
3211 | Reserved
3212 | BMS_Status | Status from BMS | R | 1
3213 | BMS_Error | Error information from BMS | R | 1
3214 | BMS_WarnInfo | Warning information from BMS | R | 1
3215 | BMS_SOC | SOC from BMS | R | 1%
3216 | BMS_BatteryVol | Battery voltage from BMS | R | 0.01V
t
3217 | BMS_BatteryCur | Battery current from BMS | R | 0.01A
r
3218 | BMS_BatteryTe mp | Battery temperature from BMS | R | 0.1℃
3219 | BMS_MaxCurr | Max. charge/discharge current from | R | 0.01A
BMS (pylon)
3220 | BMS_DeltaVolt | Delta V from BMS | R | 0.01A
3221 | BMS_CycleCnt | Cycle Count from BMS | R | 1
3222 | BMS_SOH | SOH from BMS | R | 1
3223 | BMS_ConstantV | CV voltage from BMS | R | 0.01V
olt
3224 | BMS_BMSInfo | BMSInformation from BMS | R | 1
3225 | BMS_PackInfo | Pack Information from BMS | R | 1
3226 | BMS_UsingCap | Using Cap from BMS | R | 1
3227 | BMS_FW |  | R | 1
3228 | BMS_MCUVersi on | MCU Software version from BMS | R | 1
3229 | BMSCommType | BMS Communication Type |  |  | BMS
Communicati on Type 0: RS485;
1: CAN;
3230 ~ | Reserved
3233
3234 ~ | Debug data | Debug data
3249
&*1: Inverter fault code Bit:
Fault type value | Means(The message showed on the inverter when the inverter has fault)
1~23 | " Error: 99+x ",
24 | "Auto Test Failed",
25 | "No AC Connection",
26 | "PV Isolation Low",
27 | " Residual I High",
28 | " Output High DCI",
29 | " PV Voltage High",
30 | " AC V Outrange ",
31 | " AC F Outrange ",
32 | " Module Hot "
&*2: The value is 0.1V when the fault is the voltage, is 0.01Hz when the fault is the frequency; &*3:
| High byte value |  | Means |  |  |  | low byte value |  | Means
|  | 0 |  | Auto test stop |  |  |  | 0 |  | No test
|  | 1 |  | Auto test starting |  |  |  | 1 |  | Testing grid volt high pro
|  | 2 |  | Auto testing |  |  |  | 2 |  | Testing grid volt low pro
[8 empty] | 3 |  | Testing grid frequency high pro
[8 empty] | 4 |  | Testing grid frequency low pro
&*4: The variable “wAutoTestResult” and “cTestStepStop”: wAutoTestResult is the step test time counter, when it reach cTestStepStop, this step test will stop and fail.
&*5: Inverter Model: A , could be show: “A1 B0 D0 T0 PF U1 M5 S1” or “1000F151”
Ax=(A&0XF00000000)>>28
Bx=(A&0XF0000000)>>24
Dx=(A&0XF000000)>>20
Tx=(A&0XF00000)>>16
Px=(A&0x00F000)>>12
Ux=(A&0x000F00)>>8
Mx=(A&0x0000F0)>>4
Sx=(A&0x00000F)
&*6: DTC(Device type code)
Code No. | Device type | Note
001xx | Inverter | 1 tracker and 1phase Grid connect PV inverter TL
002xx | Inverter | 2 tracker and 1phase Grid connect PV inverter TL
003xx | Inverter | 1 tracker and 1phase Grid connect PV inverter HF
004xx | Inverter | 2 tracker and 1phase Grid connect PV inverter HF
005xx | Inverter | 1 tracker and 1phase Grid connect PV inverter LF
006xx | Inverter | 2 tracker and 1phase Grid connect PV inverter LF
007xx | Inverter | 1 tracker and 3phase Grid connect PV inverter TL
008xx | Inverter | 2 tracker and 3phase Grid connect PV inverter TL
009xx | Inverter | 1 tracker and 3phase Grid connect PV inverter LF
010xx | Inverter | 2 tracker and 3phase Grid connect PV inverter LF
……
10001 | Data logger | RF-ShineVersion
10002 | Data logger | Web-ShinePano
10003 | Data logger | Web-ShineWebBox
10004 | Data logger | WL-WIFI Module
……
11001 | Confluence box | Confluence box 1
……
&*7: Grid network power control command password:
Inverter is in lock state after power on; change the power control by network command should unlock | inverter first; default pw is XXXXXX;
|  | Unlock: send 0 to 3-135, then send password to 3-136~138; inverter will auto lock in 5min after |  |  | unlocked;
|  | Change PW: unlock first, then send 1 to 3-135, then send new password to 3-136~138; |  | Lock: send 0 or 2 to 3-135;
&*8: Inverter fault code and warning code
Fault code |  |  |  | Warning code
0x00000001 | \ |  | 0x0001 | Fan warning
0x00000002 | Communication error |  | 0x0002 | String communication abnormal
0x00000004 | \ |  | 0x0004 | StrPIDconfig Warning
0x00000008 | StrReverse or StrShort fault |  | 0x0008 | \
0x00000010 | Model Init fault |  | 0x0010 | DSP and COM firmware unmatch
0x00000020 | Grid Volt Sample diffirent |  | 0x0020 | \
0x00000040 | ISO Sample diffirent |  | 0x0040 | SPD abnormal
0x00000080 | GFCI Sample diffirent |  | 0x0080 | GND and N connect abnormal
0x00000100 | \ |  | 0x0100 | PV1 or PV2 circuit short
0x00000200 | \ |  | 0x0200 | PV1 or PV2 boost driver broken
0x00000400 | \ |  | 0x0400 | \
0x00000800 | \ |  | 0x0800 | \
0x00001000 | AFCI Fault |  | 0x1000 | \
0x00002000 | \ |  | 0x2000 | \
0x00004000 | AFCI Module fault |  | 0x4000 | \
0x00008000 | \ |  | 0x8000 | \
0x00010000 | \
0x00020000 | Relay check fault
0x00040000 | \
0x00080000 | \
0x00100000 | \
0x00200000 | Communication error
0x00400000 | Bus Voltage error
0x00800000 | AutoTest fail
0x01000000 | No Utility
0x02000000 | PV Isolation Low
0x04000000 | Residual I High
0x08000000 | Output High DCI
0x10000000 | PV Voltage high
0x20000000 | AC V Outrange
0x40000000 | AC F Outrange
0x80000000 | TempratureHigh
&*9 Warning Value
| Warning Value 1 | Warning Value 2 | Warning Value 3
0x0001 | String1abnormal | PV1ShortCircuit | AC SPD abnormal
0x0002 | String2abnormal | PV2ShortCircuit | DC SPD abnormal
0x0004 | String3abnormal | PV3ShortCircuit
0x0008 | String4abnormal | PV4ShortCircuit
0x0010 | String5abnormal | PV5ShortCircuit
0x0020 | String6abnormal | PV6ShortCircuit
0x0040 | String7abnormal | PV7ShortCircuit
0x0080 | String8abnormal | PV8ShortCircuit
0x0100 | String9abnormal | BT1DriverFault
0x0200 | String10abnormal | BT2DriverFault
0x0400 | String11abnormal | BT3DriverFault
0x0800 | String12abnormal | BT4DriverFault
0x1000 | String13abnormal | BT5DriverFault
0x2000 | String14abnormal | BT6DriverFault
0x4000 | String15abnormal | BT7DriverFault
0x8000 | String16abnormal | BT8DriverFault
&*11: Inverter Model: A , could be show: “S0A D01 B01 T06 P0F U01 M03E8” or
“0A0101060F0103E8”
Sx=(A&0XFF00000000000000)>>56
Dx=(A&0X00FF000000000000)>>48
Bx=(A&0X0000FF0000000000)>>40
Tx=(A&0X000000FF00000000)>>32 Px=(A&0x00000000FF000000)>>24
Ux=(A&0x0000000000FF0000)>>16
Mx=(A&0x000000000000FFFF)
HybridAbnoram/Fault/warning bit definition
(Abnormal:record | event | for | debug,continueworking;fault:record | event | and | show | for
debug,stopworking;Warning:record event and show,continue working)
Word definition |  | Bit definition |  | comment
System fault word0 | Byte0 | MasterForceINVFault | 0 | M3 on/off control
|  | MasterForceSPFault | 1
|  | BusVoltHigh_TZ | 2 | restart PWM
|  | BusVoltHigh_ISR | 3 | restartPWM
|  | reserved | 4
|  | reserved | 5
|  | reserved | 6
|  | reserved | 7
| Byte1 | GridZClossFault | 8 | Grid side abnormal
|  | reserved | 9
|  | reserved | 10
|  | GFCIHigh | 11
|  | GridR_VFault | 12
|  | GridS_VFault | 13
|  | GridT_VFault | 14
|  | GridFFault | 15
System fault word1 | Byte2 | RelayFault | 0 | Grid side abnormal
|  | GFCIDamage | 1
|  | GridR_VLowFault | 2
|  | GridR_VHighFault | 3
|  | GridS_VLowFault | 4
|  | GridS_VHighFault | 5
|  | GridT_VLowFault | 6
|  | GridT_VHighFault | 7
| Byte3 | INVCurrOCP_ISR | 8 | Grid side abnormal
|  | INVCurrOCP_TZ | 9
|  | DCIHigh | 10
|  | reserved | 11
|  | INVR_CurrOCP_Rms | 12
|  | INVS_CurrOCP_Rms | 13
|  | INVT_CurrOCP_Rms | 14
|  | NoUtility | 15
System fault word2 | Byte4 | GridFLowFault | 0 | Grid side abnormal
|  | GridFHighFault | 1
|  | GridVolt_Unbalance_Fault | 2
|  | AC_PLL_Fault | 3
|  | OverLoadFault | 4
|  | reserved | 5
|  | reserved | 6
|  | reserved | 7
| Byte5 | EPS_LineVoltR_Loss | 8 | EPS side abnormal
|  | EPS_LineVoltS_Loss | 9
|  | EPS_LineVoltT_Loss | 10
|  | reserved | 11
|  | reserved | 12
|  | reserved | 13
|  | reserved | 14
|  | reserved | 15
System fault word3 | Byte6 | BatTerminalReversed | 0 | BAT Side abnormal
|  | BatTerminalOpen | 1
BMS Battery Open
|  | BatteryVoltageLow | 2
|  | BatteryVoltageHigh | 3
|  | reserved | 4
|  | reserved | 5
|  | reserved | 6
|  | reserved | 7
| Byte7 | reserved | 8 | BAT Side abnormal
|  | reserved | 9
|  | reserved | 10
|  | reserved | 11
|  | reserved | 12
|  | reserved | 13
|  | reserved | 14
|  | reserved | 15
System fault word4 | Byte8 | reserved | 0 | PV Side Abnormal
|  | reserved | 1
|  | reserved | 2
|  | reserved | 3
|  | reserved | 4
|  | PV1_VoltLowWarn | 5
|  | PV2-VoltLowWarn | 6
|  | reserved | 7
| Byte9 |  | 8 | PV Side Abnormal
9
10
|  | reserved | 11
|  | reserved | 12
|  | reserved | 13
|  | reserved | 14
|  | reserved | 15
System fault word5 | Byte10 | NEDetectFault | 0 | Sytem fault
|  | PVISOFault | 1
|  | reserved | 2
|  | BusVoltHighFault_ISR | 3
|  | BusSampleFault | 4
|  | UHCTFault | 5
|  | AComFault | 6
|  | BComFault | 7
| Byte11 | BusVoltHighFault_TZ | 8 | Sytem fault
|  | AuotTestFault | 9
|  | DCIHigh | 10
|  | NTCOpenFault | 11
|  | reserved | 12
|  | BBHeatsink_TempOver | 13
|  | BBOCP_FaultISR | 14
|  | BBOCP_FaultTZ | 15
System fault word6 | Byte12 | PV1_VoltHighFault | 0 | Sytem fault
|  | PV2_VoltHighFault | 1
|  | BTHeatsink_Overtemp | 2
|  | INVHeatsink_Overtemp | 3
|  | reserved | 4
|  | reserved | 5
|  | reserved | 6
|  | reserved | 7
| Byte13 | BoostDriver1Warn | 8 | System warning
|  | BoostDriver2Warn | 9
|  | WARN104 | 10
|  | PV1_ShortFault | 11
|  | PV2_ShortFault | 12
|  | Meter Comm Loss | 13
|  | PairingTimeOut | 14
|  | CT LN Reversed | 15
System fault word6 | Byte14 | BMS COM Fault | 0
|  | BMS Error: xxx | 1
|  | Battery reversed | 2
|  | BAT NTC Open | 3
|  | SS Timeout | 4
|  | Bat voltage low | 5
|  | Bat T Outrange | 6
|  | BATOutput_Overload | 7
| Byte15 | reserved | 8
|  | reserved | 9
|  | reserved | 10
|  | reserved | 11
|  | reserved | 12
|  | reserved | 13
|  | reserved | 14
|  | reserved | 15
System fault word7 |  | reserved
5 Set address
Refer to the Inverter user manual. Always is :
Knock the pv inverter to let the lcd display to the “COM Addr: xxx”, then double knock, if displays “Move”, you should another double knock, until it displays a address number, then you can give a single knock to change the address, this address will be remembered when the lcd backlight off.
6 Notice
1) It can drive mostly 32 pv inverters for one rs485 comport.
2) There are only read input and hold registers commands even the newest version.
3) App user could only care the input register.
4) App user could not care the holding registers.
5) Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing the other registers;