## Sheet1
Function | Register | Variablename | Description | Write or not | Value | Unit | Initial value | Note
3 | 0 | OnOff | Remote On/Off . On（1）；Off（0）Inverter On（3）；Off（2）BDC | W | 0、1、2、 3 |  | 1 | The inverter can be switched on and off, and the BDC can be switched on and off for the batt ready function.
3 | 1 | SaftyFuncEn | Bit0: SPI enable Bit1: AutoTestStart Bit2: LVFRT enable Bit3:FreqDerating Enable Bit4: Softstart enable Bit5: DRMS enable Bit6:PowerVoltFunc Enable Bit7: HVFRT enable Bit8:ROCOF enable Bit9: Recover FreqDeratingMode Enable Bit10：Split phase enable Bit10~15:预留 | W | 00:00 disable 1: enable |  |  | SPI: system protection interface Bit0~3:for CEI0-21 Bit4~6:for SAA
3 | 2 | PFCMD | Set Holding register3,4,5,99 CMD will be memory or not(1/0), if not, these settings are the initial value. | W | 0or1 |  | 0 | Means these settings will be acting or not when next power on
3 | 3 | ActiveP | Inverter Max output active power percent | W | 0-100 or | % | 255 | 255: power is not be limited
3 | 4 | ReactiveP | Inverter max output reactive power percent | W | -100-100 or 255 |  | % | 255: power is not be limited
3 | 5 | Powerfactor | Inverter output power factor’s 10000 times | W | 0-20000, |  |  | 0
3 | 6 | PmaxH | Normal power (high) |  |  |  | 0.1VA
3 | 7 | PmaxL | Normal power (low) |  |  |  | 0.1VA
3 | 8 | Vnormal | Normal work PV voltage |  |  |  | 0.1V
3 | 9 | FwversionH | Firmware version |  |  |  |  | ASCII
3 | 10 | Fwversion | Firmware version
3 | 11 | FwversionL | Firmware version (low)
3 | 12 | Fwversion2H | Control Firmware version (high) |  |  |  |  | ASCII
3 | 13 | Fwversion2M | Control Firmware version (middle)
3 | 14 | Fwversion2L | Control Firmware version (low)
3 | 15 | LCDlanguage | LCD language | W | 0-5 |  |  | 0: Italian;
3 | 16 | CountrySelected | Country Selected or not | W | 0: need
3 | 17 | Vpvstart | Input start voltage | W |  |  | 0.1V
3 | 18 | Timestart | Start time | W |  |  | 1s
3 | 19 | RestartDelayTime | Restart Delay Time after fault back; | W |  |  | 1s
3 | 20 | wPowerStartSlope | Power start slope | W | 1-1000 | 0.001
3 | 21 | wPowerRestartSlopeEE | Power restart slope | W | 1-1000 | 0.001
3 | 22 | wSelectBaudrate | Select communicationbaudrat e | W | 0-1 |  | 0
3 | 23 | SerialNO | Serial number 1-2 |  |  |  |  | ASCII
3 | 24 | SerialNO | Serial number 3-4
3 | 25 | SerialNO | Serial number 5-6
3 | 26 | SerialNO | Serial number 7-8
3 | 27 | SerialNO | Serial number 9-10
3 | 28 | ModuleH | Inverter Module (high) |  | &*5
3 | 29 | ModuleL | Inverter Module (low) |  | &*5
3 | 30 | ComAddr | Communicate address | W | 1-254 |  | 1
3 | 31 | FlashStart | Update firmware | W | 1
3 | 32 | ResetUserInfo | Reset User Information | W | 0x0001
3 | 33 | Resettofactory | Reset to factory | W | 0x0001
3 | 34 | ManufacturerInfo8 | Manufacturer information (high) |  |  |  |  | ASCII
3 | 35 | ManufacturerInfo7 | Manufacturer information (middle)
3 | 36 | ManufacturerInfo6 | Manufacturer information (low)
3 | 37 | ManufacturerInfo5 | Manufacturer information (high)
3 | 38 | ManufacturerInfo4 | Manufacturer information (middle)
3 | 39 | ManufacturerInfo3 | Manufacturer information (low)
3 | 40 | ManufacturerInfo2 | Manufacturer information (low)
3 | 41 | ManufacturerInfo1 | Manufacturer information (high)
3 | 42 | bfailsafeEn; | G100 fail safe | W | Enable:1 |  |  | English G100 fail safe set
3 | 43 | DTC | Device Type Code |  | &*6
3 | 44 | TP | Input tracker num and output phase num |  |  |  |  | Eg:0x020
3 | 45 | SysYear | System time-year | W | Year offset is 0 |  |  | Local time
3 | 46 | SysMonth | System time- Month | W
3 | 47 | SysDay | System time- Day | W
3 | 48 | SysHour | System time- Hour | W
3 | 49 | SysMin | System time- Min | W
3 | 50 | SysSec | System time- Second | W
3 | 51 | SysWeekly | System Weekly | W | 0-6
3 | 52 | Vaclow | Grid voltage low limit protect | W |  | 0.1V
3 | 53 | Vachigh | Grid voltage high limit protect | W |  | 0.1V
3 | 54 | Faclow | Grid frequency low limit protect | W |  | 0.01
3 | 55 | Fachigh | Grid high | W |  | 0.01
3 | 56 | Vaclow2 | Grid voltage low limit protect 2 | W |  | 0.1V
3 | 57 | Vachigh2 | Grid voltage high limit protect 2 | W |  | 0.1V
3 | 58 | Faclow2 | Grid frequency low limit protect 2 | W |  | 0.01
3 | 59 | Fachigh2 | Grid high frequency limit protect 2 | W |  | 0.01
3 | 60 | Vaclow3 | Grid voltage protect 3 | W |  | 0.1V
3 | 61 | Vachigh3 | Grid voltage protect 3 | W |  | 0.1V
3 | 62 | Faclow3 | Grid frequency limit protect 3 | W |  | 0.01Hz
3 | 63 | Fachigh3 | Grid frequency limit protect 3 | W |  | 0.01Hz
3 | 64 | VaclowC | Grid low voltage limit connect to Grid | W |  | 0.1V
3 | 65 | VachighC | Grid high voltage limit connect to Grid | W |  | 0.1V
3 | 66 | FaclowC | Grid low frequency | W |  | 0.01
3 | 67 | FachighC | Grid high frequency limit connect to Grid | W |  | 0.01
3 | 68 | Vactime | Grid voltage low protect time 1 limit | W |  | Cycle
3 | 69 | Vactime | Grid voltage protect time H lim | W |  |  |  | Cycle
3 | 70 | Vactime | Grid voltage protect time L lim | W |  |  |  | Cycle
3 | 71 | Vactime | Grid voltage protect time H lim | W |  |  |  | Cycle
3 | 72 | Factime | Grid frequency limit protect timeL | W |  | Cycle
3 | 73 | Factime | Grid frequency limit protect timeH | W |  | Cycle
3 | 74 | Factime | Grid frequency limit protect timeL | W |  | Cycle
3 | 75 | Factime | Grid frequency limit protect timeH | W |  | Cycle
3 | 76 | Vactime | Grid voltage protect time L lim | W |  |  |  | Cycle
3 | 77 | Vactime | Grid voltage protect time H lim | W |  |  |  | Cycle
3 | 78 | Factime | Grid frequency limit protect timeL | W |  | Cycle
3 | 79 | Factime | Grid frequency limit protect timeH | W |  | Cycle
3 | 80 | U10min | Volt protection for 10 min | W |  | 0.1V | 1.1Vn
3 | 81 | PVVoltageHighFault | PV Voltage High Fault | W |  | 0.1V
3 | 82 | FWBuildNo5 | Model letter version number (TJ) |  |  |  |  | ASCII
3 | 83 | FWBuildNo | Model letter version number (AA) |  |  |  |  | ASCII
3 | 84 | FWBuildNo4 | DSP1 FW Build No. |  |  |  |  | ASCII
3 | 85 | FWBuildNo3 | DSP2/M0 FW Build No. |  |  |  |  | ASCII
3 | 86 | FWBuildNo2 | CPLD/AFCI FW Build No. |  |  |  |  | ASCII
3 | 87 | FWBuildNo1 | M3 FW Build No. |  |  |  |  | ASCII
3 | 88 | ModbusVersion | Modbus Version
3 | 89 | PFModel | Set PF function Model | W
3 | 90 | GPRSIPFlag | Bit0-3:read:1;Set GPRS | W | Bit0-3:ab
3 | 91 | FreqDerateStart | Frequency derating start point | W |  | 0.01H
3 | 92 | FLrate | Frequency – load limit rate | W | 0-100 | 10tim es
3 | 93 | V1S | CEI021 V1S Q(v) | W | V1S<V2S | 0.1V
3 | 94 | V2S | CEI021 V2S Q(v) | W |  | 0.1V
3 | 95 | V1L | CEI021 V1L Q(v) | W | V1L<V1S | 0.1V
3 | 96 | V2L | CEI021 V2L Q(v) | W | V2L<V1L | 0.1V
3 | 97 | Qlockinpower | Q(v) lock in active power of CEI021 | W | 0-100 | %
3 | 98 | QlockOutpower | Q(v) lock Out active power of CEI021 | W | 0-100 | %
3 | 99 | LIGridV | Lock in gird volt of | W | nVn | 0.1V
3 | 100 | LOGridV | Lock out gird volt of | W | nVn | 0.1V
3 | 101 | PFAdj1 | PF adjust value 1 |  | 4096 is 1
3 | 102 | PFAdj2 | PF adjust value 2 |  | 4096 is 1
3 | 103 | PFAdj3 | PF adjust value 3 |  | 4096 is 1
3 | 104 | PFAdj4 | PF adjust value 4 |  | 4096 is 1
3 | 105 | PFAdj5 | PF adjust value 5 |  | 4096 is 1
3 | 106 | PFAdj6 | PF adjust value 6 |  | 4096 is 1
3 | 107 | QVRPDelayTimeEE | QV Reactive Power | W | 0-30 | 1S | 3S
3 | 108 | OverFDeratDelayTimeEE | Overfrequency derati ngdelaytime | W | 0-20 | 50ms | 0 | System power L
3 | 109 | QpercentMax | Qmax for Q(V) curve | W | 0-1000 | 0.001
3 | 110 | PFLineP1_LP | PF limit line point 1 load percent | W | 0-255 | % |  | 255 means no this point
3 | 111 | PFLineP1_PF | PF limit line point 1 power factor | W | 0-20000
3 | 112 | PFLineP2_LP | PF limit line point 2 load percent | W | 0-255 | % |  | 255 means no this point
3 | 113 | PFLineP2_PF | PF limit line point | W | 0-20000
3 | 114 | PFLineP3_LP | PF limit line point 3 load percent | W | 0-255 | % |  | 255 means no this point
3 | 115 | PFLineP3_PF | PF limit line point 3 power factor | W | 0-20000
3 | 116 | PFLineP4_LP | PF limit line point 4 load percent | W | 0-255 | % |  | 255 means no this point
3 | 117 | PFLineP4_PF | PF limit line point 4 power factor | W | 0-20000
3 | 118 | Module4 | Inverter Module (4) |  | &*11 |  |  | SxxBxx
3 | 119 | Module3 | Inverter Module (3) |  | &*11 |  |  | DxxTxx
3 | 120 | Module2 | Inverter Module (2) |  | &*11 |  |  | PxxUxx
3 | 121 | Module1 | Inverter Module (1) |  | &*11 |  |  | Mxxxx Power
3 | 122 | ExportLimit_ | ExportLimit_En/dis | R/W | 1/0 |  |  | ExportLimit enable,
3 | 123 | ExportLimitPowerRate | ExportLimitPowerRate | R/W | -1000~+1 | 0.001 |  | ExportLimit PowerRate
3 | 124 | TrakerModel | Traker Model | W | 0,1,2 |  |  | 0:Independent
3 | 125 | INVType-1 | Inverter type-1 | R |  |  |  | ASCII
3 | 126 | INVType-2 | Inverter type-2 | R |  |  |  | ASCII
3 | 127 | INVType-3 | Inverter type-3 | R |  |  |  | ASCII
3 | 128 | INVType-4 | Inverter type-4 | R |  |  |  | ASCII
3 | 129 | INVType-5 | Inverter type-5 | R |  |  |  | ASCII
3 | 130 | INVType-6 | Inverter type-6 | R |  |  |  | ASCII
3 | 131 | INVType-7 | Inverter type-7 | R |  |  |  | ASCII
3 | 132 | INVType-8 | Inverter type-8 | R |  |  |  | ASCII
3 | 133 | BLVersion1 | Boot loader version1 | R
3 | 134 | BLVersion2 | Boot loader version2 | R
3 | 135 | BLVersion3 | Boot loader version3 | R
3 | 136 | BLVersion4 | Boot loader version4 | R
3 | 137 | ReactivePowerH | Reactive PowerH | R/W |  | 0.1var
3 | 138 | ReactiveP | Reactive PowerL | R/W |  | 0.1var
3 | 139 | ReactiveOutputPriorityenable | ReactiveOutput Priority | R/W |  | 0/1 |  | 0：disable
3 | 140 | ReactiveP | Reactive Power Ratio | R/W |  | 0.1
3 | 141 | SvgFunction | Svg enable on night | R/W |  | 0/1 |  | 0：disable
3 | 142 | uwUnderFUploadPoint | UnderF Upload Point | R/W |  | 0.01H
3 | 143 | uwOFDerateRecoverPoin | OFDerate RecoverPoint | R/W |  | 0.01H
3 | 144 | uwOFDerateRecoverDelayTime | OFDerate | R/W | 0-30000 | 50ms
3 | 145 | ZeroCurrent | ZeroCurrent Enable | R/W | 0-1
3 | 146 | uwZeroCurrentStaticlowV | ZeroCurrent | R/W | 46-230V | 0.1V | 115V
3 | 147 | uwZeroCurrentStaticHigh | ZeroCurrent | R/W | 230-276V | 0.1V | 276V
3 | 148 | uwHVoltDer | HVoltDerate HighPoint | R/W | 0-1000V | 0.1V
3 | 149 | uwHVoltDerateLowPoint | HVoltDerate LowPoint | R/W | 0-1000V | 0.1V
3 | 150 | uwQVPower | QVPower Stable Time | R/W | 0-60S | 0.1S
3 | 151 | uwUnderFUploadStopPo | UnderF Upload | R/W |  | 0.01H
3 | 152 | fUnderFreqPoint | Underfrequency load | R/W | 46.00-50. | 0.01Hz | 49.8 | CEI
3 | 153 | fUnderFreqendPoint | Underfrequency down load end point | R/W | 46.00-50. | 0.01Hz | 49.1 | CEI
3 | 154 | fOverFreqPo | Over frequency loading start point | R/W | 50.00-52. | 0.01Hz | 50.2 | CEI
3 | 155 | fOverFreqEndPoint | Over frequency loading end point | R/W | 50.00-52. | 0.01Hz | 51.5 | CEI
3 | 156 | fUnderVoltPoint | Undervoltage load | R/W | 160-300 | 0.1V | 220 | CEI
3 | 157 | fUnderVoltendPoint | Undervoltage derating end point | R/W | 160-300 | 0.1V | 207 | CEI
3 | 158 | fOverVoltPoint | Overvoltage loading | R/W | 160-300 | 0.1V | 230 | CEI
3 | 159 | fOverVoltEndPoint | Overvoltage loading end point | R/W | 160-300 | 0.1V | 245 | CEI
3 | 160 | uwNominal | NominalGridVolt Select | R/W | 0~3 |  |  | UL
3 | 161 | uwGridWatt | GridWatt DelayTime | R/W | 0~3000 | 20ms |  | UL
3 | 162 | uwReconnec | Reconnect StartSlope | R/W | 1~1000 | 0.1 |  | UL
3 | 163 | uwLFRTEE | LFRT1 Freq | R/W | 5500~650 | 0.01Hz |  | UL
3 | 164 | uwLFRTTime | LFRT1 Time | R/W |  | 20ms |  | UL
3 | 165 | uwLFRT2EE | LFRT2 Freq | R/W | 5500~650 | 0.01Hz |  | UL
3 | 166 | uwLFRTTime | LFRT2 Time | R/W |  | 20ms |  | UL
3 | 167 | uwHFRTEE | HFRT1 Freq | R/W | 5500~650 | 0.01Hz |  | UL
3 | 168 | uwHFRTTimeEE | HFRT1 Time | R/W |  | 20ms |  | UL
3 | 169 | uwHFRT2EE | HFRT2 Freq | R/W | 5500~650 | 0.01Hz |  | UL
3 | 170 | uwHFRTTime2EE | HFRT2 Time | R/W |  | 20ms |  | UL
3 | 171 | uwHVRTEE | HVRT1 Volt | R/W |  | 0.001 |  | UL
3 | 172 | uwHVRTTimeEE | HVRT1 Time | R/W |  | 20ms |  | UL
3 | 173 | uwHVRT2EE | HVRT2 Volt | R/W |  | 0.001 |  | UL
3 | 174 | uwHVRTTime2EE | HVRT2 Time | R/W |  | 0.001 |  | UL
3 | 175 | uwUnderFU | UnderF | R/W | 0-2s | 50ms | 0s | 50549
3 | 176 | uwUnderFUploadRateEE | UnderF UploadRate | R/W |  |  |  | 50549
3 | 177 | uwGridRestart_H_Freq | GridRestart HighFreq | R/W |  | 0.01Hz |  | 50549
3 | 178 | OverFDeratResponseTime | OverFDerat | R/W | 0-500
3 | 179 | UnderFUploadResponse | UnderFUpload | R/W | 0-500
3 | 180 | MeterLink | Whether to elect the meter | R/W |  |  |  | 0: Missed, 1: Received
3 | 181 | OPTNumber | Number of connection optimizers | R/W | 0-64 |  |  | The total number of optimizers connected to the inverter
3 | 182 | OPT | Optimizer configuration completion flag | R/W |  |  |  | 0x00:Not configured success
3 | 183 | PvStrScan | String Num | R/W | 0、8、16、 |  |  | 0：Not support
3 | 184 | BDCLinkNum | BDC parallel Num | R/W |  |  |  | The number of BDCs connected to the current machine Default is 0
3 | 185 | PackNum | Number of battery modules | R |  |  |  | Total number of battery modules currently associated with all BDCs
3 | 186 | Reserved
3 | 187 | VPPfunctionenablestatus | VPP function enable status | R |  |  |  | 0：Disable
3 | 188 | dataLogConnectServerstatus | dataLog Connect |  |  |  |  | 0：connection succeeded
3 | 201 | PIDWorkingModel | PID Operating mode | W | 0
3 | 202 | PIDOn_OffCtrl | PID Break control | W | 0:On 1:Off
3 | 203 | PIDOption | PID Output voltage | W | 300~1000 | V
3 | 209 | NewSerialNO | Serial number 1-2 |  |  |  |  | ASCII
3 | 210 | NewSerialNO | Serial number 3-4 |  |  |  |  | ASCII
3 | 211 | NewSerialNO | Serial number 5-6 |  |  |  |  | ASCII
3 | 212 | NewSerialNO | Serial number 7-8 |  |  |  |  | ASCII
3 | 213 | NewSerialNO | Serial number 9-10 |  |  |  |  | ASCII
3 | 214 | NewSerialNO | Serial number 11-12 |  |  |  |  | ASCII
3 | 215 | NewSerialNO | Serial number 13-14 |  |  |  |  | ASCII
3 | 216 | NewSerialNO | Serial number 15-16 |  |  |  |  | ASCII
3 | 217 | NewSerialNO | Serial number 17-18 |  |  |  |  | ASCII
3 | 218 | NewSerialNO | Serial number 19-20 |  |  |  |  | ASCII
3 | 219 | Time9 | [5 empty] | SpecialDay1_Time
3 | 219 | NewSerialNO | Serial number 21-22 |  |  |  |  | ASCII
3 | 220 | NewSerialNO | Serial number 23-24 |  |  |  |  | ASCII
3 | 221 | NewSerialNO | Serial number 25-26 |  |  |  |  | ASCII
3 | 222 | NewSerialNO | Serial number 27-28 |  |  |  |  | ASCII
3 | 223 | NewSerialNO | Serial number 29-30 |  |  |  |  | ASCII
3 | 229 | EnergyAdjust | Power generation incremental calibration coefficient | R/W |  | 0.001 |  | 1-1000,(Percent ratio)
3 | 230 | IslandDisable | Island Disable or not. | W | 0,1 |  | 0
3 | 231 | FanCheck | Start Fan Check | W | 1
3 | 232 | EnableNLine | Enable N Line of grid | W | 1 |  | 0
3 | 233 | wCheckHardware | wCheckHardware
3 | 234 | wCheckHardware2 | [5 empty] | reserved
3 | 235 | ubNToGNDDetect | Dis/enable N to GND | W | 1:enable |  | 1
3 | 236 | NonStdVacenable | Enable/Disable | W | 0-2 |  | 0 | 0:Disable;
3 | 237 | uwEnableSpecSet | Disablse/enable appointed spec setting | W | 1:enable | Binary | 0x000 | Bit 0: Hungary
3 | 238 | FastMPPTenable | About Fast mppt |  | 0,1,2 |  | 0 | Reserved
3 | 240 | CheckStep |  | W
3 | 241 | INV-Lng | Inverter Longitude | W |  |  |  | Longitude
3 | 242 | INV-Lat | Inverter Latitude | W |  |  |  | Latitude
3 | 304 | uwAntiBackflowFailPowerLimitEE | Anti-backflow failure power percentage | R/W | 0-1000 | 0.001 |  | Anti-backflow failure default setting power percentage
3 | 305 | Qloadspeed | Reactive loading speed | R/W | 0-100 | 0.01 |  | Reactive power adjustment speed setting item, n%Pn/s, 0 means that the loading speed is not enabled, that is, it is directly loaded to the set value
3 | 306 | bParallelAntiBackflowEnable | ParallelAnti-Backflow | R/W | 0-1 |  |  | Parallel anti-Backflow open enable bit
3 | 307 | uwAntiBackflowFailureResponseTime | AntiBackflowFailure | R/W | 1132254 | 1s |  | AntiBackflow Failure
3 | 308 | uwParallelAntiBackflowPowerLimitEE | ParallelAntiBackflowPo wer | R/W | 0-1000 | 0.001 |  | Parallel AntiBackflow Power
3 | 309 | bISOCheckCmd | ISO detection | R/W | 0-1 | 1 |  | ISO detection command
3 | 310 | bGPRSStatus | GPRS Status | R/W | 0-255 | 1
3 | 311 | uwQmax_Inductive | The inductive Qmax of the Q(V) curve | R/W | 0-1000 | 0.001
3 | 312 | uwQmax_Capactive | The Capactive Qmax of | R/W | 0-1000 | 0.001
3 | 313 | uwReactivePowerAdjustFailureResponseTime | ReactivePowerAdjust | R/W | 0-5000 | S
3 | 314 | bSuperAntiBackflowEnable | SuperAntiBackflow | R/W |  |  |  | 0：disable，1：enable
3 | 315 | uwReactivePowerStableTime | ReactivePowerStableTi | R/W | 0-200 | S
3 | 316 | uwQpStableTime | QpStableTime | R/W | 0-200 | S
3 | 317 | uwPuDerateTime | PuDerateTime | R/W | 0-200 | S
3 | 318 | uwQVModelQ2Point | QV mode Q2 set point reactive power | R/W | 0-2000 | 0.001 |  | Capacitive 30%
3 | 319 | uwQVModelQ3Point | QV mode Q3 set point reactive power | R/W | 0-2000 | 0.001 |  | 1300)； used for IEE1547
3 | 320 | bVrefModelEnable | VrefModelEnable | R/W | 0 ： Vref mode for QV curve is not active |  |  | When the Vref mode is not activated, the V1~V4 and Q1~Q4 upper computer of the QV curve can be adjusted;
3 | 321 | uwVrefModelFilterTime | VrefModelFilterTime | R/W | 0-5000 | S |  | Activate Vref mode, the output filter value is equal to
3 | 322 | uwUserQPModeP1Krate | Active power P1 set point percentage for | R/W | 0-1000 | 0.001 |  | used for IEE1547
3 | 323 | uwUserQPModeP2Krate | Active power P2 point percentage | R/W | 0-1000 | 0.001 |  | used for IEE1547
3 | 324 | uwUserQPModeP3Krate | Active power P3 point percentage | R/W | 0-1000 | 0.001 |  | used for IEE1547
3 | 325 | uwUserQPModeQ1Krate | Reactive power Q1 set point percentage for | R/W | -1010 | 0.001 |  | -1000~1000：Inductive（100%
3 | 326 | uwUserQPModeQ2Krate | Reactive power Q2 set point percentage for | R/W | -1010 | 0.001 |  | -1000~1000：Inductive（100%
3 | 327 | uwUserQPModeQ3Krate | Reactive power Q3 set point percentage for | R/W | -1010 | 0.001 |  | -1000~1000：Inductive（100%
3 | 328 | uwAcVoltHighDeratPowerLimit | AcVoltHighDeratPower | R/W | 0-1000 | 0.001
3 | 329 | BackflowSingleCtrl | BackflowSingleCtrl | R/W | 0: disable
3 | 330 | bAntiBackflowProtectMode | AntiBackflowProtectM ode | R/W | 0-3 |  |  | Used for Australian
3 | 331 | uwUnderFUploadZeroPowerPoint | UnderfreqUploadZeroP owerPoint | W |  | 0.01H
3 | 332 | FreqDerateZeroPowerPoint | FreqDerateZeroPowerP oint | W |  | 0.01H
3 | 333 | bFreqDeratingStopModeEnable | FreqDeratingStopMode | R/W | 0-1
3 | 334 | bFreqIncreasingEnable | FreqIncreasingEnable | R/W | 0-1
3 | 335 | uwFreqIncreasingRecoverTime | FreqIncreasingRecover | R/W |  | 50ms
3 | 336 | uwFreqIncreasingEndLowPoint | FreqIncreasingEndLow | R/W |  | 0.01H
3 | 337 | bFreqIncreasingStopModeEnable | FreqIncreasingStopMo deEnable | R/W | 0-1
3 | 338 | uwUserQpChrP1Krate | User QP charge P1 percentage | R/W | 0-1000 | 0.001
3 | 339 | uwUserQpChrP2Krate | User QP charge P2 percentage | R/W | 0-1000 | 0.001
3 | 340 | uwUserQpChrP3Krate | User QP charge P3 percentage | R/W | 0-1000 | 0.001
3 | 341 | wUserQpChrQ1Krate | User QP | R/W | -1010 | 0.001 |  | -1000~1000：Inductive（100%
3 | 342 | wUserQpChrQ2Krate | User QP | R/W | -1010 | 0.001 |  | -1000~1000：Inductive（100%
3 | 343 | wUserQpChrQ3Krate | User QP | R/W | -1010 | 0.001 |  | -1000~1000：Inductive（100%
3 | 344 | uwFreqDeratingRecoverLowPoint | FreqDeratingRecoverLo wPoint | R/W |  | 0.01H
3 | 345 | uwFreqIncreasingRecoverHighPoint | FreqIncreasingRecover | R/W |  | 0.01H
3 | 532 | TurnOffUnloadSpeed | TurnOffUnloadSpeed | R/W | 0-1000 |  | 0.001 | 0 means not enabled, that is, the function is not enabled; 1-1000 means n%Pn/min
3 | 533 | LimitDevice | Anti-backflow equipment selection | R/W | 0-3 |  |  | 1：Meter
3 | 534 | PowerSetOndCSourceMode | Power settings in dc source mode | R/W | 0-90000 |  |  | The unit is W
3 | 535 | OUFreqGrade1En | Over-under-frequency | R/W | 0-1 |  |  | 0:disable
3 | 536 | CountrySet | Country settings under the same safety regulations | R/W | 0-200 |  |  | For mobile APP use only
3 | 538 | InterlockEnable | Three-machine communication | R/W | 0-2 |  |  | 0：disable
3 | 539 | OvTemperDeratePoint | Over temperature derate point | R/W
3 | 540 | SafetySetPassword | Switch between different safety regulations to set the | R/W
3 | 541 | AFCIOnoff | AFCI Onoff | R/W | 0xA0/0xA |  |  | 0xA0：AFCI off
3 | 542 | AfciSelfCheck | AfciSelfCheck | R/W |  |  |  | 0：No self check
3 | 543 | AfciReset | AfciReset | R/W |  |  |  | 0：Not Reset
3 | 544 | AFCIValue1 | AFCIThresholdValue | R/W | 0-65000
3 | 545 | AFCIValue2 | AFCIThresholdValue | R/W | 0-65000
3 | 546 | AFCIValue3 | AFCIThresholdValue | R/W | 0-65000
3 | 547 | OverThresholdValueMaxCnt | OverThresholdValueMa xCnt | R/W | 0-255
3 | 548 | AFCIScanTypeEnable | AFCI curve scan type | R/W | 1~4 |  |  | 1：A road strength
3 | 549 | PowerVoltStopModeEn | PowerVoltStopModeEn | R/W | 0、1 |  |  | 0：disable
3 | 550 | VoltWattRecoverTime | Voltage active power recovery time | R/W | 0-15000 | 20ms
3 | 551 | HVoltDerate | Voltage active cut-off | R/W | -5011
3 | 552 | QVTimeExponent | QVTimeExponent | R/W | 1-255 |  |  | Q varies exponentially with time
3 | 553 | Volt-Watt1 | Voltage active V1 point, corresponding active power | R/W | 0-11400
3 | 554 | Volt-Watt2 | Voltage active V2 point, corresponding active power | R/W | 0-11400
3 | 600 | Volt-Var1 | Voltage reactive V1 | R/W | 0-1000 |  |  | 0%~100.0%,US regulations
3 | 601 | Volt-Var2 | Voltage reactive point,V2 | R/W | 0-1000 |  |  | 0%~100.0%,US regulations
3 | 602 | Volt-Var3 | Voltage reactive point,V3 | R/W | 0-1000 |  |  | 0%~100.0%,US regulations
3 | 603 | Volt-Var4 | Voltage reactive point,V4 | R/W | 0-1000 |  |  | 0%~100.0%,US latest safety regulations
3 | 605 | OPModEner | Allowed inverter output power | R/W | 0/1 |  |  | 0: output power not allowed
3 | 608 | OneKeySetB | One key to set battery mode function | R/W |  |  |  | 0: self-use
3 | 609 | PowerOutputEnable | Zero Power Output |  |  |  |  | 0：Zero Power Output
3 | 610 | DealDebugParaFlag | Flag bit for clearing debug variables |  |  |  |  | Currently only bit0 and bit1 are used bit0 is used to manually clear the Debug data uploaded to the server bit1 is used to manually clear the fault codes that need to be powered off to clear
3 | 612 | bAcCoupleen | AcCoupleEn | R/W | 0-1 |  |  | 0：disable
3 | 660 | ReloadCmd | M3 remote command |  |  |  |  | 0xA0: Initialize safety defaults
3 | 1000 | Floatchargecurrentlimit | When charge current battery need is lower than this value, enter into float charge | W |  | 0.1A | 600 | CC current
3 | 1001 | PFCMD | Set the following 19-22 | W | 0or1, |  | 0 | Means these settings will be acting or not when next
3 | 1002 | VbatStartForDischarge | LV Vbat | R/W |  | 0.1V |  | Lead-acid battery LV voltage
3 | 1003 | VbatlowWa | LoadPercent(only lead-Acid): | W |  | 0.1V |  | Clear battery low voltage error voltage point
3 | 1004 | Vbatstopfordischarge | Should stop discharge when lower than this | W |  | 0.01V
3 | 1005 | Vbatstop | Should stop charge when higher than this voltage | W |  | 0.01V | 5800
3 | 1006 | Vbatstart | Should not discharge when lower than this | W |  | 0.01V | 4800
3 | 1007 | Vbatconstantcharge | can charge when lower than this voltage | W |  | 0.01V | 5800 | CV voltage（acid）
3 | 1008 | EESysInfoSysSetEn | Bit0：Resved; | W |  |  |  | System Enable
3 | 1009 | Battemplowerlimitd | Battery temperature lower limit for discharge | W | 0-200:0-2 | 0.1℃ | 1170
3 | 1010 | Battempupperlimitd | Battery temperature upper limit for discharge | W | 200-1000 | 0.1℃ | 420
3 | 1011 | Battemplowerlimitc | Battery temperature lower limit for charge | W | 0-200:0-2 | 0.1℃ | 30 | Lower temperature limit
3 | 1012 | Battempupperlimitc | Battery temperature upper limit for charge | W | 200-1000 | 0.1℃ | 370 | Upper temperature limit
3 | 1013 | uwUnderFreDischargeDelyTime | Under Fre Delay Time |  | 0-20 | 50ms |  | Under Fre Delay Time
3 | 1014 | BatMdlSerialNum | Battery serial number | W | 0 |  |  | SPH4-11K used
3 | 1015 | BatMdlParallNum | Battery parallel section | W | 0 |  |  | SPH4-11K used
3 | 1016 | DRMS_EN | [5 empty] | 0：disable 1：enable
3 | 1017 | BatFirstStartTime4 | High eight:hours | W | 0-23 | h
3 | 1018 | BatFirstStopTime4 | High eight:hours | W | 0-23 | h
3 | 1019 | BatFirston_offSwitch4 | Enable:1 | W | 0 or 1 |  |  | Battery priority enable 1
3 | 1020 | BatFirstStartTime5 | High eight:hours | W | 0-23 | h
3 | 1021 | BatFirstStopTime5 | High eight:hours | W | 0-23 | h
3 | 1022 | BatFirston_offSwitch5 | Enable:1 | W | 0 or 1 |  |  | Battery priority enable 1
3 | 1023 | BatFirstStartTime6 | High eight:hours | W | 0-23 | h
3 | 1024 | BatFirstStopTime6 | High eight:hours | W | 0-23 | h
3 | 1025 | BatFirston_offSwitch6 | Enable:1 | W | 0 or 1 |  |  | Battery priority enable 1
3 | 1026 | GridFirstStartTime4 | High eight:hours | W | 0-23 | h
3 | 1027 | GridFirstStopTime4 | High eight:hours | W | 0-23 | h
3 | 1028 | GridFirstStopSwitch4 | Enable:1 | W | 0 or 1 |  |  | Grid priority enable
3 | 1029 | GridFirstStartTime5 | High eight:hours | W | 0-23 | h
3 | 1030 | GridFirstStopTime5 | High eight:hours | W | 0-23 | h
3 | 1031 | GridFirstStopSwitch5 | Enable:1 | W | 0 or 1 |  |  | Grid priority enable
3 | 1032 | GridFirstStartTime6 | High eight:hours | W | 0-23 | h
3 | 1033 | GridFirstStopTime6 | High eight:hours | W | 0-23 | h
3 | 1034 | GridFirstStopSwitch6 | Enable:1 | W | 0 or 1 |  |  | Grid priority enable
3 | 1035 | BatFirstStartTime | High eight:hours | W | 0-23 | h
3 | 1037 | bCTMode | Use the CTMode to | W | 2:METER 1:cWirele ssCT |  | 0
3 | 1038 | CTAdjust | CTAdjust enable | W | 0:disable |  | 0
3 | 1044 | Priority | ForceChrEn/ForceDischr | R |  |  |  | 0.Load(de fault)/1.B attery/2.G rid
3 | 1047 | AgingTestStepCmd | Command for aging test |  |  |  | 0: default
3 | 1048 | BatteryType | Battery type choose of buck-boost input |  |  |  | 0:Lithium 1:Lead-aci d
3 | 1060 | BuckUpsFunen | Ups function enable |  | 0:disable
3 | 1061 | BuckUPSVoltSet | UPS output voltage |  | 0.15972 |  | 230V
3 | 1062 | UPSFreqSet | UPS output frequency |  | 0:50Hz |  | 50Hz
3 | 1070 | GridFirstDischargePowerRate | Discharge Power Rate | W | 0-100 | 0.01 |  | Discharge
3 | 1071 | GridFirstStopSOC | Stop Discharge soc when | W | 0-100 | 0.01 |  | Stop Discharge soc when
3 | 1080 | GridFirstStartTime1 | High eight bit：hour |  | 0-23 | h
3 | 1081 | GridFirstStopTime1 | High eight bit：hour |  | 0-23 | h
3 | 1082 | GridFirstStopSwitch1 | Enable :1 |  | 0 or 1 |  |  | Grid First enable
3 | 1083 | GridFirstStartTime2 | High eight bit：hour |  | 0-23 | h
3 | 1084 | GridFirstStopTime2 | High eight bit：hour |  | 0-23 | h
3 | 1085 | GridFirstStopSwitch2 | ForceDischarge.bSwitch&L |  | 0 or 1 |  |  | Grid First enable
3 | 1086 | GridFirstStartTime3 | High eight bit：hour |  | 0-23 | h
3 | 1087 | GridFirstStopTime3 | High eight bit：hour |  | 0-23 | h
3 | 1088 | GridFirstStopSwitch3 | Enable :1 |  | 0 or 1 |  |  | Grid First enable
3 | 1090 | BatFirstPowerRate | Charge Power Rate when | W |  | 0.01 |  | Charge
3 | 1091 | wBatFirststopSOC | Stop Charge soc when Bat | W | 0-100 | 0.01 |  | Stop
3 | 1092 | ACchargeSwitch | When Bat First |  | Enable:1 |  |  | AC Charge
3 | 1100 | BatFirstStartTime1 | High eight bit：hour |  | 0-23 | h
3 | 1101 | BatFirstStopTime1 | High eight bit：hour |  | 0-23 | h
3 | 1102 | BatFirston_offSwitch1 | Enable :1 |  | 0 or 1 |  |  | Bat First
3 | 1103 | BatFirstStartTime2 | High eight bit：hour |  | 0-23 | h
3 | 1104 | BatFirstStopTime2 | High eight bit：hour |  | 0-23 | h
3 | 1105 | BatFirston_offSwitch2 | Enable :1 |  | 0 or 1 |  |  | Bat First
3 | 1106 | BatFirstStartTime3 | High eight bit：hour |  | 0-23 | h
3 | 1107 | BatFirstStopTime3 | High eight bit：hour |  | 0-23 | h
3 | 1108 | BatFirston_offSwitch3 | Enable :1 |  | 0 or 1 |  |  | Bat First
3 | 1110 | LoadFirstStartTime1 | High eight bit：hour |  | 0-23 | h |  | SPA/ reserve
3 | 1111 | LoadFirstStopTime1 | High eight bit：hour |  | 0-23 | h |  | SPA/ reserve
3 | 1112 | LoadFirstSwitch1 | Enable :1 |  | 0 or 1 |  |  | SPA/ reserve
3 | 1113 | LoadFirstStartTime2 | High eight bit：hour |  | 0-23 | h |  | SPA/ reserve
3 | 1114 | LoadFirstStopTime2 | High eight bit：hour |  | 0-23 | h |  | SPA/ reserve
3 | 1115 | LoadFirstSwitch2 | Enable :1 |  | 0 or 1 |  |  | SPA/ reserve
3 | 1116 | LoadFirstStartTime3 | High eight bit：hour |  | 0-23 | h |  | SPA/ reserve
3 | 1117 | LoadFirstStopTime3 | High eight bit：hour |  | 0-23 | h |  | SPA/ reserve
3 | 1118 | LoadFirstSwitch3 | Enable :1 |  | 0 or 1 |  |  | SPA/ reserve
3 | 1119 | NewEPowerCalcFlag | [5 empty] | 0：The old formula
3 | 1120 | BackUpEn | BackUp Enable |  |  |  |  | MIX US
3 | 1121 | SGIPEn | SGIP Enable |  |  |  |  | MIX US
3 | 1125 | BatSerialNO | Product serial number of the first PACK of energy |  |  |  |  | ASCII
3 | 1126 | BatSerialNO7 | [5 empty] | ASCII
3 | 1127 | BatSerialNO6 | [5 empty] | ASCII
3 | 1128 | BatSerialNO5 | [5 empty] | ASCII
3 | 1129 | BatSerialNO4 | [5 empty] | ASCII
3 | 1130 | BatSerialNO3 | [5 empty] | ASCII
3 | 1131 | BatSerialNO2 | [5 empty] | ASCII
3 | 1132 | BatSerialNO | The serial number of the second to tenth packs of the energy storage battery consists of nine packs, and |  |  |  |  | ASCII
3 | 1132 | BatSerialNO1 | [5 empty] | ASCII
3 | 1244 | ComversionNameH | Name of the battery main control firmware version |  |  |  |  | ASCII
3 | 1245 | ComversionNameL | Name of the battery main control firmware version |  |  |  |  | ASCII
3 | 1246 | ComversionNo | Version of the battery main control firmware |  |  |  |  | digital
3 | 1247 | ComversionNameH | Name of battery monitoring firmware |  |  |  |  | ASCII
3 | 1248 | ComversionNameL | Name of battery monitoring firmware |  |  |  |  | ASCII
3 | 1249 | ComversionNo | Battery monitoring |  |  |  |  | digital
3 | 3000 | ExportLimitFailedPowerRate | The power rate when | R/W |  | 0.001 |  | The power rate when exportLimit
3 | 3001 | NewSerialNO | Serial number 1-2 | R/W |  |  |  | ASCII
3 | 3002 | NewSerialNO | Serial number 3-4 | R/W |  |  |  | ASCII
3 | 3003 | NewSerialNO | Serial number 5-6 | R/W |  |  |  | ASCII
3 | 3004 | NewSerialNO | Serial number 7-8 | R/W |  |  |  | ASCII
3 | 3005 | NewSerialNO | Serial number 9-10 | R/W |  |  |  | ASCII
3 | 3006 | NewSerialNO | Serial number 11-12 | R/W |  |  |  | ASCII
3 | 3007 | NewSerialNO | Serial number 13-14 | R/W |  |  |  | ASCII
3 | 3008 | NewSerialNO | Serial number 15-16 | R/W |  |  |  | ASCII
3 | 3009 | NewSerialNO | Serial number 17-18 | R/W |  |  |  | ASCII
3 | 3010 | NewSerialNO | Serial number 19-20 | R/W |  |  |  | ASCII
3 | 3011 | NewSerialNO | Serial number 21-22 | R/W |  |  |  | ASCII
3 | 3012 | NewSerialNO | Serial number 23-24 | R/W |  |  |  | ASCII
3 | 3013 | NewSerialNO | Serial number 25-26 | R/W |  |  |  | ASCII
3 | 3014 | NewSerialNO | Serial number 27-28 | R/W |  |  |  | ASCII
3 | 3015 | NewSerialNO | Serial number 29-30 | R/W |  |  |  | ASCII
3 | 3016 | DryContactFuncEn | DryContact function enable | R/W | 0:Disable |  |  | DryContact function enable
3 | 3017 | DryContactOn | The power rate of | R/W | 0~1000 | 0.001 |  | The power rate of drycontact turn on
3 | 3018 | bWorkMode | WorkMode----0:default,1: | R/W | 0、1、2 |  |  | MIN2.5~6KTL-XH/ XA Double CT
3 | 3019 | DryContactOffRate | Dry contact closure power | R/W | 0~100 | 0.001 |  | Dry contact closure power pe rcentage
3 | 3020 | BoxCtrlInvOrder | BoxCtrlInvOrderOff-net box control instruct ion | R/W
3 | 3021 | ExterCommOffGridEn | External communication setting manual off-network enable | R/W |  |  |  | 0x00: Disable;
3 | 3022 | uwBdcStopWorkOfBusVolt | BdcStopWorkOfBusVolt | R
3 | 3023 | bGridType | GridType---0:SinglePhase | R/W | 0、1、2 |  |  | MIN2.5~6KTL-XH/ XA Double CT
3 | 3024 | Floatchargecurrentlimit | When charge current battery need is lower than | R/W |  | 0.1A | 600 | CC current
3 | 3025 | VbatWarning | "Battery-low" warning setup voltage | R/W |  | 0.1V | 4800 | Lead acid battery
3 | 3026 | VbatlowWarn | "Battery-low" warning clear voltage | R/W |  | 0.1V |  | Clear battery low voltage error voltage point
3 | 3027 | Vbatstopfordischarge | Battery cut off voltage | R/W |  | 0.1V |  | Should stop discharge when lower than this voltage(only lead-Acid):
3 | 3028 | Vbatstopforcharge | Battery over charge voltage | R/W |  | 0.01V | 5800 | Should stop charge when higher than this voltage
3 | 3029 | Vbatstartfordischarge | Battery start discharge voltage | R/W |  | 0.01V | 4800 | Should not discharge when lower than this voltage
3 | 3030 | Vbatconstantcharge | Battery constant charge voltage | R/W |  | 0.01V | 5800 | CV voltage（acid） can charge when lower than this voltage
3 | 3031 | Battemplowerlimitd | Battery temperature lower limit for discharge | R/W |  | 0.1℃ | 1170 | 0-200:0-20℃
3 | 3032 | Battempupperlimitd | Battery temperature upper limit for discharge | R/W |  | 0.1℃ | 420
3 | 3033 | Battemplowerlimitc | Battery temperature lower limit for charge | R/W |  | 0.1℃ | 30 | Battery temperature lower
3 | 3034 | Battempupperlimitc | Battery temperature upper limit for charge | R/W |  | 0.1℃ | 370 | Battery temperature upper limit
3 | 3035 | uwUnderFreDischargeDelyTime | Under Fre Delay Time | R/W |  | 50ms |  | Under Fre Delay
3 | 3036 | GridFirstDischargePowerRate | Discharge Power Rate when Grid First |  |  |  | 1-255
3 | 3037 | GridFirstStopS | Stop Discharge soc when |  |  |  | 1-100
3 | 3038 | Time1 | Period 1: [Start Time ~ End | R/W |  |  |  | Bit0~7: minutes;
3 | 3040 | Time2 | Time period 2: [start time ~ end time], [charge / | R/W |  |  |  | Bit0~7: minutes;
3 | 3042 | Time3 | With Time1 | R/W |  |  |  | With Time1
3 | 3044 | Time4 | With Time1 | R/W |  |  |  | With Time1
3 | 3047 | BatFirstPower | Charge Power Rate when |  |  |  | 1-100
3 | 3048 | wBatFirststop | Stop Charge soc when Bat |  |  |  | 1-100
3 | 3049 | AcChargeEnable | AcChargeEnable |  |  |  |  | Enable :1
3 | 3050 | Time5 | With Time1 | R/W |  |  |  | With Time1
3 | 3052 | Time6 | With Time1 | R/W |  |  |  | With Time1
3 | 3054 | Time7 | With Time1 | R/W |  |  |  | With Time1
3 | 3056 | Time8 | With Time1 | R/W |  |  |  | With Time1
3 | 3058 | Time9 | With Time1 | R/W |  |  |  | With Time1
3 | 3070 | BatteryType | Battery type choose of buck-boost input | R/W |  |  |  | Battery type
3 | 3071 | BatMdlSeria_ | BatMdlSeria/ParalNum | R/W |  |  |  | BatMdlSeria/Paral
3 | 3072 | Reserved
3 | 3073 | Reserved
3 | 3074 | Reserved
3 | 3075 | Reserved
3 | 3076 | Reserved
3 | 3077 | Reserved
3 | 3078 | Reserved
3 | 3079 | UpsFunEn | Ups function enable or disable | R/W |  |  | 0 | 0:disable
3 | 3080 | UPSVoltSet | UPS output voltage | R/W |  |  | 0 | 0:230V
3 | 3081 | UPSFreqSet | UPS output frequency | R/W |  |  | 0 | 0:50Hz
3 | 3082 | bLoadFirstStopSocSet | StopSoc When LoadFirst | R/W | 13-100 |  |  | ratio
3 | 3083 | Reserved
3 | 3084 | Reserved
3 | 3085 | ComAddress | Communication addr | R/W |  |  | 1 | 1 : Communication addr=1
3 | 3086 | BaudRate | Communication BaudRate | R/W |  |  | 0 | 0: 9600 bps
3 | 3087 | SerialNO1 | Serial Number 1-2 | R/W |  |  |  | ASCII
3 | 3088 | SerialNO2 | Serial Number 3-4 | R/W |  |  |  | ASCII
3 | 3089 | SerialNO3 | Serial Number 5-6 | R/W |  |  |  | ASCII
3 | 3090 | SerialNO4 | Serial Number 7-8 | R/W |  |  |  | ASCII
3 | 3091 | SerialNo5 | Serial Number 9-10 | R/W |  |  |  | ASCII
3 | 3092 | SerialNo6 | Serial Number 11-12 | R/W |  |  |  | ASCII
3 | 3093 | SerialNo7 | Serial Number 13-14 | R/W |  |  |  | ASCII
3 | 3094 | SerialNo8 | Serial Number 15-16 | R/W |  |  |  | ASCII
3 | 3095 | BdcResetCmd | BDC Reset command | R/W |  |  |  | 0：Invalid data 1：Reset setting parameters 2：Reset correction parameter 3：Clear historical power
3 | 3096 | ARKM3Code | BDCMonitoring software code | R |  |  |  | ASCII
3 | 3098 | DTC | DTC | R
3 | 3099 | FWCode | DSP software code | R |  |  |  | ASCII
3 | 3101 | Processor1 | DSP Software Version | R |  |  |  | ASCII
3 | 3102 | BusVoltRef | Minimum BUS voltage for charging and discharging batteries | R
3 | 3103 | ARKM3Ver | BDC monitoring software version | R
3 | 3104 | BMS_MCUVersion | BMS hardware version | R |  | 1
3 | 3105 | BMS_FW | BMS software version information | R |  | 1
3 | 3106 | BMS_Info | BMS ManufacturerName | R |  | 1
3 | 3107 | BMSCommType | BMSCommType | R |  | 1 |  | BMSCommunicati on interface type：
3 | 3108 | Module4 | BDCmodel (4) | R/W | &*11 |  |  | SxxBxx
3 | 3109 | Module3 | BDCmodel (3) | R/W | &*11 |  |  | DxxTxx
3 | 3110 | Module2 | BDCmodel (2) | R/W | &*11 |  |  | PxxUxx
3 | 3111 | Module1 | BDCmodel (1) | R/W | &*11 |  |  | Mxxxx
3 | 3112 | Reserved
3 | 3113 | unProtocolVe | BDCProtocolVer | R | 1 |  |  | Bit8-bit15 The major version number ranges from 0-256. In principle, it cannot be changed
3 | 3114 | uwCertificationVer | BDC CertificationVer | R | 1
3 | 3125 | TimeMonth1 | Use with Time1-9（us） | R/W |  |  |  | bit0~3:month_L； bit4~7: month_H
3 | 3126 | TimeMonth2 | Use with Time10-18（us） | R/W |  |  |  | With Time Month1
3 | 3127 | TimeMonth3 | Use with Time19-27（us） | R/W |  |  |  | With Time Month1
3 | 3128 | TimeMonth4 | Use with Time28-36（us） | R/W |  |  |  | With Time Month1
3 | 3129 | Time1 | time1：[starttime~endtime] | R/W
3 | 3201 | SpecialDay1MD | SpecialDay1（month，Day） | R/W |  |  |  | bit0~7:day； bit8~14:month bit15， 0：disable 1： enable
3 | 3202 | SpecialDay1_Time1 | Start time | R/W |  |  |  | bit0~6:min； bit7~11:hour； bit12~14, 0:loadfirst;
3 | 3220 | SpecialDay2MD | SpecialDay2（month，Day） | R/W |  |  |  | bit0~7:day； bit8~14:month bit15， 0：disable
3 | 3221 | SpecialDay2_Time1 | Start time | R/W |  |  |  | bit0~6: min； bit7~11: hour； bit12~14,
3 | 3060~ | Reserved
3 | 3115 ~ | Reserved
3 | 3131-3132 | Time2 | Time 2（us） | R/W |  |  |  | Same as Time 1
3 | 3133-3134 | Time3 | Time 3（us） | R/W |  |  |  | Same as Time 1
3 | 3135-3136 | Time4 | Time 4（us） | R/W |  |  |  | Same as Time 1
3 | 3137-3138 | Time5 | Time 5（us） | R/W |  |  |  | Same as Time 1
3 | 3139-3140 | Time6 | Time 6（us） | R/W |  |  |  | Same as Time 1
3 | 3141-3142 | Time7 | Time 7（us） | R/W |  |  |  | Same as Time 1
3 | 3143-3144 | Time8 | Time 8（us） | R/W |  |  |  | Same as Time 1
3 | 3145-3146 | Time9 | Time9（us） | R/W |  |  |  | Same as Time 1
3 | 3147-3148 | Time10 | Time 10（us） | R/W |  |  |  | Same as Time 1
3 | 3149-3150 | Time11 | Time 11（us） | R/W |  |  |  | Same as Time 1
3 | 3151-3152 | Time12 | Time 12（us） | R/W |  |  |  | Same as Time 1
3 | 3153-3154 | Time13 | Time 13（us） | R/W |  |  |  | Same as Time 1
3 | 3155-3156 | Time14 | Time 14（us） | R/W |  |  |  | Same as Time 1
3 | 3157-3158 | Time15 | Time15（us） | R/W |  |  |  | Same as Time 1
3 | 3159-3160 | Time16 | Time 16（us） | R/W |  |  |  | Same as Time 1
3 | 3161-3162 | Time17 | Time 17（us） | R/W |  |  |  | Same as Time 1
3 | 3163-3164 | Time18 | Time 18（us） | R/W |  |  |  | Same as Time 1
3 | 3165-3166 | Time19 | Time 19（us） | R/W |  |  |  | Same as Time 1
3 | 3167-3168 | Time20 | Time 20（us） | R/W |  |  |  | Same as Time 1
3 | 3169-3170 | Time21 | Time 21（us） | R/W |  |  |  | Same as Time 1
3 | 3171-3172 | Time22 | Time 22（us） | R/W |  |  |  | Same as Time 1
3 | 3173-3174 | Time23 | Time 23（us） | R/W |  |  |  | Same as Time 1
3 | 3175-3176 | Time24 | Time 24（us） | R/W |  |  |  | Same as Time 1
3 | 3177-3178 | Time25 | Time 25（us） | R/W |  |  |  | Same as Time 1
3 | 3179-3180 | Time26 | Time 26（us） | R/W |  |  |  | Same as Time 1
3 | 3181-3182 | Time27 | Time 27（us） | R/W |  |  |  | Same as Time 1
3 | 3183-3184 | Time28 | Time 28（us） | R/W |  |  |  | Same as Time 1
3 | 3185-3186 | Time29 | Time 29（us） | R/W |  |  |  | Same as Time 1
3 | 3187-3188 | Time30 | Time 30（us） | R/W |  |  |  | Same as Time 1
3 | 3189-3190 | Time31 | Time 31（us） | R/W |  |  |  | Same as Time 1
3 | 3191-3192 | Time32 | Time 32（us） | R/W |  |  |  | Same as Time 1
3 | 3193-3194 | Time33 | Time 33（us） | R/W |  |  |  | Same as Time 1
3 | 3195-3196 | Time34 | Time 34（us） | R/W |  |  |  | Same as Time 1
3 | 3197-3198 | Time35 | Time 35（us） | R/W |  |  |  | Same as Time 1
3 | 3199-3200 | Time36 | Time 36（us） | R/W |  |  |  | Same as Time 1
3 | 3204-3205 | SpecialDay1_Time2 | SpecialDay1_Time2 | R/W |  |  |  | Same as
3 | 3206-3207 | SpecialDay1_Time3 | SpecialDay1_Time3 | R/W |  |  |  | Same as
3 | 3208-3209 | SpecialDay1_Time4 | SpecialDay1_Time4 | R/W |  |  |  | Same as
3 | 3210-3211 | SpecialDay1_Time5 | SpecialDay1_Time5 | R/W |  |  |  | Same as
3 | 3212-3213 | SpecialDay1_Time6 | SpecialDay1_Time6 | R/W |  |  |  | Same as
3 | 3214-3215 | SpecialDay1_Time7 | SpecialDay1_Time7 | R/W |  |  |  | Same as
3 | 3216-3217 | SpecialDay1_Time8 | SpecialDay1_Time8 | R/W |  |  |  | Same as
3 | 3218-3219 | SpecialDay1_Time9 | SpecialDay1_Time9 | R/W |  |  |  | Same as
3 | 3223-3224 | SpecialDay2_Time2 | SpecialDay2_Time2 | R/W |  |  |  | Same as
3 | 3225-3226 | SpecialDay2_Time3 | SpecialDay2_Time3 | R/W |  |  |  | Same as
3 | 3227-3228 | SpecialDay2_Time4 | SpecialDay2_Time4 | R/W |  |  |  | Same as
3 | 3229-3230 | SpecialDay2_Time5 | SpecialDay2_Time5 | R/W |  |  |  | Same as
3 | 3231-3232 | SpecialDay2_Time6 | SpecialDay2_Time6 | R/W |  |  |  | Same as
3 | 3233-3234 | SpecialDay2_Time7 | SpecialDay2_Time7 | R/W |  |  |  | Same as
3 | 3235-3236 | SpecialDay2_Time8 | SpecialDay2_Time8 | R/W |  |  |  | Same as
3 | 3237-3238 | SpecialDay2_Time9 | SpecialDay2_Time9 | R/W |  |  |  | Same as
3 | 3239-3249 | Reserve | Reserve | R/W
4 | 0 | InverterStatus | Inverter run state |  | 0:waiting,
4 | 1 | PpvH | Input power (high) |  |  | 0.1W
4 | 2 | PpvL | Input power (low) |  |  | 0.1W
4 | 3 | Vpv1 | PV1 voltage |  |  | 0.1V
4 | 4 | PV1Curr | PV1 input current |  |  | 0.1A
4 | 5 | Ppv1H | PV1 input power(high) |  |  | 0.1W
4 | 6 | Ppv1L | PV1 input power(low) |  |  | 0.1W
4 | 7 | Vpv2 | PV2 voltage |  |  | 0.1V
4 | 8 | PV2Curr | PV2 input current |  |  | 0.1A
4 | 9 | Ppv2H | PV2 input power (high) |  |  | 0.1W
4 | 10 | Ppv2L | PV2 input power (low) |  |  | 0.1W
4 | 11 | Vpv3 | PV3 voltage |  |  | 0.1V
4 | 12 | PV3Curr | PV3 input current |  |  | 0.1A
4 | 13 | Ppv3H | PV3 input power (high) |  |  | 0.1W
4 | 14 | Ppv3L | PV3 input power (low) |  |  | 0.1W
4 | 15 | Vpv4 | PV4 voltage |  |  | 0.1V
4 | 16 | PV4Curr | PV4 input current |  |  | 0.1A
4 | 17 | Ppv4H | PV4 input power (high) |  |  | 0.1W
4 | 18 | Ppv4L | PV4 input power (low) |  |  | 0.1W
4 | 19 | Vpv5 | PV5 voltage |  |  | 0.1V
4 | 20 | PV5Curr | PV5 input current |  |  | 0.1A
4 | 21 | Ppv5H | PV5 input power(high) |  |  | 0.1W
4 | 22 | Ppv5L | PV5 input power(low) |  |  | 0.1W
4 | 23 | Vpv6 | PV6 voltage |  |  | 0.1V
4 | 24 | PV6Curr | PV6 input current |  |  | 0.1A
4 | 25 | Ppv6H | PV6 input power (high) |  |  | 0.1W
4 | 26 | Ppv6L | PV6 input power (low) |  |  | 0.1W
4 | 27 | Vpv7 | PV7 voltage |  |  | 0.1V
4 | 28 | PV7Curr | PV7 input current |  |  | 0.1A
4 | 29 | Ppv7H | PV7 input power (high) |  |  | 0.1W
4 | 30 | Ppv7L | PV7 input power (low) |  |  | 0.1W
4 | 31 | Vpv8 | PV8 voltage |  |  | 0.1V
4 | 32 | PV8Curr | PV8 input current |  |  | 0.1A
4 | 33 | Ppv8H | PV8 input power (high) |  |  | 0.1W
4 | 34 | Ppv8L | PV8 input power (low) |  |  | 0.1W
4 | 35 | PacH | Output power (high) |  |  | 0.1W
4 | 36 | PacL | Output power (low) |  |  | 0.1W
4 | 37 | Fac | Grid frequency |  |  | 0.01Hz
4 | 38 | Vac1 | Three/single phase grid voltage |  |  | 0.1V
4 | 39 | Iac1 | Three/single phase grid output current |  |  | 0.1A
4 | 40 | Pac1H | Three/single phase grid output watt |  |  | 0.1VA
4 | 41 | Pac1L | Three/single phase grid output watt |  |  | 0.1VA
4 | 42 | Vac2 | Three phase grid voltage |  |  | 0.1V
4 | 43 | Iac2 | Three phase grid output current |  |  | 0.1A
4 | 44 | Pac2H | Three phase grid output power (high) |  |  | 0.1VA
4 | 45 | Pac2L | Three phase grid output power (low) |  |  | 0.1VA
4 | 46 | Vac3 | Three phase grid voltage |  |  | 0.1V
4 | 47 | Iac3 | Three phase grid output current |  |  | 0.1A
4 | 48 | Pac3H | Three phase grid output power (high) |  |  | 0.1VA
4 | 49 | Pac3L | Three phase grid output power (low) |  |  | 0.1VA
4 | 50 | Vac_RS | Three phase grid voltage |  |  | 0.1V |  | Line voltage
4 | 51 | Vac_ST | Three phase grid voltage |  |  | 0.1V |  | Line voltage
4 | 52 | Vac_TR | Three phase grid voltage |  |  | 0.1V |  | Line voltage
4 | 53 | EactodayH | Today generate energy (high) |  |  | 0.1kWH
4 | 54 | EactodayL | Today generate energy (low) |  |  | 0.1kWH
4 | 55 | EactotalH | Total generate energy (high) |  |  | 0.1kWH
4 | 56 | EactotalL | Total generate energy (low) |  |  | 0.1kWH
4 | 57 | TimetotalH | Work time total (high) |  |  | 0.5s
4 | 58 | TimetotalL | Work time total (low) |  |  | 0.5s
4 | 59 | Epv1_todayH | PV1Energy today(high) |  |  | 0.1kWh
4 | 60 | Epv1_todayL | PV1Energy today (low) |  |  | 0.1kWh
4 | 61 | Epv1_totalH | PV1Energy total(high) |  |  | 0.1kWh
4 | 62 | Epv1_totalL | PV1Energy total (low) |  |  | 0.1kWh
4 | 63 | Epv2_todayH | PV2Energy today(high) |  |  | 0.1kWh
4 | 64 | Epv2_todayL | PV2Energy today (low) |  |  | 0.1kWh
4 | 65 | Epv2_totalH | PV2Energy total(high) |  |  | 0.1kWh
4 | 66 | Epv2_totalL | PV2Energy total (low) |  |  | 0.1kWh
4 | 67 | Epv3_todayH | PV3 Energy today(high) |  |  | 0.1kWh
4 | 68 | Epv3_todayL | PV3 Energy today (low) |  |  | 0.1kWh
4 | 69 | Epv3_totalH | PV3 Energy total(high) |  |  | 0.1kWh
4 | 70 | Epv3_totalL | PV3 Energy total (low) |  |  | 0.1kWh
4 | 71 | Epv4_todayH | PV4Energy today(high) |  |  | 0.1kWh
4 | 72 | Epv4_todayL | PV4Energy today (low) |  |  | 0.1kWh
4 | 73 | Epv4_totalH | PV4Energy total(high) |  |  | 0.1kWh
4 | 74 | Epv4_totalL | PV4Energy total (low) |  |  | 0.1kWh
4 | 75 | Epv5_todayH | PV5Energy today(high) |  |  | 0.1kWh
4 | 76 | Epv5_todayL | PV5Energy today (low) |  |  | 0.1kWh
4 | 77 | Epv5_totalH | PV5Energy total(high) |  |  | 0.1kWh
4 | 78 | Epv5_totalL | PV5Energy total (low) |  |  | 0.1kWh
4 | 79 | Epv6_todayH | PV6Energy today(high) |  |  | 0.1kWh
4 | 80 | Epv6_todayL | PV6Energy today (low) |  |  | 0.1kWh
4 | 81 | Epv6_totalH | PV6Energy total(high) |  |  | 0.1kWh
4 | 82 | Epv6_totalL | PV6Energy total (low) |  |  | 0.1kWh
4 | 83 | Epv7_todayH | PV7Energy today(high) |  |  | 0.1kWh
4 | 84 | Epv7_todayL | PV7Energy today (low) |  |  | 0.1kWh
4 | 85 | Epv7_totalH | PV7 Energy total(high) |  |  | 0.1kWh
4 | 86 | Epv7_totalL | PV7Energy total (low) |  |  | 0.1kWh
4 | 87 | Epv8_todayH | PV8Energy today(high) |  |  | 0.1kWh
4 | 88 | Epv8_todayL | PV8Energy today (low) |  |  | 0.1kWh
4 | 89 | Epv8_totalH | PV8Energy total(high) |  |  | 0.1kWh
4 | 90 | Epv8_totalL | PV8Energy total (low) |  |  | 0.1kWh
4 | 91 | Epv_totalH | PV Energy total(high) |  |  | 0.1kWh
4 | 92 | Epv_totalL | PV Energy total (low) |  |  | 0.1kWh
4 | 93 | Temp1 | Inverter temperature |  |  | 0.1C
4 | 94 | Temp2 | The inside IPM in inverter Temperature |  |  | 0.1C
4 | 95 | Temp3 | Boost temperature |  |  | 0.1C
4 | 96 | Temp4
4 | 97 | uwBatVolt_DSP | BatVolt_DSP |  | 0.1V | BatVolt(DSP)
4 | 98 | PBusVoltage | P Bus inside Voltage |  |  | 0.1V
4 | 99 | NBusVoltage | N Bus inside Voltage |  |  | 0.1V
4 | 100 | IPF | Inverter output PF now |  | 0-20000
4 | 101 | RealOPPercent | Real Output power Percent |  | 0.01
4 | 102 | OPFullwattH | Output Maxpower Limited high
4 | 103 | OPFullwattL | Output Maxpower Limited low |  |  | 0.1W
4 | 104 | DeratingMode | DeratingMode |  | 0:no derate;
4 | 105 | FaultMaincode | Inverter fault maincode
4 | 107 | FaultSubcode | Inverter fault subcode
4 | 108 | RemoteCtrlEn |  |  | 0.Load First |  |  | StoragePow er (SPA)
4 | 109 | RemoteCtrlPower |  |  | 2.Grid |  |  | StoragePow er (SPA)
4 | 110 | WarningbitH | Warning bit H
4 | 111 | WarnSubcode | Inverter warn subcode
4 | 112 | WarnMaincode | Inverter warn maincode
4 | 113 | realPowerPercent | real Power Percent |  | 0-100 | % |  | MAX
4 | 114 | invstartdelaytime | inv start delay time
4 | 115 | bINVAllFaultCode | bINVAllFaultCode
4 | 116 | ACchargePower_H | Grid power to local load |  | 0.1kwh |  |  | Storage
4 | 117 | ACchargePower_L | Grid power to local load |  | 0.1kwh |  |  | Storage
4 | 118 | Priority |  |  | 0:Load First |  |  | Storage
4 | 119 | BatteryType |  |  | 0：Lead-acid |  |  | Storage
4 | 120 | AutoProofreadCMD | Aging mode Auto-calibration command |  |  |  |  | Storage
4 | 124 | reserved | [5 empty] | off
4 | 125 | PIDPV1_Voltage | PID PV1PE Volt/ Flyspan voltage |  | 0~1000V | 0.1V
4 | 126 | PIDPV1_Current | PID PV1PE Curr |  | -10~10mA | 0.1mA
4 | 127 | PIDPV2_Voltage | PID PV2PE Volt/ |  | 0~1000V | 0.1V
4 | 128 | PIDPV2_Current | PID PV2PE Curr |  | -10~10mA | 0.1mA
4 | 129 | PIDPV3_Voltage | PID PV3PE Volt/ |  | 0~1000V | 0.1V
4 | 130 | PIDPV3_Current | PID PV3PE Curr |  | -10~10mA | 0.1mA
4 | 131 | PIDPV4_Voltage | PID PV4PE Volt/ |  | 0~1000V | 0.1V
4 | 132 | PIDPV4_Current | PID PV4PE Curr |  | -10~10mA | 0.1mA
4 | 133 | PIDPV5_Voltage | PID PV5PE Volt/ |  | 0~1000V | 0.1V
4 | 134 | PIDPV5_Current | PID PV5PE Curr |  | -10~10mA | 0.1mA
4 | 135 | PIDPV6_Voltage | PID PV6PE Volt/ |  | 0~1000V | 0.1V
4 | 136 | PIDPV6_Current | PID PV6PE Curr |  | -10~10mA | 0.1mA
4 | 137 | PIDPV7_Voltage | PID PV7PE Volt/ |  | 0~1000V | 0.1V
4 | 138 | PIDPV7_Current | PID PV7PE Curr |  | -10~10mA | 0.1mA
4 | 139 | PIDPV8_Voltage | PID PV8PE Volt/ |  | 0~1000V | 0.1V
4 | 140 | PIDPV8_Current | PID PV8PE Curr |  | -10~10mA | 0.1mA
4 | 141 | PIDStatus | Bit0~7:PID Working Status |  | 0~3
4 | 142 | V_String1 | PV String1 voltage |  |  | 0.1V
4 | 143 | Curr_String1 | PV String1 current |  | -15~15A | 0.1A
4 | 144 | V_String2 | PV String2 voltage |  |  | 0.1V
4 | 145 | Curr_String2 | PV String2 current |  | -15~15A | 0.1A
4 | 146 | V_String3 | PV String3 voltage |  |  | 0.1V
4 | 147 | Curr_String3 | PV String3 current |  | -15~15A | 0.1A
4 | 148 | V_String4 | PV String4 voltage |  |  | 0.1V
4 | 149 | Curr_String4 | PV String4 current |  | -15~15A | 0.1A
4 | 150 | V_String5 | PV String5 voltage |  |  | 0.1V
4 | 151 | Curr_String5 | PV String5 current |  | -15~15A | 0.1A
4 | 152 | V_String6 | PV String6 voltage |  |  | 0.1V
4 | 153 | Curr_String6 | PV String6 current |  | -15~15A | 0.1A
4 | 154 | V_String7 | PV String7 voltage |  |  | 0.1V
4 | 155 | Curr_String7 | PV String7 current |  | -15~15A | 0.1A
4 | 156 | V_String8 | PV String8 voltage |  |  | 0.1V
4 | 157 | Curr_String8 | PV String8 current |  | -15A~15A | 0.1A
4 | 158 | V_String9 | PV String9 voltage |  |  | 0.1V
4 | 159 | Curr_String9 | PV String9 current |  | -15A~15A | 0.1A
4 | 160 | V_String10 | PV String10 voltage |  |  | 0.1V
4 | 161 | Curr_String10 | PV String10 current |  | -15~15A | 0.1A
4 | 162 | V_String11 | PV String11 voltage |  |  | 0.1V
4 | 163 | Curr_String11 | PV String11 current |  | -15~15A | 0.1A
4 | 164 | V_String12 | PV String12 voltage |  |  | 0.1V
4 | 165 | Curr_String12 | PV String12 current |  | -15~15A | 0.1A
4 | 166 | V_String13 | PV String13 voltage |  |  | 0.1V
4 | 167 | Curr_String13 | PV String13 current |  | -15A~15A | 0.1A
4 | 168 | V_String14 | PV String14 voltage |  |  | 0.1V
4 | 169 | Curr_String14 | PV String14 current |  | -15~15A | 0.1A
4 | 170 | V_String15 | PV String15 voltage |  |  | 0.1V
4 | 171 | Curr_String15 | PV String15 current |  | -15~15A | 0.1A
4 | 172 | V_String16 | PV String16 voltage |  |  | 0.1V
4 | 173 | Curr_String16 | PV String16 current |  | -15~15A | 0.1A
4 | 174 | StrUnmatch | Bit0~15: String1~16 unmatch |  |  |  |  | suggestive
4 | 175 | StrCurrentUnblance | Bit0~15: String1~16 current unblance |  |  |  |  | suggestive
4 | 176 | StrDisconnect | Bit0~15: String1~16 disconnect |  |  |  |  | suggestive
4 | 177 | PIDFaultCode | Bit0:Output over voltage
4 | 178 | StringPrompt | String Prompt
4 | 179 | PVWarningValue | PV Warning Value
4 | 180 | DSP075Value | DSP075 Warning Value
4 | 181 | DSP075Value | DSP075 Fault Value
4 | 182 | DSP067Data1 | DSP067 Debug Data1
4 | 183 | DSP067Data2 | DSP067 Debug Data2
4 | 184 | DSP067Data3 | DSP067 Debug Data3
4 | 185 | DSP067Data4 | DSP067 Debug Data4
4 | 186 | DSP067Data5 | DSP067 Debug Data5
4 | 187 | DSP067Data6 | DSP067 Debug Data6
4 | 188 | DSP067Data7 | DSP067 Debug Data7
4 | 189 | DSP067Data8 | DSP067 Debug Data8
4 | 190 | DSP075Data1 | DSP075 Debug Data1
4 | 191 | DSP075Data2 | DSP075 Debug Data2
4 | 192 | DSP075Data3 | DSP075 Debug Data3
4 | 193 | DSP075Data4 | DSP075 Debug Data4
4 | 194 | DSP075Data55 | DSP075 Debug Data5
4 | 195 | DSP075Data6 | DSP075 Debug Data6
4 | 196 | DSP075Data7 | DSP075 Debug Data7
4 | 197 | DSP075Data8 | DSP075 Debug Data8
4 | 198 | bUSBAgingTestOk | USBAgingTestOkFlag |  | 0-1
4 | 199 | bFlashEraseAging | FlashEraseAgingOkFlag |  | 0-1
4 | 200 | PVISO | PVISOValue |  |  | KΩ
4 | 201 | R_DCI | R DCI Curr |  |  | 0.1mA
4 | 202 | S_DCI | S DCI Curr |  |  | 0.1mA
4 | 203 | T_DCI | T DCI Curr |  |  | 0.1mA
4 | 204 | PID_Bus | PIDBusVolt |  |  | 0.1V
4 | 205 | GFCI | GFCI Curr |  |  | mA
4 | 206 | SVG_APF | SVG/APF Status+SVGAPFEqualRatio |  | High 8 bit：
4 | 207 | CT_I_R | R phase load side current for SVG |  |  | 0.1A
4 | 208 | CT_I_S | S phase load side current for SVG |  |  | 0.1A
4 | 209 | CT_I_T | T phase load side current for SVG |  |  | 0.1A
4 | 210 | CT_Q_RH | R phase load side output power for SVG(High) |  |  | 0.1Var
4 | 211 | CT_Q_RL | R phase load side output power for SVG(low) |  |  | 0.1Var
4 | 212 | CT_Q_SH | S phase load side output power for SVG(High) reactive |  |  | 0.1Var
4 | 213 | CT_Q_SL | S phase load side output power for SVG(low) reactive |  |  | 0.1Var
4 | 214 | CT_Q_TH | T phase load side output power for SVG(High) |  |  | 0.1Var
4 | 215 | CT_Q_TL | T phase load side output power for SVG(low) |  |  | 0.1Var
4 | 216 | CTHAR_I_R | R phase load side harmonic |  |  | 0.1A
4 | 217 | CTHAR_I_S | S phase load side harmonic |  |  | 0.1A
4 | 218 | CTHAR_I_T | T phase load side harmonic |  |  | 0.1A
4 | 219 | COMP_Q_RH | R phase compensate reactive power for SVG(High) |  |  | 0.1Var
4 | 220 | COMP_Q_RL | R phase compensate reactive power for SVG(low) |  |  | 0.1Var
4 | 221 | COMP_Q_SH | S phase compensate reactive power for SVG(High) |  |  | 0.1Var
4 | 222 | COMP_Q_SL | S phase compensate reactive power |  |  | 0.1Var
4 | 223 | COMP_Q_TH | T phase compensate reactive power for SVG(High) |  |  | 0.1Var
4 | 224 | COMP_Q_TL | T phase compensate reactive power for SVG(low) |  |  | 0.1Var
4 | 225 | COMPHAR_I_R | R phase compensate harmonic for |  |  | 0.1A
4 | 226 | COMPHAR_I_S | S phase compensate harmonic for |  |  | 0.1A
4 | 227 | COMPHAR_I_T | T phase compensate harmonic for |  |  | 0.1A
4 | 228 | bRS232AgingTest | RS232AgingTestOkFlag |  | 0-1
4 | 229 | bFanFaultBit | Bit0: Fan 1 fault bit
4 | 230 | SacH | Output apparent power H |  |  | 0.1W
4 | 231 | SacL | Output apparent power L |  |  | 0.1W
4 | 232 | ReActPowerH | Real Output Reactive Power H |  | Int32 | 0.1W
4 | 233 | ReActPowerL | Real Output Reactive Power L
4 | 234 | ReActPowerMaxH | Nominal Output Reactive Power H |  |  | 0.1var
4 | 235 | ReActPowerMaxL | Nominal Output Reactive Power L
4 | 236 | ReActPower_TotalH | Reactive power generation |  |  | 0.1kwh
4 | 237 | ReActPower_TotalL | Reactive power generation
4 | 238 | bAfciStatus |  |  | 0：Waiting
4 | 239 | uwPresentFFTValue_CHANNEL_A | PresentFFTValue [CHANNEL_A]
4 | 240 | uwPresentFFTValue_CHANNEL_B | PresentFFTValue [CHANNEL_B]
4 | 241 | DSP067Data1 | DSP067 Debug Data1
4 | 242 | DSP067Data2 | DSP067 Debug Data2
4 | 243 | DSP067Data3 | DSP067 Debug Data3
4 | 244 | DSP067Data4 | DSP067 Debug Data4
4 | 245 | DSP067Data5 | DSP067 Debug Data5
4 | 246 | DSP067Data6 | DSP067 Debug Data6
4 | 247 | DSP067Data7 | DSP067 Debug Data7
4 | 248 | DSP067Data8 | DSP067 Debug Data8
4 | 875 | Vpv9 | PV9 voltage |  |  | 0.1V
4 | 876 | PV9Curr | PV9 Input current |  |  | 0.1A
4 | 877 | Ppv9H | PV9 input power (High) |  |  | 0.1W
4 | 878 | Ppv9L | PV9 input power (Low) |  |  | 0.1W
4 | 879 | Vpv10 | PV10 voltage |  |  | 0.1V
4 | 880 | PV10Curr | PV10 Input current |  |  | 0.1A
4 | 881 | Ppv10H | PV10 input power (High) |  |  | 0.1W
4 | 882 | Ppv10L | PV10 input power (Low) |  |  | 0.1W
4 | 883 | Vpv11 | PV11 voltage |  |  | 0.1V
4 | 884 | PV11Curr | PV11 Input current |  |  | 0.1A
4 | 885 | Ppv11H | PV11 input power (High) |  |  | 0.1W
4 | 886 | Ppv11L | PV11 input power (Low) |  |  | 0.1W
4 | 887 | Vpv12 | PV12 voltage |  |  | 0.1V
4 | 888 | PV12Curr | PV12 Input current |  |  | 0.1A
4 | 889 | Ppv12H | PV12 input power (High) |  |  | 0.1W
4 | 890 | Ppv12L | PV12 input power (Low) |  |  | 0.1W
4 | 891 | Vpv13 | PV13 voltage |  |  | 0.1V
4 | 892 | PV13Curr | PV13 Input current |  |  | 0.1A
4 | 893 | Ppv13H | PV13 input power (High) |  |  | 0.1W
4 | 894 | Ppv13L | PV13 input power (Low) |  |  | 0.1W
4 | 895 | Vpv14 | PV14 voltage |  |  | 0.1V
4 | 896 | PV14Curr | PV14 Input current |  |  | 0.1A
4 | 897 | Ppv14H | PV14 input power (High) |  |  | 0.1W
4 | 898 | Ppv14L | PV14 input power (Low) |  |  | 0.1W
4 | 899 | Vpv15 | PV15 voltage |  |  | 0.1V
4 | 900 | PV15Curr | PV15 Input current |  |  | 0.1A
4 | 901 | Ppv15H | PV15 input power (High) |  |  | 0.1W
4 | 902 | Ppv15L | PV15 input power (Low) |  |  | 0.1W
4 | 903 | Vpv16 | PV16 voltage |  |  | 0.1V
4 | 904 | PV16Curr | PV16 Input current |  |  | 0.1A
4 | 905 | Ppv16H | PV16 input power (High) |  |  | 0.1W
4 | 906 | Ppv16L | PV16 input power (Low) |  |  | 0.1W
4 | 907 | Epv9_todayH | PV9 energy today (High) |  |  | 0.1kWh
4 | 908 | Epv9_todayL | PV9 energy today (Low) |  |  | 0.1kWh
4 | 909 | Epv9_totalH | PV9 energy total (High) |  |  | 0.1kWh
4 | 910 | Epv9_totalL | PV9 energy total (Low) |  |  | 0.1kWh
4 | 911 | Epv10_todayH | PV10 energy today (High) |  |  | 0.1kWh
4 | 912 | Epv10_todayL | PV10 energy today (Low) |  |  | 0.1kWh
4 | 913 | Epv10_totalH | PV10 energy total (High) |  |  | 0.1kWh
4 | 914 | Epv10_totalL | PV10 energy total (Low) |  |  | 0.1kWh
4 | 915 | Epv11_todayH | PV11 energy today (High) |  |  | 0.1kWh
4 | 916 | Epv11_todayL | PV11 energy today (Low) |  |  | 0.1kWh
4 | 917 | Epv11_totalH | PV11 energy total (High) |  |  | 0.1kWh
4 | 918 | Epv11_totalL | PV11 energy total (Low) |  |  | 0.1kWh
4 | 919 | Epv12_todayH | PV12 energy today (High) |  |  | 0.1kWh
4 | 920 | Epv12_todayL | PV12 energy today (Low) |  |  | 0.1kWh
4 | 921 | Epv12_totalH | PV12 energy total (High) |  |  | 0.1kWh
4 | 922 | Epv12_totalL | PV12 energy total (Low) |  |  | 0.1kWh
4 | 923 | Epv13_todayH | PV13 energy today (High) |  |  | 0.1kWh
4 | 924 | Epv13_todayL | PV13 energy today (Low) |  |  | 0.1kWh
4 | 925 | Epv13_totalH | PV13 energy total (High) |  |  | 0.1kWh
4 | 926 | Epv13_totalL | PV13 energy total (Low) |  |  | 0.1kWh
4 | 927 | Epv14_todayH | PV14 energy today (High) |  |  | 0.1kWh
4 | 928 | Epv14_todayL | PV14 energy today (Low) |  |  | 0.1kWh
4 | 929 | Epv14_totalH | PV14 energy total (High) |  |  | 0.1kWh
4 | 930 | Epv14_totalL | PV14 energy total (Low) |  |  | 0.1kWh
4 | 931 | Epv15_todayH | PV15 energy today (High) |  |  | 0.1kWh
4 | 932 | Epv15_todayL | PV15 energy today (Low) |  |  | 0.1kWh
4 | 933 | Epv15_totalH | PV15 energy total (High) |  |  | 0.1kWh
4 | 934 | Epv15_totalL | PV15 energy total (Low) |  |  | 0.1kWh
4 | 935 | Epv16_todayH | PV16 energy today (High) |  |  | 0.1kWh
4 | 936 | Epv16_todayL | PV16 energy today (Low) |  |  | 0.1kWh
4 | 937 | Epv16_totalH | PV16 energy total (High) |  |  | 0.1kWh
4 | 938 | Epv16_totalL | PV16 energy total (Low) |  |  | 0.1kWh
4 | 939 | PIDPV9_Voltage | PID PV9PE Volt/ Flyspan |  | 0~1000V | 0.1V
4 | 940 | PIDPV9_Current | PID PV9PE Current |  | -10~10mA | 0.1mA
4 | 941 | PIDPV10_ | PID PV10PE/ Flyspan voltage (MAX |  | 0~1000V | 0.1V
4 | 942 | PIDCurrentPV10_ | PID PV10PE Current |  | -10~10mA | 0.1mA
4 | 943 | PIDVoltagePV11_ | PID PV11PE Volt/ |  | 0~1000V | 0.1V
4 | 944 | PIDCurrentPV11_ | PID PV11PE Current |  | -10~10mA | 0.1mA
4 | 945 | PIDVoltagePV12_ | PID PV12PE Volt/ |  | 0~1000V | 0.1V
4 | 946 | PIDCurrentPV12_ | PID PV12PE Current |  | -10~10mA | 0.1mA
4 | 947 | PIDVoltagePV13_ | PID PV13PE Volt/ |  | 0~1000V | 0.1V
4 | 948 | PIDCurrentPV13_ | PID PV13PE Current |  | -10~10mA | 0.1mA
4 | 949 | PIDVoltagePV14_ | PID PV14PE Volt/ |  | 0~1000V | 0.1V
4 | 950 | PIDCurrentPV14_ | PID PV14PE Current |  | -10~10mA | 0.1mA
4 | 951 | PIDVoltagePV15_ | PID PV15PE Volt/ |  | 0~1000V | 0.1V
4 | 952 | PIDCurrentPV15_ | PID PV15PE Current |  | -10~10mA | 0.1mA
4 | 953 | PIDVoltagePV16_ | PID PV16PE Volt/ |  | 0~1000V | 0.1V
4 | 954 | PIDCurrent | PID PV16PE Current |  | -10~10mA | 0.1mA
4 | 955 | V_String17 | PV String 17 voltage |  |  | 0.1V
4 | 956 | Curr_String17 | PV String 17 Current |  | -15~15A | 0.1A
4 | 957 | V_String18 | PV String 18 voltage |  |  | 0.1V
4 | 958 | Curr_String18 | PV String 18 Current |  | -15~15A | 0.1A
4 | 959 | V_String19 | PV String 19 voltage |  |  | 0.1V
4 | 960 | Curr_String19 | PV String 19 Current |  | -15~15A | 0.1A
4 | 961 | V_String20 | PV String 20 voltage |  |  | 0.1V
4 | 962 | Curr_String20 | PV String 20 Current |  | -15~15A | 0.1A
4 | 963 | V_String21 | PV String 21 voltage |  |  | 0.1V
4 | 964 | Curr_String21 | PV String 21 Current |  | -15~15A | 0.1A
4 | 965 | V_String22 | PV String22 voltage |  |  | 0.1V
4 | 966 | Curr_String22 | PV String 22 Current |  | -15~15A | 0.1A
4 | 967 | V_String23 | PV String 23 voltage |  |  | 0.1V
4 | 968 | Curr_String23 | PV String 23 Current |  | -15~15A | 0.1A
4 | 969 | V_String24 | PV String 24 voltage |  | -15A~15A | 0.1A
4 | 970 | Curr_String24 | PV String 24 Current |  |  | 0.1V
4 | 971 | V_String25 | PV String 25 voltage |  | -15A~15A | 0.1A
4 | 972 | Curr_String25 | PV String 25 Current |  |  | 0.1V
4 | 973 | V_String26 | PV String 26 voltage |  | -15~15A | 0.1A
4 | 974 | Curr_String26 | PV String 26 Current |  |  | 0.1V
4 | 975 | V_String27 | PV String 27 voltage |  | -15~15A | 0.1A
4 | 976 | Curr_String27 | PV String 27 Current |  |  | 0.1V
4 | 977 | V_String28 | PV String 28 voltage |  | -15~15A | 0.1A
4 | 978 | Curr_String28 | PV String 28 Current |  |  | 0.1V
4 | 979 | V_String29 | PV String 29 voltage |  | -15A~15A | 0.1A
4 | 980 | Curr_String29 | PV String 29 Current |  |  | 0.1V
4 | 981 | V_String30 | PV String 30 voltage |  | -15~15A | 0.1A
4 | 982 | Curr_String30 | PV String 30 Current |  |  | 0.1V
4 | 983 | V_String31 | PV String 31 voltage |  | -15~15A | 0.1A
4 | 984 | Curr_String31 | PV String 31 Current |  |  | 0.1V
4 | 985 | V_String32 | PV String 32 voltage |  | -15~15A | 0.1A
4 | 986 | Curr_String32 | PV String 32 Current
4 | 987 | StrUnmatch2 | Bit0~15: String 17~32 unmatch
4 | 988 | StrCurrentUnblance2 | Bit0~15:String 17~32 current
4 | 989 | StrDisconnect2 | Bit0~15: String 17~32 disconnect
4 | 990 | PVWarningValue | PV Warning Value (PV9-PV16)
4 | 991 | StrWaringvalue1 | string1~string16 abnormal
4 | 992 | StrWaringvalue2 | string17~string32 abnormal
4 | 999 | SystemCmd | M3 to DSP system command
4 | 1000 | uwSysWorkMode | System work mode |  | 0x00:waiting module
4 | 1001 | Systemfaultword0 | System fault word0
4 | 1002 | Systemfaultword1 | System fault word1
4 | 1003 | Systemfaultword2 | System fault word2
4 | 1004 | Systemfaultword3 | System fault word3
4 | 1005 | Systemfaultword4 | System fault word4
4 | 1006 | Systemfaultword5 | System fault word5
4 | 1007 | Systemfaultword6 | System fault word6
4 | 1008 | Systemfaultword7 | System fault word7
4 | 1009 | Pdischarge1H | Discharge power(high) |  |  | 0.1W
4 | 1010 | Pdischarge1L | Discharge power (low) |  |  | 0.1W
4 | 1011 | Pcharge1H | Charge power(high) |  |  | 0.1W
4 | 1012 | Pcharge1L | Charge power (low) |  |  | 0.1W
4 | 1013 | Vbat | Battery voltage |  |  | 0.1V
4 | 1014 | SOC | State of charge Capacity |  | 0-100 | 0.01 |  | lith/leadacid
4 | 1015 | PactouserRH | AC power to user H |  |  | 0.1w
4 | 1016 | PactouserRL | AC power to user L |  |  | 0.1w
4 | 1017 | PactouserSH | Pactouser S H |  |  | 0.1w
4 | 1018 | PactouserSL | Pactouser S L |  |  | 0.1w
4 | 1019 | PactouserTH | Pactouser T H |  |  | 0.1w
4 | 1020 | PactouserTL | Pactouser T H |  |  | 0.1w
4 | 1021 | PactouserTotalH | AC power to user total H |  |  | 0.1w
4 | 1022 | PactouserTotalL | AC power to user total L |  |  | 0.1w
4 | 1023 | PactogridRH | AC power to grid H |  |  | 0.1w
4 | 1024 | PactogridRL | AC power to grid L |  |  | 0.1w
4 | 1025 | PactogridSH |  |  |  | 0.1w
4 | 1026 | PactogridSL |  |  |  | 0.1w
4 | 1027 | PactogridTH |  |  |  | 0.1w
4 | 1028 | PactogridTL |  |  |  | 0.1w
4 | 1029 | PactogridtotalH | AC power to grid total H |  |  | 0.1w
4 | 1030 | PactogridtotalL | AC power to grid total L |  |  | 0.1w
4 | 1031 | PLocalLoadRH | INV power to local load H |  |  | 0.1w
4 | 1032 | PLocalLoadRL | INV power to local load L |  |  | 0.1w
4 | 1033 | PLocalLoadSH |  |  |  | 0.1w
4 | 1034 | PLocalLoadSL |  |  |  | 0.1w
4 | 1035 | PLocalLoadTH |  |  |  | 0.1w
4 | 1036 | PLocalLoadTL |  |  |  | 0.1w
4 | 1037 | PLocalLoadtotalH | INV power to local load total H |  |  | 0.1w
4 | 1038 | PLocalLoadtotalL | INV power to local load total |  |  | 0.1w
4 | 1039 | IPMTemperature | REC Temperature |  |  | 0.1℃ |  | No use
4 | 1040 | Battery | Battery Temperature |  |  | 0.1℃ |  | Lead acid/lithium battery temp
4 | 1041 | SPDSPStatus | SP state |  |  |  |  | CHG/DisCHG
4 | 1042 | SPBusVolt | SP BUS2 Volt |  |  | 0.1V
4 | 1044 | Etouser_todayH | Energy to user today high |  |  | 0.1kWh
4 | 1045 | Etouser_todayL | Energy to user today low |  |  | 0.1kWh
4 | 1046 | Etouser_totalH | Energy to user total high |  |  | 0.1kWh
4 | 1047 | Etouser_totalL | Energy to user total high |  |  | 0.1kWh
4 | 1048 | Etogrid_todayH | Energy to grid today high |  |  | 0.1kWh
4 | 1049 | Etogrid_todayL | Energy to grid today low |  |  | 0.1kWh
4 | 1050 | Etogrid_totalH | Energy to grid total high |  |  | 0.1kWh
4 | 1051 | Etogrid_totalL | Energy to grid total high |  |  | 0.1kWh
4 | 1052 | Edischarge1_todayH | Discharge energy1 today |  |  | 0.1kWh
4 | 1053 | Edischarge1_todayL | Discharge energy1 today |  |  | 0.1kWh
4 | 1054 | Edischarge1_totalH | Total discharge energy1 (high) |  |  | 0.1kWh
4 | 1055 | Edischarge1_totalL | Total discharge energy1 (low) |  |  | 0.1kWh
4 | 1056 | Echarge1_todayH | Charge1 energy today |  |  | 0.1kWh
4 | 1057 | Echarge1_todayL | Charge1 energy today |  |  | 0.1kWh
4 | 1058 | Echarge1_totalH | Charge1 energy total |  |  | 0.1kWh
4 | 1059 | Echarge1_totalL | Charge1 energy total |  |  | 0.1kWh
4 | 1060 | ElocalLoad_TodayH | Local load energy today |  |  | 0.1kWh
4 | 1061 | ElocalLoad_TodayL | Local load energy today |  |  | 0.1kWh
4 | 1062 | ElocalLoad_TotalH | Local load energy total |  |  | 0.1kWh
4 | 1063 | ElocalLoad_TotalL | Local load energy total |  |  | 0.1kWh
4 | 1064 | dwExportLimitApparentPower | ExportLimitApparentPower H |  |  | 0.1kWh |  | ApparentPower
4 | 1065 | dwExportLimitApparentPower | ExportLimitApparentPower L |  |  | 0.1kWh |  | ApparentPower
4 | 1067 | EPSFac | UPSfrequency |  | 5000/6000 | 0.01Hz
4 | 1068 | EPSVac1 | UPS phase R output voltage |  | 2300 | 0.1V
4 | 1069 | EPSIac1 | UPS phase R output current |  |  | 0.1A
4 | 1070 | EPSPac1H | UPS phase R output power (H) |  |  | 0.1VA
4 | 1071 | EPSPac1L | UPS phase R output power (L) |  |  | 0.1VA
4 | 1072 | EPSVac2 | UPS phase S output voltage |  |  | 0.1V
4 | 1073 | EPSIac2 | UPS phase S output current |  |  | 0.1A |  | No use
4 | 1074 | EPSPac2H | UPS phase S output power (H) |  |  | 0.1VA
4 | 1075 | EPSPac2L | UPS phase S output power (L) |  |  | 0.1VA
4 | 1076 | EPSVac3 | UPS phase T output voltage |  |  | 0.1V
4 | 1077 | EPSIac3 | UPS phase T output current |  |  | 0.1A |  | No use
4 | 1078 | EPSPac3H | UPS phase T output power (H) |  |  | 0.1VA
4 | 1079 | EPSPac3L | UPS phase T output power (L) |  |  | 0.1VA
4 | 1080 | Loadpercent | Load percent of UPS ouput |  | 0-100 | 0.01
4 | 1081 | PF | Power factor |  | 0-2 | 0.1 |  | Primary Value+1
4 | 1082 | BMS_StatusOld | StatusOld from BMS
4 | 1083 | BMS_Status | Status from BMS | R/W
4 | 1084 | BMS_ErrorOld | Error info Old from BMS
4 | 1085 | BMS_Error | Errorinfomation from BMS
4 | 1086 | BMS_SOC | SOC from BMS |  |  |  |  | R SPH6K
4 | 1087 | BMS_BatteryVolt | Battery voltage from BMS |  |  |  |  | R SPH6K
4 | 1088 | BMS_BatteryCur | Battery current from BMS
4 | 1089 | BMS_BatteryTemp | Battery temperature from BMS
4 | 1090 | BMS_MaxCurr | Max. charge/discharge current from BMS (pylon)
4 | 1091 | BMS_GaugeRM | Gauge RM from BMS
4 | 1092 | BMS_GaugeFCC | Gauge FCC from BMS
4 | 1093 | BMS_FW
4 | 1094 | BMS_DeltaVolt | Delta V from BMS
4 | 1095 | BMS_CycleCnt | Cycle Count from BMS
4 | 1096 | BMS_SOH | SOH from BMS
4 | 1097 | BMS_ConstantVolt | CV voltage from BMS
4 | 1098 | BMS_WarnInfoOld | Warning info old from BMS
4 | 1099 | BMS_WarnInfo | Warning info from BMS
4 | 1100 | BMS_GaugeICCurrrr | Gauge IC current from BMS
4 | 1101 | BMS_MCUVersion | MCU Software version from BMS
4 | 1102 | BMS_GaugeVersion | Gauge Version from BMS
4 | 1103 | BMS_wGaugeFRVersion_L | Gauge FR Version L16 from BMS
4 | 1104 | BMS_wGaugeFRVersion_H | Gauge FR Version H16 from BMS
4 | 1105 | BMS_BMSInfo | BMSInformation from BMS
4 | 1106 | BMS_PackInfo | Pack Information from BMS
4 | 1107 | BMS_UsingCap | Using Cap from BMS
4 | 1108 | uwMaxCellVolt | Maximum single battery voltage |  |  | 0.001V
4 | 1109 | uwMinCellVolt | Lowest single battery voltage |  |  | 0.001V
4 | 1110 | bModuleNum | Battery parallel number |  |  | 1
4 | 1112 | uwMaxVoltCellNo | MaxVoltCellNo |  |  | 1
4 | 1113 | uwMinVoltCellNo | MinVoltCellNo |  |  | 1
4 | 1114 | uwMaxTemprCell_10T | MaxTemprCell_10T |  |  | 0.1℃
4 | 1115 | uwMinTemprCell_10T | MinTemprCell_10T |  |  | 0.1℃
4 | 1116 | uwMaxTemprCellNo | MaxVoltTemprCellNo |  |  | 1
4 | 1117 | uwMinTemprCellNo | MinVoltTemprCellNo |  |  | 1
4 | 1118 | ProtectpackID | Faulty Battery Address |  |  | 1
4 | 1119 | MaxSOC | Parallel maximum SOC |  |  | 0.01
4 | 1120 | MinSOC | Parallel minimum SOC |  |  | 0.01
4 | 1121 | BMS_Error2 | Battery Protection 2 |  |  |  |  | CAN ID ： 0x323
4 | 1122 | BMS_Error3 | Battery Protection3 |  |  |  |  | CAN ID ： 0x323
4 | 1123 | BMS_WarnInfo2 | Battery Warn2 |  |  |  |  | CAN ID ： 0x323
4 | 1124 | ACChargeEnergyTodayH | AC Charge Energy today kWh |  |  | kwh |  | Energy today
4 | 1125 | ACChargeEnergyTodayL | AC Charge Energy today kWh |  |  | kwh
4 | 1126 | ACChargeEnergyTotalH | Energy total
4 | 1127 | ACChargeEnergyTotalL
4 | 1128 | ACChargePowerH | AC Charge Power | W
4 | 1129 | ACChargePowerL | AC Charge Power | W
4 | 1130 | 70PctINVPoweradjust | uwGridPower_70_AdjEE_SP | W
4 | 1131 | ExtraACPowertogrid_H | Extra inverte AC Power to grid |  |  |  |  | SPA used
4 | 1132 | ExtraACPowertogrid_L | Extrainverte AC Power to grid Low |  |  |  |  | SPA used
4 | 1133 | Eextra_todayH | Extra inverter PowerTOUser_Extra today (high) | R |  | 0.1kWh |  | SPA used
4 | 1134 | Eextra_todayL | Extra inverter PowerTOUser_Extra today (low) | R |  | 0.1kWh |  | SPA used
4 | 1135 | Eextra_totalH | Extra inverter PowerTOUser_Extra total(high) |  |  | 0.1kWh |  | SPA used
4 | 1136 | Eextra_totalL | Extra inverter PowerTOUser_Extra total(low) |  |  | 0.1kWh |  | SPA used
4 | 1137 | Esystem_today | System electric energy today H |  |  | 0.1kWh |  | SPA used
4 | 1138 | Esystem_today | System electric energy today L |  |  | 0.1kWh |  | self power L
4 | 1139 | Esystem_totalH | System electric energy total H |  |  | 0.1kWh |  | SPA used
4 | 1140 | Esystem_totalL | System electric energy total L |  |  | 0.1kWh |  | SPA used
4 | 1141 | Eself_todayH | self electric energy today H |  |  | 0.1kWh |  | self electric
4 | 1142 | Eself_todayL | self electric energy today L |  |  | 0.1kWh |  | self electric energy today H
4 | 1143 | Eself_totalH | self electric energy total H |  |  | 0.1kWh |  | self electric energy today L
4 | 1144 | Eself_totalL | self electric energy total L |  |  | 0.1kWh |  | reserved
4 | 1145 | PSystemH | System power H |  |  | 0.1w |  | Storage
4 | 1146 | PSystemL | System power L |  |  | 0.1w |  | System power H
4 | 1147 | PSelfH | self power H |  |  | 0.1w |  | self electric energy total H
4 | 1148 | PSelfL | self power L |  |  | 0.1w |  | self power H
4 | 1149 | EPVAll_TodayH | PV electric energy today H
4 | 1150 | EPVAll_TodayL | PV electric energy today L
4 | 1151 | AcDischargePackSn | Discharge number power pack serial | R
4 | 1152 | Accdischargepower_H | Cumulativedischarge power high | R | 0.1 | kWH
4 | 1153 | Accdischargepower_L | Cumulativedischarge power low | R | 0.1 | kWH
4 | 1154 | AccChargePackSn | charge power pack serial number | R
4 | 1155 | AccChargepower_H | Cumulative charge power H | R | 0.1 | kWH
4 | 1156 | AccChargepower_L | Cumulative charge power L | R | 0.1 | kWH
4 | 1157 | FirstBattFaultSn | FirstBattFaultSn | R
4 | 1158 | Second | Second | R
4 | 1159 | Third | Third | R
4 | 1160 | Fourth | Fourth | R
4 | 1161 | Batteryhistoryfaultcode1 | Battery history fault code 1 | R
4 | 1162 | Batteryhistoryfaultcode2 | Battery history fault code 2 | R
4 | 1163 | Batteryhistoryfaultcode3 | Battery history fault code 3 | R
4 | 1164 | Batteryhistoryfaultcode4 | Battery history fault code 4 | R
4 | 1165 | Batteryhistoryfaultcode5 | Battery history fault code 5 | R
4 | 1166 | Batteryhistoryfaultcode6 | Battery history fault code 6 | R
4 | 1167 | Batteryhistoryfaultcode7 | Battery history fault code 7 | R
4 | 1168 | Batteryhistoryfaultcode8 | Battery history fault code 8 | R
4 | 1169 | Numberofbatterycodes | Number of battery codes PACK number + BIC forward and | R
4 | 1199 | NewEPowerCalcFlag | Intelligent reading is used to identify software compatibility features |  |  |  |  | 0 ： Old energy
4 | 1200 | MaxCellVolt | Maximum cell voltage | R |  | 0.001V
4 | 1201 | MinCellVolt | Minimum cell voltage | R |  | 0.001V
4 | 1202 | ModuleNum | Number of Battery modules | R
4 | 1203 | TotalCellNum | Total number of cells | R
4 | 1204 | MaxVoltCellNo | MaxVoltCellNo | R
4 | 1205 | MinVoltCellNo | MinVoltCellNo | R
4 | 1206 | MaxTemprCell_10T |  | R |  | 0.1℃
4 | 1207 | MinTemprCell_10T |  | R |  | 0.1℃
4 | 1208 | MaxTemprCellNo | MaxTemprCellNo | R
4 | 1209 | MinTemprCellNo | MinTemprCellNo | R
4 | 1210 | ProtectPackID | Fault Pack ID | R
4 | 1211 | MaxSOC | Parallel maximum SOC | R | 0.01
4 | 1212 | MinSOC | Parallel minimum SOC | R | 0.01
4 | 1213 | BatProtect1Add | BatProtect1Add | R
4 | 1214 | BatProtect2Add | BatProtect2Add | R
4 | 1215 | BatWarn1Add | BatWarn1Add | R
4 | 1216 | BMS_HighestSoftVersion | BMS_HighestSoftVersion | R
4 | 1217 | BMS_Hardware | BMS_HardwareVersion | R
4 | 1218 | BMS_RequestType | BMS_RequestType | R
4 | 1248 | bKeyAgingTestOkFlag | Success sign of key detection before aging |  | 1：Finished test
4 | 2000 | InverterStatus | Inverter run state |  | 0:waiting, |  |  | SPA
4 | 2035 | PacH | Output power (high) |  |  | 0.1W |  | SPA
4 | 2036 | PacL | Output power (low) |  |  | 0.1W |  | SPA
4 | 2037 | Fac | Grid frequency |  |  | 0.01Hz |  | SPA
4 | 2038 | Vac1 | Three/single phase grid voltage |  |  | 0.1V |  | SPA
4 | 2039 | Iac1 | Three/single phase grid output current |  |  | 0.1A |  | SPA
4 | 2040 | Pac1H | Three/single phase grid output watt |  |  | 0.1VA |  | SPA
4 | 2041 | Pac1L | Three/single phase grid output watt |  |  | 0.1VA |  | SPA
4 | 2053 | EactodayH | Today generate energy (high) |  |  | 0.1kWH |  | SPA
4 | 2054 | EactodayL | Today generate energy (low) |  |  | 0.1kWH |  | SPA
4 | 2055 | EactotalH | Total generate energy (high) |  |  | 0.1kWH |  | SPA
4 | 2056 | EactotalL | Total generate energy (low) |  |  | 0.1kWH |  | SPA
4 | 2057 | TimetotalH | Work time total (high) |  |  | 0.5s |  | SPA
4 | 2058 | TimetotalL | Work time total (low) |  |  | 0.5s |  | SPA
4 | 2093 | Temp1 | Inverter temperature |  |  | 0.1C |  | SPA
4 | 2094 | Temp2 | The inside IPM in inverter Temperature |  |  | 0.1C |  | SPA
4 | 2095 | Temp3 | Boost temperature |  |  | 0.1C |  | SPA
4 | 2096 | Temp4 | [5 empty] | reserved
4 | 2097 | uwBatVolt_DSP | BatVolt_DSP |  |  | 0.1V |  | BatVolt(DSP)
4 | 2098 | PBusVoltage | P Bus inside Voltage |  |  | 0.1V |  | SPA
4 | 2099 | NBusVoltage | N Bus inside Voltage |  |  | 0.1V |  | SPA
4 | 2100 | RemoteCtrlEn | [5 empty] | Remote setup enable
4 | 2101 | RemoteCtrlPower | [5 empty] | Remotely set power
4 | 2102 | ExtraACPowertogrid_H | Extra inverte AC Power to grid High |  |  |  |  | SPA used
4 | 2103 | ExtraACPowertogrid_L | Extrainverte AC Power to grid Low |  |  |  |  | SPA used
4 | 2104 | Eextra_todayH | Extra inverter PowerTOUser_Extra today (high) | R |  | 0.1kWh |  | SPA used
4 | 2105 | Eextra_todayL | Extra inverter PowerTOUser_Extra today (low) | R |  | 0.1kWh |  | SPA used
4 | 2106 | Eextra_totalH | Extra inverter |  |  | 0.1kWh |  | SPA used
4 | 2107 | Eextra_totalL | Extra inverter PowerTOUser_Extra total(low) |  |  | 0.1kWh |  | SPA used
4 | 2108 | Esystem_todayH | System electric energy today H |  |  | 0.1kWh |  | SPA used
4 | 2109 | Esystem_todayL | System electric energy today L |  |  | 0.1kWh |  | SPA used
4 | 2110 | Esystem_totalH | System electric energy total H |  |  | 0.1kWh |  | SPA used
4 | 2111 | Esystem_totalL | System electric energy total L |  |  | 0.1kWh |  | SPA used
4 | 2112 | EACharge_Today | ACCharge energy today |  |  | 0.1kwh |  | Storage
4 | 2113 | EACharge_Today_L | ACCharge energy today |  |  | 0.1kwh |  | Storage
4 | 2114 | EACharge_Total_H | ACCharge energy total |  |  | 0.1kwh |  | Storage
4 | 2115 | EACharge_Total_L | ACCharge energy total |  |  | 0.1kwh |  | Storage
4 | 2116 | ACchargePowerH | Grid power to local load |  |  | 0.1kwh |  | SPA used
4 | 2117 | ACChargePowerL | Grid power to local load |  |  | 0.1kwh |  | Storage
4 | 2118 | Priority |  |  | 0:Load First |  |  | Storage
4 | 2119 | BatteryType |  |  | 0：Lead-acid |  |  | Storage
4 | 2120 | AutoProofreadCMD | Aging mode |  |  |  |  | Storage
4 | 2124 | reserved | [5 empty] | reserved
4 | 3000 | InverterStatus | Inverter run state
4 | 3001 | PpvH | PV total power |  |  | 0.1W
4 | 3002 | PpvL
4 | 3003 | Vpv1 | PV1 voltage |  |  | 0.1V
4 | 3004 | Ipv1 | PV1 input current |  |  | 0.1A
4 | 3005 | Ppv1H | PV1 power |  |  | 0.1W
4 | 3006 | Ppv1L
4 | 3007 | Vpv2 | PV2 voltage |  |  | 0.1V
4 | 3008 | Ipv2 | PV2 input current |  |  | 0.1A
4 | 3009 | Ppv2H | PV2 power |  |  | 0.1W
4 | 3010 | Ppv2L
4 | 3011 | Vpv3 | PV3 voltage |  |  | 0.1V
4 | 3012 | Ipv3 | PV3 input current |  |  | 0.1A
4 | 3013 | Ppv3H | PV3 power |  |  | 0.1W
4 | 3014 | Ppv3L
4 | 3015 | Vpv4 | PV4 voltage
4 | 3016 | Ipv4 | PV4 input current
4 | 3017 | Ppv4H | PV4 power
4 | 3018 | Ppv4L
4 | 3019 | PsysH | System output power |  |  | 0.1W
4 | 3020 | PsysL
4 | 3021 | QacH | reactive power |  |  | 0.1Var
4 | 3022 | QacL
4 | 3023 | PacH | Output power |  |  | 0.1W |  | Output power
4 | 3024 | PacL
4 | 3025 | Fac | Grid frequency |  |  | 0.01Hz |  | Grid frequency
4 | 3026 | Vac1 | Three/single phase grid voltage |  |  | 0.1V |  | Three/single
4 | 3027 | Iac1 | Three/single phase grid output current |  |  | 0.1A |  | Three/single
4 | 3028 | Pac1H | Three/single phase grid output watt |  |  | 0.1VA |  | Three/single phase grid output watt
4 | 3029 | Pac1L | VA |  |  |  |  | VA
4 | 3030 | Vac2 | Three phase grid voltage |  |  | 0.1V |  | Three phase grid voltage
4 | 3031 | Iac2 | Three phase grid output current |  |  | 0.1A |  | Three phase grid output current
4 | 3032 | Pac2H | Three phase grid output power |  |  | 0.1VA |  | Three phase grid output power
4 | 3033 | Pac2L
4 | 3034 | Vac3 | Three phase grid voltage |  |  | 0.1V |  | Three phase grid voltage
4 | 3035 | Iac3 | Three phase grid output current |  |  | 0.1A |  | Three phase grid output current
4 | 3036 | Pac3H | Three phase grid output power |  |  | 0.1VA |  | Three phase grid output power
4 | 3037 | Pac3L
4 | 3038 | Vac_RS | Three phase grid voltage |  |  | 0.1V
4 | 3039 | Vac_ST | Three phase grid voltage |  |  | 0.1V
4 | 3040 | Vac_TR | Three phase grid voltage |  |  | 0.1V
4 | 3041 | PtousertotalH | Total forward power |  |  | 0.1W |  | Total forward power
4 | 3042 | PtousertotalL
4 | 3043 | PtogridtotalH | Total reverse power |  |  | 0.1W |  | Total reverse power
4 | 3044 | PtogridtotalL
4 | 3045 | PtoloadtotalH | Total load power |  |  | 0.1W |  | Total load power
4 | 3046 | PtoloadtotalL
4 | 3047 | TimetotalH | Work time total |  |  | 0.5s
4 | 3048 | TimetotalL
4 | 3049 | EactodayH | Today generate energy |  |  | 0.1kWh |  | Today generate energy
4 | 3050 | EactodayL
4 | 3051 | EactotalH | Total generate energy |  |  | 0.1kWh |  | Total generate
4 | 3052 | EactotalL
4 | 3053 | Epv_totalH | PV energy total |  |  | 0.1kWh |  | PV energy
4 | 3054 | Epv_totalL | [5 empty] | total
4 | 3055 | Epv1_todayH | PV1 energy today |  |  | 0.1kWh
4 | 3056 | Epv1_todayL
4 | 3057 | Epv1_totalH | PV1 energy total |  |  | 0.1kWh
4 | 3058 | Epv1_totalL
4 | 3059 | Epv2_todayH | PV2 energy today |  |  | 0.1kWh
4 | 3060 | Epv2_todayL
4 | 3061 | Epv2_totalH | PV2 energy total |  |  | 0.1kWh
4 | 3062 | Epv2_totalL
4 | 3063 | Epv3_todayH | PV3 energy today |  |  | 0.1kWh
4 | 3064 | Epv3_todayL
4 | 3065 | Epv3_totalH | PV3 energy total |  |  | 0.1kWh
4 | 3066 | Epv3_totalL
4 | 3067 | Etouser_todayH | Today energy to user |  |  | 0.1kWh |  | Today energy to user
4 | 3068 | Etouser_todayL
4 | 3069 | Etouser_totalH | Total energy to user |  |  | 0.1kWh |  | Total energy to user
4 | 3070 | Etouser_totalL
4 | 3071 | Etogrid_todayH | Today energy to grid |  |  | 0.1kWh |  | Today energy to grid
4 | 3072 | Etogrid_todayL
4 | 3073 | Etogrid_totalH | Total energy to grid |  |  | 0.1kWh |  | Total energy to grid
4 | 3074 | Etogrid_totalL
4 | 3075 | Eload_todayH | Today energy of user load |  |  | 0.1kWh |  | Today energy of user load
4 | 3076 | Eload_todayL
4 | 3077 | Eload_totalH | Total energy of user load |  |  | 0.1kWh |  | Total energy of user load
4 | 3078 | Eload_totalL
4 | 3079 | Epv4_todayH | PV4 energy today |  |  | 0.1kWh
4 | 3080 | Epv4_todayL
4 | 3081 | Epv4_totalH | PV4 energy total |  |  | 0.1kWh
4 | 3082 | Epv4_totalL
4 | 3083 | Epv_todayH | PV energy today |  |  | 0.1kWh
4 | 3084 | Epv_todayL
4 | 3085 | Reserved
4 | 3086 | DeratingMode | DeratingMode |  |  |  |  | 0:cNOTDerate 1:cPVHighDer ate
4 | 3087 | ISO | PV ISO value |  |  | 1KΩ
4 | 3088 | DCI_R | R DCI Curr |  |  | 0.1mA
4 | 3089 | DCI_S | S DCI Curr |  |  | 0.1mA
4 | 3090 | DCI_T | T DCI Curr |  |  | 0.1mA
4 | 3091 | GFCI | GFCI Curr |  |  | 1mA
4 | 3092 | BusVoltage | total bus voltage |  |  | 0.1V
4 | 3093 | Temp1 | Inverter temperature |  |  | 0.1℃
4 | 3094 | Temp2 | The inside IPM in inverter temperature |  |  | 0.1℃
4 | 3095 | Temp3 | Boost temperature |  |  | 0.1℃
4 | 3096 | Temp4 | Reserved |  |  | 0.1℃
4 | 3097 | Temp5 | Commmunication broad temperature |  |  | 0.1℃
4 | 3098 | PBusVoltage | P Bus inside Voltage |  |  | 0.1V
4 | 3099 | NBusVoltage | N Bus inside Voltage |  |  | 0.1V
4 | 3100 | IPF | Inverter output PF now |  |  |  |  | 0-20000
4 | 3101 | RealOPPercent | Real Output power Percent |  |  | 0.01 |  | 1~100
4 | 3102 | OPFullwattH | Output Maxpower Limited |  |  | 0.1W |  | Output
4 | 3103 | OPFullwattL | [5 empty] | Limited
4 | 3104 | StandbyFlag | Inverter standby flag |  |  |  |  | bitfield
4 | 3105 | FaultMaincode | Inverter fault maincode
4 | 3106 | WarnMaincode | Inverter Warning maincode
4 | 3107 | FaultSubcode | Inverter fault subcode |  |  |  |  | bitfield
4 | 3108 | WarnSubcode | Inverter Warning subcode |  |  |  |  | bitfield
4 | 3111 | uwPresentFFTValue_CHANNEL_A | PresentFFTValue [CHANNEL_A] |  |  |  |  | bitfield
4 | 3112 | bAfciStatus | AFCI Status |  |  |  |  | 0 ： waiting
4 | 3113 | uwStrength_CHANNEL_A | AFCI Strength[CHANNEL_A]
4 | 3114 | uwSelfCheckValue_CHANNEL_A | AFCI SelfCheck[CHANNEL_A]
4 | 3115 | invstartdelaytime | inv start delay time |  |  | 1S |  | inv start delay time
4 | 3116 | Reserved
4 | 3117 | Reserved
4 | 3118 | BDC_OnOffState | BDC connect state |  |  |  |  | 0:No BDC
4 | 3119 | DryContactState | Current status of DryContact |  |  |  |  | Current
4 | 3120 | Reserved
4 | 3121 | PselfH | self-use power |  |  | 0.1W
4 | 3122 | PselfL
4 | 3123 | Esys_todayH | System energy today |  |  | 0.1kwh
4 | 3124 | Esys_todayL
4 | 3125 | Edischr_todayH | Today discharge energy |  |  | 0.1kWh |  | Today discharge energy
4 | 3126 | Edischr_todayL
4 | 3127 | Edischr_totalH | Total discharge energy |  |  | 0.1kWh |  | Total discharge energy
4 | 3128 | Edischr_totalL
4 | 3129 | Echr_todayH | Charge energy today |  |  | 0.1kWh |  | Charge energy today
4 | 3130 | Echr_todayL
4 | 3131 | Echr_totalH | Charge energy total |  |  | 0.1kWh |  | Charge energy total
4 | 3132 | Echr_totalL
4 | 3133 | Eacchr_todayH | Today energy of AC charge |  |  | 0.1kWh |  | Today energy of AC charge
4 | 3134 | Eacchr_todayL
4 | 3135 | Eacchr_totalH | Total energy of AC charge |  |  | 0.1kWh |  | Total energy of AC charge
4 | 3136 | Eacchr_totalL
4 | 3137 | Esys_totalH
4 | 3138 | Esys_totalL | Total energy of system output \ |  |  | 0.1kWh
4 | 3139 | Eself_todayH | Today energy of Self output |  |  | 0.1kWh
4 | 3140 | Eself_todayL
4 | 3141 | Eself_totalH | Total energy of Self output |  |  | 0.1kwh
4 | 3142 | Eself_totalL
4 | 3143 | Reserved
4 | 3144 | Priority | Word Mode |  |  |  |  | 0 LoadFirst 1
4 | 3145 | EPSFac | UPS frequency |  |  | 0.01Hz
4 | 3146 | EPSVac1 | UPS phase R output voltage |  |  | 0.1V
4 | 3147 | EPSIac1 | UPS phase R output current |  |  | 0.1A
4 | 3148 | EPSPac1H | UPS phase R output power |  |  | 0.1VA
4 | 3149 | EPSPac1L
4 | 3150 | EPSVac2 | UPS phase S output voltage |  |  | 0.1V
4 | 3151 | EPSIac2 | UPS phase S output current |  |  | 0.1A
4 | 3152 | EPSPac2H | UPS phase S output power |  |  | 0.1VA
4 | 3153 | EPSPac2L
4 | 3154 | EPSVac3 | UPS phase T output voltage |  |  | 0.1V
4 | 3155 | EPSIac3 | UPS phase T output current |  |  | 0.1A
4 | 3156 | EPSPac3H | UPS phase T output power |  |  | 0.1VA
4 | 3157 | EPSPac3L
4 | 3158 | EPSPacH | UPS output power |  |  | 0.1VA
4 | 3159 | EPSPacL
4 | 3160 | Loadpercent | Load percent of UPS ouput |  |  | 0.001
4 | 3161 | PF | Power factor |  |  | 0.1
4 | 3162 | DCV | DC voltage |  |  | 1mV
4 | 3163 | Reserved
4 | 3164 | NewBdcFlag | Whether to parse BDC data separately |  |  |  |  | 0: Don't need
4 | 3165 | BDCDeratingMode | BDCDeratingMode：
4 | 3166 | SysState_Mode | System work State and mode The upper 8 bits indicate the mode; |  |  |  |  | BDC1
4 | 3167 | FaultCode | Storge device fault code
4 | 3168 | WarnCode | Storge device warning code
4 | 3169 | Vbat | Battery voltage |  |  | 0.01V
4 | 3170 | Ibat | Battery current |  |  | 0.1A
4 | 3171 | SOC | State of charge Capacity |  |  | 0.01
4 | 3172 | Vbus1 | Total BUS voltage |  |  | 0.1V
4 | 3173 | Vbus2 | On the BUS voltage |  |  | 0.1V
4 | 3174 | Ibb | BUCK-BOOST Current |  |  | 0.1A
4 | 3175 | Illc | LLC Current |  |  | 0.1A
4 | 3176 | TempA | Temperture A |  |  | 0.1℃
4 | 3177 | TempB | Temperture B |  |  | 0.1℃
4 | 3178 | PdischrH | Discharge power |  |  | 0.1W
4 | 3179 | PdischrL
4 | 3180 | PchrH | Charge power |  |  | 0.1W
4 | 3181 | PchrL
4 | 3182 | Edischr_totalH | Discharge total energy of storge device |  |  | 0.1kWh
4 | 3183 | Edischr_totalL
4 | 3184 | Echr_totalH | Charge total energy of storge device |  |  | 0.1kWh
4 | 3185 | Echr_totalL
4 | 3186 | Reserved | Reserved
4 | 3187 | BDC1_Flag | BDC mark (charge and discharge, fault alarm code)
4 | 3188 | Vbus2 | Lower BUS voltage |  |  | 0.1V
4 | 3189 | BmsMaxVoltCellNo | BmsMaxVoltCellNo
4 | 3190 | BmsMinVoltCellNo | BmsMinVoltCellNo
4 | 3191 | BmsBatteryAvgTemp | BmsBatteryAvgTemp
4 | 3192 | BmsMaxCellTemp | BmsMaxCellTemp |  |  | 0.1°C
4 | 3193 | BmsBatteryAvgTemp | BmsBatteryAvgTemp |  |  | 0.1°C
4 | 3194 | BmsMaxCellTemp | BmsMaxCellTemp
4 | 3195 | BmsBatteryAvgTemp | BmsBatteryAvgTemp
4 | 3196 | BmsMaxSOC | BmsMaxSOC |  |  | 0.01
4 | 3197 | BmsMinSOC | BmsMinSOC |  |  | 0.01
4 | 3198 | ParallelBatteryNum | ParallelBatteryNum
4 | 3199 | BmsDerateReason | BmsDerateReason
4 | 3200 | BmsGaugeFCCAh | BmsGaugeFCC（Ah）
4 | 3201 | BmsGaugeRMAh | BmsGaugeRM（Ah）
4 | 3202 | BmsError | BMS Protect1
4 | 3203 | BmsWarn | BMSWarn1
4 | 3204 | BmsFault | BMS Fault1
4 | 3205 | BmsFault2 | BMS Fault2
4 | 3206 | Reserved
4 | 3207 | Reserved
4 | 3208 | Reserved
4 | 3209 | Reserved
4 | 3210 | BatIsoStatus | Battery ISO detection status |  |  |  |  | 0：Not
4 | 3211 | BattNeedCharge | battery work request |  | bit0:1： Prohibit chargin g，0：
4 | 3212 | BMS_Status | battery working status | R | 0: dormancy
4 | 3213 | BmsError2 | BMS Protect2 | R |  | 1
4 | 3214 | BmsWarn2 | BMS Warn2 | R |  | 1
4 | 3215 | BMS_SOC | BMS SOC | R |  | 0.01
4 | 3216 | BMS_BatteryVolt | BMS BatteryVolt | R |  | 0.01V
4 | 3217 | BMS_BatteryCurr | BMS BatteryCurr | R |  | 0.01A
4 | 3218 | BMS_BatteryTemp | battery cell maximum temperature | R |  | 0.1℃
4 | 3219 | BMS_MaxCurr | Maximum charging current | R |  | 0.01A
4 | 3220 | BMS_MaxDischrCurr | Maximum discharge current | R |  | 0.01A
4 | 3221 | BMS_CycleCnt | BMSCycleCnt | R |  | 1
4 | 3222 | BMS_SOH | BMS SOH | R |  | 1
4 | 3223 | BMS_ChargeVoltLimit | Battery charging voltage limit value | R |  | 0.01V
4 | 3224 | BMS_DischargeVoltLimit | Battery discharge voltage limit value
4 | 3225 | BmsWarn3 | BMS Warn 3 | R |  | 1
4 | 3226 | BmsError3 | BMS Protect3 | R |  | 1
4 | 3227 | Reserved
4 | 3228 | Reserved
4 | 3229 | Reserved
4 | 3230 | BMSSingleVoltMax | BMS Battery SingleVoltMax | R |  | 0.001V
4 | 3231 | BMSSingleVoltMin | BMS Battery SingleVoltMin | R |  | 0.001V
4 | 3232 | BatLoadVolt | Battery LoadVolt | R |  | 0.01V |  | [0，650.00]
4 | 3234 | Debugdata1 | Debug data1 | R
4 | 3235 | Debugdata2 | Debug data2 | R
4 | 3236 | Debugdata3 | Debug data3 | R
4 | 3237 | Debugdata4 | Debug data4 | R
4 | 3238 | Debugdata5 | Debug data5 | R
4 | 3239 | Debugdata6 | Debug data6 | R
4 | 3240 | Debugdata7 | Debug data7 | R
4 | 3241 | Debugdata8 | Debug data8 | R
4 | 3242 | Debugdata9 | Debug data9 | R
4 | 3243 | Debugdata10 | Debug data10 | R
4 | 3244 | Debugdata10 | Debug data10 | R
4 | 3245 | Debugdata12 | Debug data12 | R
4 | 3246 | Debugdata13 | Debug data13 | R
4 | 3247 | Debugdata14 | Debug data14 | R
4 | 3248 | Debugdata15 | Debug data15 | R
4 | 3249 | Debugdata16 | Debug data16 | R
4 | 3250 | Pex1H | PV inverter 1 output power H | R |  | 0.1W
4 | 3251 | Pex1L | PV inverter 1 output power L | R |  | 0.1W
4 | 3252 | Pex2H | PV inverter 2 output power H | R |  | 0.1W
4 | 3253 | Pex2L | PV inverter 2 output power L | R |  | 0.1W
4 | 3254 | Eex1TodayH | PV inverter 1 energy Today H | R |  | 0.1kWh
4 | 3255 | Eex1TodayL | PV inverter 1 energy Today L | R |  | 0.1kWh
4 | 3256 | Eex2TodayH | PV inverter 2 energy Today H | R |  | 0.1kWh
4 | 3257 | Eex2TodayL | PV inverter 2 energy Today L | R |  | 0.1kWh
4 | 3258 | Eex1TotalH | PV inverter 1 energy Total H | R |  | 0.1kWh
4 | 3259 | Eex1TotalL | PV inverter 1 energy Total L | R |  | 0.1kWh
4 | 3260 | Eex2TotalH | PV inverter 2 energy Total H | R |  | 0.1kWh
4 | 3261 | Eex2TotalL | PV inverter 2 energy Total L | R |  | 0.1kWh
4 | 3262 | uwBatNo | battery pack number | R
4 | 3263 | BatSerialNum1 | Battery pack serial numberSN[0]SN[1] | R
4 | 3264 | BatSerialNum2 | Battery pack serial numberSN[2]SN[3] | R
4 | 3265 | BatSerialNum3 | Battery pack serial numberSN[4]SN[5] | R
4 | 3266 | BatSerialNum4 | Battery pack serial numberSN[6]SN[7] | R
4 | 3267 | BatSerialNum5 | Battery pack serial numberSN[8]SN[9] | R
4 | 3268 | BatSerialNum6 | Battery pack serial numberSN[10]SN[11] | R
4 | 3269 | BatSerialNum7 | Battery pack serial numberSN[12]SN[13] | R
4 | 3270 | BatSerialNum8 | Battery pack serial numberSN[14]SN[15] | R
4 | 3280 | bClrTodayDataFlag | Clear day data flag | R
4 | '3271-3279 | Reserve | Reserve
4 | '4000-4107 | BDCBlock1 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4 | '4108-4215 | BDCBlock2 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4 | '4864-4971 | BDCBlock3 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4 | '4972-5079 | BDCBlock4 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).