## Sheet1
Growatt Inverter Modbus RTU Protocol
V1.24
Make： weiwei.shi
Check： qixing.ren
Authorize： liangcai.wu
Effective date：
Change Record
Index | Version | Change Content | Make | Make date
1 | 0 | First Republic | Weiwei.shi | 2020.4.28
Instruction：Register range for various types of inverter
TL-X/TL-XH/TL-XHUS（MINType）：03registerrange：0~124,3000~3124，
3125~3249(TL-XHUS)；04 register range：3000~3124,3125~3249， 3250~3374（TL-XH）
TL3-X(MAX、MID、MAC Type)：03 register range：0~124,125~249； 04 register range：0~124,125~249
MAX1500V、MAX-XLV:03registerrange：0~124,125~249；04register range：0~124,125~249,875~999
MODTL3-XH:03registerrange：0~124,3000~3124；04registerrange：
3000~3124,3125~3249
Storage(MIXType)：03registerrange：0~124,1000~1124；04register range：0~124,1000~1124
Storage(SPAType)：03registerrange：0~124,1000~1124；04register range：1000~1124,2000~2124，1125~1249
Storage(SPHType)：03registerrange：0~124,1000~1124；04register range：0~124,1000~1124，1125~1249
catalog
1 Data format | 5
2 Command Format | 5
3 Device Message Transmission Mode / Framing | 8
4 Register map | 9
4.1 Holding Reg | 9
4.2 Input Reg | 47
5 Set address | 84
6 Notice | 84
1 Data format
Valid slave device addresses are in the range of 0 – 254 decimal.
The individual slave devices are assigned addresses in the range of 1 – 254.
0 is the broadcast address
It is 16bits (two bytes) unsigned integer for each holding and input register;
2 Command Format
Function 3 Read holding register
Response Error:
11 0x80¦0x03 ErrornumCRC(Errornum as a byte)
Function 4 Read input | register
Response Error:
| 11 0x80¦0x04 ErrornumCRC | (Errornum as a byte)
Function 6 Preset single register
Response Error:
| 11 0x80¦0x06 ErrornumCRC | (Errornum as a byte)
Function 16 Preset multiple register
Response Error:
| 11 0x80¦0x10 ErrornumCRC | (Errornum as a byte)
3 Device Message Transmission Mode / Framing
RTU Mode
When controllers are setup to communicate on a Modbus network using RTU (Remote Terminal Unit) mode, each 8–bit byte in a message contains two 4–bit hexadecimal characters. Each message must be transmitted in a continuous stream.
The format for each byte in RTU mode is:
Coding System: 8–bit binary, hexadecimal 0–9, A–F
Two hexadecimal characters contained in each
8–bit field of the message
Bits per Byte:
1 start bit
8 data bits, least significant bit sent first
None parity
1 stop bit
Error Check Field: Cyclical Redundancy Check (CRC)
The baud rate of the transmission is:
Default Baud Rate: 9600 bps
Can be set through hold register 22
Minimum CMD period (RS485 Time out): 850ms.
Wait for minimum850ms to send a new CMD after last CMD. Suggestion is 1s;
Maximum Data Length Define:
Maximum read data length is 125 words in read command;
Maximum update data length is 125 words in preset command;
Note:
Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing other registers;
4 Register map
It is 16bits (two bytes) unsigned integer for each holding and input register;
4.1 Holding Reg
Registe r NO. | Variable | Description | Write or not | Value | Unit | Initial value | Note
Name
First group
0 | OnOff | Remote On/Off . | W | 0、1、2、 |  | 1 | The inverter can be switched on and off, and the BDC can be switched on and off for the batt ready function.
|  | On（1）；Off（0）Inverter |  | 3
On（3）；Off（2）BDC
1 | SaftyFuncEn | Bit0: SPI enable | W | 0:00 |  |  | SPI: system | protection
|  | Bit1: AutoTestStart |  | disable 1: enable |  |  | interface
|  | Bit2: LVFRT enable |  |  |  |  | Bit0~3:for CEI0-21
|  | Bit3:FreqDerating |  |  |  |  | Bit4~6:for SAA
Enable
Bit4: Softstart enable
Bit5: DRMS enable
Bit6:PowerVoltFunc
Enable
Bit7: HVFRT enable
Bit8:ROCOF enable Bit9: Recover
FreqDeratingMode
Enable
Bit10：Split phase enable
Bit10~15:预留
2 | PF CMD | Set Holding register3,4,5,99 CMD will be memory or not(1/0), if not, these settings are the initial value. | W | 0or1 |  | 0 | Means these settings will be acting or not when next power on
memory
state
3 | Active P | Inverter Max output active power percent | W | 0-100 or | % | 255 | 255: power is not be limited
| Rate |  |  | 255
4 | Reactive P | Inverter max output reactive power percent | W | -100-100 or 255 |  | % | 255 | 255: power is not be limited
Rate
5 | Power factor | Inverter output power factor’s 10000 times | W | 0-20000, |  |  | 0
0-10000
is
underexci ted, other
is
overexcit ed
6 | Pmax H | Normal power (high) |  |  |  | 0.1VA
7 | Pmax L | Normal power (low) |  |  |  | 0.1VA
8 | Vnormal | Normal work PV voltage |  |  |  | 0.1V
9 | Fw version H | Firmware version |  |  |  | ASCII
(high)
10 | Fw version | Firmware version
| M | (middle)
11 | Fw version L | Firmware version (low)
12 | Fw version2 | Control Firmware version (high) |  |  |  | ASCII
H
13 | Fw version2 | Control Firmware version (middle)
M
14 | Fw version2 | Control Firmware version (low)
L
15 | LCD language | LCD language | W | 0-5 |  |  |  | 0: Italian;
1: English;
2: German;
3: Spanish;
4: French;
5: Chinese;
6：Polish
7：Portugues
8：Hungary
16 | CountrySele cted | Country Selected or not | W | 0: need
to select;
1: have
selected
17 | Vpv start | Input start voltage | W |  |  | 0.1V
18 | Time start | Start time | W |  |  | 1s
19 | RestartDelay | Restart Delay Time after fault back; | W |  |  | 1s
Time
20 | wPowerStart | Power start slope | W | 1-1000 | 0.1%
Slope
21 | wPowerRest artSlopeEE | Power restart slope | W | 1-1000 | 0.1%
22 | wSelectBaud rate | Select communicationbaudrat e | W | 0-1 |  | 0
0: 9600bps
1:38400bps
23 | Serial NO | Serial number 1-2 |  |  | ASCII
24 | Serial NO | Serial number 3-4
25 | Serial NO | Serial number 5-6
26 | Serial NO | Serial number 7-8
27 | Serial NO | Serial number 9-10
28 | Module H | Inverter Module (high) |  | &*5
29 | Module L | Inverter Module (low) |  | &*5
30 | Com | Communicate address | W | 1-254 |  | 1
Address
31 | FlashStart | Update firmware | W | 1
32 | Reset User | Reset User Information | W | 0x0001
Info
33 | Reset to | Reset to factory | W | 0x0001
factory
34 | Manufacture r Info 8 | Manufacturer information (high) |  |  | ASCII
35 | Manufacture r Info 7 | Manufacturer information (middle)
36 | Manufacture r Info 6 | Manufacturer information (low)
37 | Manufacture r Info 5 | Manufacturer information (high)
38 | Manufacture r Info 4 | Manufacturer information (middle)
39 | Manufacture r Info3 | Manufacturer information (low)
40 | Manufacture r Info 2 | Manufacturer information (low)
41 | Manufacture r Info 1 | Manufacturer information (high)
42 | bfailsafeEn; | G100 fail safe | W | Enable:1 |  |  | English G100 fail safe set
Disable:0
43 | DTC | Device Type Code |  | &*6
44 | TP | Input tracker num and output phase num |  |  |  | Eg:0x020
3 is two MPPT and 3ph
output
45 | Sys Year | System time-year |  |  | W | Year offset is 0 |  |  | Local time
46 | Sys Month | System time- Month |  |  | W
47 | Sys Day | System time- Day |  |  | W
48 | Sys Hour | System time- Hour |  |  | W
49 | Sys Min | System time- Min |  |  | W
50 | Sys Sec | System time- Second |  |  | W
51 | Sys Weekly | System Weekly |  |  | W | 0-6
52 | Vac low | Grid voltage low limit protect |  |  | W |  | 0.1V
53 | Vac high | Grid voltage high limit protect |  |  | W |  | 0.1V
54 | Fac low | Grid frequency low limit protect |  |  | W |  | 0.01
Hz
55 | Fac high | Grid high |  |  | W |  | 0.01
|  | frequencylimit protect |  |  |  |  | Hz
56 | Vac low 2 | Grid voltage low limit protect 2 |  |  | W |  | 0.1V
57 | Vac high 2 | Grid voltage high limit protect 2 |  |  | W |  | 0.1V
58 | Fac low 2 | Grid frequency low limit protect 2 |  |  | W |  | 0.01
Hz
59 | Fac high 2 | Grid high frequency limit protect 2 |  |  | W |  | 0.01
Hz
60 | Vac low 3 | Grid voltage protect 3 | low | limit | W |  | 0.1V
61 | Vac high 3 | Grid voltage protect 3 | high | limit | W |  | 0.1V
62 | Fac low 3 | Grid frequency limit protect 3 |  | low | W |  | 0.01Hz
63 | Fac high 3 | Grid frequency limit protect 3 |  | high | W |  | 0.01Hz
64 | Vac low C | Grid low voltage limit connect to Grid |  |  | W |  | 0.1V
65 | Vac high C | Grid high voltage limit connect to Grid |  |  | W |  | 0.1V
66 | Fac low C | Grid low frequency |  |  | W |  | 0.01
|  |  | limit connect to Grid |  |  |  |  | Hz
67 | Fac high C |  | Grid high frequency limit connect to Grid |  |  | W |  | 0.01
Hz
68 | Vac time | low1 | Grid voltage low protect time 1 |  | limit | W |  | Cycle
69 | Vac time | high1 | Grid voltage protect time | high | limit | W |  | Cycle
1
70 | Vac time | low2 | Grid voltage protect time | low | limit | W |  | Cycle
2
71 | Vac time | high2 | Grid voltage protect time | high | limit | W |  | Cycle
2
72 | Fac time | low1 | Grid frequency limit protect time |  | low | W |  | Cycle
1
73 | Fac time | high1 | Grid frequency limit protect time |  | high | W |  | Cycle
1
74 | Fac time | low2 | Grid frequency limit protect time |  | low | W |  | Cycle
2
75 | Fac time | high2 | Grid frequency limit protect time |  | high | W |  | Cycle
2
76 | Vac time | low3 | Grid voltage protect time | low | limit | W |  | Cycle
3
77 | Vac time | high3 | Grid voltage protect time | high | limit | W |  | Cycle
3
78 | Fac time | low3 | Grid frequency limit protect time |  | low | W |  | Cycle
3
79 | Fac time | high3 | Grid frequency limit protect time |  | high | W |  | Cycle
3
80 | U10min |  | Volt protection for 10 min |  |  | W |  | 0.1V | 1.1Vn
81 | PV Voltage |  | PV Voltage High Fault |  |  | W |  | 0.1V
High Fault
82 | FW Build No. |  | Model letter version number (TJ) |  |  |  |  | ASCII
5
83 | FW Build No. |  | Model letter version number (AA) |  |  |  |  | ASCII
4
84 | FW Build No. |  | DSP1 FW Build No. |  |  |  |  | ASCII
3
85 | FW Build No. |  | DSP2/M0 FW Build No. |  |  |  |  | ASCII
2
86 | FW Build No. |  | CPLD/AFCI FW Build No. |  |  |  |  | ASCII
1
87 | FW Build No. |  | M3 FW Build No. |  |  |  |  | ASCII
0
88 | ModbusVers ion | Modbus Version |  | Eg：207 is | Int(16 bits)
V2.07
89 | PFModel | Set PF function Model | W
0: PF=1
1: PF by set
2: default PF line
3: User PF line
4: UnderExcited (Inda)
Reactive Power
5: OverExcited(Capa)
Reactive Power
6：Q(v)model
7：Direct Control mode
8. Static capacitive QV mode
9. Static inductive QV
mode
90 | GPRS IP Flag | Bit0-3:read:1;Set GPRS | W | Bit0-3:ab
|  | IP Successed |  | out GPRS
|  | Write:2;Read GPRS IP |  | IP SET
|  | Successed |  | Bit4-7:ab out GRPRS
|  | Bit4-7:GPRS status |  | Status
91 | FreqDerateS tart | Frequency derating start point | W |  | 0.01H
Z
92 | FLrate | Frequency – load limit rate | W | 0-100 | 10tim es
93 | V1S | CEI021 V1S Q(v) | W | V1S<V2S | 0.1V
94 | V2S | CEI021 V2S Q(v) | W |  | 0.1V
95 | V1L | CEI021 V1L Q(v) | W | V1L<V1S | 0.1V
96 | V2L | CEI021 V2L Q(v) | W | V2L<V1L | 0.1V
97 | Qlockinpow er | Q(v) lock in active power of CEI021 | W | 0-100 | Percen
t
98 | QlockOutpo wer | Q(v) lock Out active power of CEI021 | W | 0-100 | Percen
t
99 | LIGridV | Lock in gird volt of | W | nVn | 0.1V
CEI021 PF line
100 | LOGridV | Lock out gird volt of | W | nVn | 0.1V
CEI021 PF line
101 | PFAdj1 | PF adjust value 1 |  | 4096 is 1
102 | PFAdj2 | PF adjust value 2 |  | 4096 is 1
103 | PFAdj3 | PF adjust value 3 |  | 4096 is 1
104 | PFAdj4 | PF adjust value 4 |  | 4096 is 1
105 | PFAdj5 | PF adjust value 5 |  | 4096 is 1
106 | PFAdj6 | PF adjust value 6 |  | 4096 is 1
107 | QVRPDelayTi meEE | QV Reactive Power | W | 0-30 | 1S | 3S
delaytime
108 | OverFDeratD elayTimeEE | Overfrequency derati ngdelaytime | W | 0-20 | 50ms | 0
109 | QpercentMa x | Qmax for Q(V) curve | W | 0-1000 | 0.1%
110 | PFLineP1_LP | PF limit line point 1 load percent | W | 0-255 | percen |  | 255 means no this point
t
111 | PFLineP1_PF | PF limit line point 1 power factor | W | 0-20000
112 | PFLineP2_LP | PF limit line point 2 load percent | W | 0-255 | percen |  | 255 means no this point
t
113 | PFLineP2_PF | PF limit line point | W | 0-20000
2power factor
114 | PFLineP3_LP | PF limit line point 3 load percent | W | 0-255 | percen |  | 255 means no this point
t
115 | PFLineP3_PF | PF limit line point 3 power factor | W | 0-20000
116 | PFLineP4_LP | PF limit line point 4 load percent | W | 0-255 | percen |  | 255 means no this point
t
117 | PFLineP4_PF | PF limit line point 4 power factor | W | 0-20000
118 | Module 4 | Inverter Module (4) |  | &*11 |  |  | SxxBxx
119 | Module 3 | Inverter Module (3) |  | &*11 |  |  | DxxTxx
120 | Module 2 | Inverter Module (2) |  | &*11 |  |  | PxxUxx
121 | Module 1 | Inverter Module (1) |  | &*11 |  |  | Mxxxx Power
122 | ExportLimit_ | ExportLimit_En/dis | R/W | 1/0 |  |  | ExportLimit enable,
| En/dis | [5 empty] | 0: Disable exportLimit;
1: Enable 485 exportLimit;
2: Enable 232 exportLimit;
3: Enable CT exportLimit;
123 | ExportLimitP owerRate | ExportLimitPowerRate | R/W | -1000~+1 | 0.1% |  | ExportLimit PowerRate
0
124 | TrakerModel | Traker Model | W | 0,1,2 |  |  | 0:Independent
1:DC Source
2:Parallel
Second group
125 | INV Type-1 | Inverter type-1 | R |  | ASCII |  | Reserved
126 | INV Type-2 | Inverter type-2 | R |  | ASCII
127 | INV Type-3 | Inverter type-3 | R |  | ASCII
128 | INV Type-4 | Inverter type-4 | R |  | ASCII
129 | INV Type-5 | Inverter type-5 | R |  | ASCII
130 | INV Type-6 | Inverter type-6 | R |  | ASCII
131 | INV Type-7 | Inverter type-7 | R |  | ASCII
132 | INV Type-8 | Inverter type-8 | R |  | ASCII
133 | BLVersion1 | Boot loader version1 | R |  |  |  | Reserved
134 | BLVersion2 | Boot loader version2 | R |  |  |  | Reserved
135 | BLVersion3 | Boot loader version3 | R |  |  |  | Reserved
136 | BLVersion4 | Boot loader version4 | R |  |  |  | Reserved
137 | Reactive P | Reactive PowerH | R/W |  | 0.1var
ValueH
138 | Reactive P | Reactive PowerL | R/W |  | 0.1var
ValueL
139 | ReactiveOut putPriorityE nable | ReactiveOutput Priority | R/W |  | 0/1 |  | 0：disable
|  | Enable |  |  |  |  | 1：enable
140 | Reactive P | Reactive Power Ratio | R/W |  | 0.1
Value(Ratio)
……
141 | SvgFunction | Svg enable on night | R/W |  | 0/1 |  | 0：disable
| Enable | [5 empty] | 1：enable
142 | uwUnderFU ploadPoint | UnderF Upload Point | R/W |  | 0.01H
Z
143 | uwOFDerate RecoverPoin | OFDerate RecoverPoint | R/W |  | 0.01H
| t |  |  |  | Z
144 | uwOFDerate RecoverDela yTime | OFDerate | R/W | 0-30000 | 50ms
RecoverDelayTime
145 | ZeroCurrent | ZeroCurrent Enable | R/W | 0-1
Enable
146 | uwZeroCurre ntStaticlowV | ZeroCurrent | R/W | 46-230V | 0.1V | 115V
| olt | StaticlowVolt
147 | uwZeroCurre ntStaticHigh | ZeroCurrent | R/W | 230-276V | 0.1V | 276V
| Volt | StaticHighVolt
148 | uwHVoltDer | HVoltDerate HighPoint | R/W | 0-1000V | 0.1V
ateHighPoint
149 | uwHVoltDer ateLowPoint | HVoltDerate LowPoint | R/W | 0-1000V | 0.1V
150 | uwQVPower | QVPower Stable Time | R/W | 0-60S | 0.1S
StableTime
151 | uwUnderFU ploadStopPo | UnderF Upload | R/W |  | 0.01H
| int | StopPoint |  |  | Z
152 | fUnderFreqP oint | Underfrequency load | R/W | 46.00-50. | 0.01Hz | 49.8 | CEI
|  | start point |  | 0
153 | fUnderFreqE ndPoint | Underfrequency down load end point | R/W | 46.00-50. | 0.01Hz | 49.1 | CEI
0
154 | fOverFreqPo | Over frequency loading start point | R/W | 50.00-52. | 0.01Hz | 50.2 | CEI
| int |  |  | 0
155 | fOverFreqEn dPoint | Over frequency loading end point | R/W | 50.00-52. | 0.01Hz | 51.5 | CEI
0
156 | fUnderVoltP oint | Undervoltage load | R/W | 160-300 | 0.1V | 220 | CEI
shedding start point
157 | fUnderVoltE ndPoint | Undervoltage derating end point | R/W | 160-300 | 0.1V | 207 | CEI
158 | fOverVoltPoi nt | Overvoltage loading | R/W | 160-300 | 0.1V | 230 | CEI
start point
159 | fOverVoltEn dPoint | Overvoltage loading end point | R/W | 160-300 | 0.1V | 245 | CEI
160 | uwNominal | NominalGridVolt Select | R/W | 0~3 |  |  | UL
GridVolt
161 | uwGridWatt | GridWatt DelayTime | R/W | 0~3000 | 20ms |  | UL
Delay
162 | uwReconnec | Reconnect StartSlope | R/W | 1~1000 | 0.1 |  | UL
tStartSlope
163 | uwLFRTEE | LFRT1 Freq | R/W | 5500~650 | 0.01Hz |  | UL
0
164 | uwLFRTTime | LFRT1 Time | R/W |  | 20ms |  | UL
EE
165 | uwLFRT2EE | LFRT2 Freq | R/W | 5500~650 | 0.01Hz |  | UL
0
166 | uwLFRTTime | LFRT2 Time | R/W |  | 20ms |  | UL
2EE
167 | uwHFRTEE | HFRT1 Freq | R/W | 5500~650 | 0.01Hz |  | UL
0
168 | uwHFRTTim eEE | HFRT1 Time | R/W |  | 20ms |  | UL
169 | uwHFRT2EE | HFRT2 Freq | R/W | 5500~650 | 0.01Hz |  | UL
0
170 | uwHFRTTim e2EE | HFRT2 Time | R/W |  | 20ms |  | UL
171 | uwHVRTEE | HVRT1 Volt | R/W |  | 0.001 |  | UL
Un
172 | uwHVRTTim eEE | HVRT1 Time | R/W |  | 20ms |  | UL
173 | uwHVRT2EE | HVRT2 Volt | R/W |  | 0.001 |  | UL
Un
174 | uwHVRTTim e2EE | HVRT2 Time | R/W |  | 0.001 |  | UL
Un
175 | uwUnderFU | UnderF | R/W | 0-2s | 50ms | 0s | 50549
| ploadDelayTi | UploadDelayTime
me
176 | uwUnderFU ploadRateEE | UnderF UploadRate | R/W |  |  |  | 50549
177 | uwGridResta rt_H_Freq | GridRestart HighFreq | R/W |  | 0.01Hz |  | 50549
178 | OverFDeratR esponseTim e | OverFDerat | W/R | 0-500
ResponseTime
179 | UnderFUplo adResponse | UnderFUpload | W/R | 0-500
| Time | ResponseTime
Intelligent control reads relevant data, used to identify the logo 180-200
180 | MeterLink | Whether to elect the meter | R/W |  |  |  | 0: Missed, 1: Received
181 | OPT Number | Number of connection optimizers | R/W | 0-64 |  |  | The total number of optimizers connected to the inverter
182 | OPT | Optimizer configuration completion flag | R/W |  |  |  | 0x00:Not configured success
| ConfigOK | [5 empty] | 0x01:Configuration is complete
Flag
183 | PvStrScan | String Num | R/W | 0、8、16、 |  |  | 0：Not support
|  |  |  | 32 |  |  | Other：PvString Num
184 | BDCLinkNum | BDC parallel Num | R/W |  |  |  | The number of BDCs connected to the current machine Default is 0
185 | PackNum |  | Number of battery modules | R |  |  |  | Total number of battery modules currently associated with all BDCs
186 | Reserved
187 | VPP function enable status |  | VPP function enable status | R |  |  |  | 0：Disable
1：Enable
188 | dataLog Connect |  | dataLog Connect |  |  |  |  | 0：connection succeeded
| Server status |  | Server status |  |  |  |  | 1：Connection failed
……
200 | Reserved | [6 empty] | Reserved
201 | PID Working |  | PID Operating mode | W | 0:00
| Model |  |  |  | automati c 1:
continuo us 2: All night
202 | PID On/Off |  | PID Break control | W | 0:On 1:Off
Ctrl
203 | PID | Volt | PID Output voltage | W | 300~1000 | V
| Option |  | option
…… | [7 empty] | Reserved
209 | New | NO | Serial number 1-2 |  |  | ASCII
Serial
210 | New | NO | Serial number 3-4 |  |  | ASCII
Serial
211 | New | NO | Serial number 5-6 |  |  | ASCII
Serial
212 | New | NO | Serial number 7-8 |  |  | ASCII
Serial
213 | New | NO | Serial number 9-10 |  |  | ASCII
Serial
214 | New | NO | Serial number 11-12 |  |  | ASCII
Serial
215 | New | NO | Serial number 13-14 |  |  | ASCII
Serial
216 | New | NO | Serial number 15-16 |  |  | ASCII
Serial
217 | New | NO | Serial number 17-18 |  |  | ASCII
Serial
218 | New | NO | Serial number 19-20 |  |  | ASCII
Serial
219 | New | NO | Serial number 21-22 |  |  | ASCII
Serial
220 | New | NO | Serial number 23-24 |  |  | ASCII
Serial
221 | New | NO | Serial number 25-26 |  |  | ASCII
Serial
222 | New | NO | Serial number 27-28 |  |  | ASCII
Serial
223 | New | NO | Serial number 29-30 |  |  | ASCII
Serial
…… | [7 empty] | Reserved
229 | EnergyAdjus |  | Power generation incremental calibration coefficient | W/R |  | 0.1% |  | 1-1000,(Percent ratio)
t
230~249 for growatt debug setting
230 | IslandDisabl e |  | Island Disable or not. | W | 0,1 |  | 0
1:disable 0:Enable
231 | FanCheck |  | Start Fan Check | W | 1
232 | EnableNLine |  | Enable N Line of grid | W | 1 |  | 0
233 | wCheckHard ware |  | wCheckHardware
Bit0: GFCIBreak;
Bit1:SPSDamage Bit8:EepromReadWarni ng
Bit9:EEWriteWarning
……
234 | wCheckHard ware2 | [6 empty] | reserved
235 | ubNToGNDD |  | Dis/enable N to GND | W | 1:enable |  | 1
| etect |  | detect function |  | 0:disable
236 | NonStdVacE nable |  | Enable/Disable | W | 0-2 |  | 0 | 0:Disable;
|  |  | Nonstandard |  |  |  |  | 1:Enable Voltgrade1
|  |  | Grid voltage range |  |  |  |  | 2:Enable Voltgrade2
237 | uwEnableSp ecSet |  | Disablse/enable appointed spec setting | W | 1:enable | Binary | 0x000 | Bit 0: Hungary
[5 empty] | 0:disable |  | 0
238 | Fast MPPT | About Fast mppt |  | 0,1,2 |  | 0 | Reserved
enable
239 | / | / | / | / |  | / | Reserved
240 | Check Step |  | W
241 | INV-Lng | Inverter Longitude | W |  |  |  | Longitude
242 | INV-Lat | Inverter Latitude | W |  |  |  | Latitude
…… | [6 empty] | Reserved
303 | [6 empty] | Reserved
304 | uwAntiBackf lowFailPowe rLimitEE | Anti-backflow failure power percentage | R/W | 0-1000 | 0.1% |  | Anti-backflow failure default setting power percentage
305 | Qloadspeed | Reactive loading speed | R/W | 0-100 | 1% |  | Reactive power adjustment speed setting item, n%Pn/s, 0 means that the loading speed is not enabled, that is, it is directly loaded to the set value
306 | bParallelAnti BackflowEna ble | ParallelAnti-Backflow | R/W | 0-1 |  |  | Parallel anti-Backflow open enable bit
|  | Enable |  |  |  |  | 1: enable 0:disable
307 | uwAntiBackf lowFailureRe sponseTime | AntiBackflowFailure | R/W | 1132254 | 1s |  | AntiBackflow Failure
|  | ResponseTime |  |  |  |  | Response Time
308 | uwParallelAn tiBackflowPo werLimitEE | ParallelAntiBackflowPo wer | R/W | 0-1000 | 0.1% |  | Parallel AntiBackflow Power
limit value setting
309 | bISOCheckC | ISO detection | R/W | 0-1 | 1 |  | ISO detection command
| md | command
310 | bGPRSStatus | GPRS Status | R/W | 0-255 | 1
1: module not working
2: no sim card
3: No internet
4. TCP not connecting to server
5. TCP connection
succeeded
311 | uwQmax_In | The inductive Qmax of the Q(V) curve | R/W | 0-1000 | 0.1%
ductive
312 | uwQmax_Ca | The Capactive Qmax of | R/W | 0-1000 | 0.1%
| pactive | the Q(V) curve
313 | uwReactiveP owerAdjustF ailureRespon seTime | ReactivePowerAdjust | R/W | 0-5000 | S
Failur ResponseTime
314 | bSuperAntiB ackflowEnab | SuperAntiBackflow | R/W |  |  |  | 0：disable，1：enable
| le | Enable
315 | uwReactiveP owerStableT ime | ReactivePowerStableTi | R/W | 0-200 | S
me
316 | uwQpStable | QpStableTime | R/W | 0-200 | S
Time
317 | uwPuDerate | PuDerateTime | R/W | 0-200 | S
Time
318 | uwQVModel | QV mode Q2 set point reactive power | R/W | 0-2000 | 0.1% |  | Capacitive 30%
| Q2Point | percentage |  |  |  |  | （ The corresponding setting is 700)； Inductive 30%
(The corresponding setting is
319 | uwQVModel | QV mode Q3 set point reactive power | R/W | 0-2000 | 0.1% |  | 1300)； used for IEE1547
| Q3Point | percentage
320 | bVrefModel | VrefModelEnable | R/W | 0 ： Vref mode for QV curve is not active |  |  | When the Vref mode is not activated, the V1~V4 and Q1~Q4 upper computer of the QV curve can be adjusted;
| Enable |  |  | 1 ： Vref mode for QV curve |  |  | When Vref mode is activated, V1~V4 of the QV curve are determined with Vref and cannot be changed, and Q1~Q4 can be modified by the host computer .used for IEE1547
is active
321 | uwVrefMod elFilterTime | VrefModelFilterTime | R/W | 0-5000 | S |  | Activate Vref mode, the output filter value is equal to
Vref with in the set time
.used for IEE1547
322 | uwUserQPM odeP1Krate | Active power P1 set point percentage for | R/W | 0-1000 | 0.1% |  | used for IEE1547
QP mode
323 | uwUserQPM odeP2Krate | Active power P2 point percentage | set for | R/W | 0-1000 | 0.1% |  | used for IEE1547
QP mode
324 | uwUserQPM odeP3Krate | Active power P3 point percentage | set for | R/W | 0-1000 | 0.1% |  | used for IEE1547
QP mode
325 | uwUserQPM odeQ1Krate | Reactive power Q1 set point percentage for |  | R/W | -1010 | 0.1% |  | -1000~1000：Inductive（100%
|  | QP mode |  |  | 0 |  |  | ~ Capacitive（100%）
326 | uwUserQPM odeQ2Krate | Reactive power Q2 set point percentage for |  | R/W | -1010 | 0.1% |  | -1000~1000：Inductive（100%
|  | QP mode |  |  | 0 |  |  | ~ Capacitive（100%）
327 | uwUserQPM odeQ3Krate | Reactive power Q3 set point percentage for |  | R/W | -1010 | 0.1% |  | -1000~1000：Inductive（100%
|  | QP mode |  |  | 0 |  |  | ~ Capacitive（100%）
328 | uwAcVoltHig hDeratPowe | AcVoltHighDeratPower |  | R/W | 0-1000 | 0.1%
| rLimit | Limit
329 | BackflowSin gleCtrl | BackflowSingleCtrl |  | R/W | 0: disable
1: enable
330 | bAntiBackflo wProtectMo de | AntiBackflowProtectM ode |  | R/W | 0-3 |  |  | Used for Australian
331 | uwUnderFU ploadZeroPo werPoint | UnderfreqUploadZeroP owerPoint |  | W |  | 0.01H
Z
332 | FreqDerateZ eroPowerPoi nt | FreqDerateZeroPowerP oint |  | W |  | 0.01H
Z
333 | bFreqDerati ngStopMode | FreqDeratingStopMode |  | R/W | 0-1
| Enable | Enable
334 | bFreqIncreas ingEnable | FreqIncreasingEnable |  | R/W | 0-1
335 | uwFreqIncre asingRecove rTime | FreqIncreasingRecover |  | R/W |  | 50ms
Time
336 | uwFreqIncre asingEndLow | FreqIncreasingEndLow |  | R/W |  | 0.01H
|  | Point |  |  |  | Z
）
）
）
Point
337 | bFreqIncreas ingStopMod eEnable | FreqIncreasingStopMo deEnable |  | R/W | 0-1
338 | uwUserQpC hrP1Krate | User QP charge P1 percentage | function, set point | R/W | 0-1000 | 0.1%
339 | uwUserQpC hrP2Krate | User QP charge P2 percentage | function, set point | R/W | 0-1000 | 0.1%
340 | uwUserQpC hrP3Krate | User QP charge P3 percentage | function, set point | R/W | 0-1000 | 0.1%
341 | wUserQpChr | User QP | function, set point | R/W | -1010 | 0.1% |  | -1000~1000：Inductive（100%
| Q1Krate | charge Q1 |  |  | 0 |  |  | ~ Capacitive（100%）
percentage
342 | wUserQpChr | User QP | function, set point | R/W | -1010 | 0.1% |  | -1000~1000：Inductive（100%
| Q2Krate | charge Q2 |  |  | 0 |  |  | ~ Capacitive（100%）
percentage
343 | wUserQpChr | User QP | function, set point | R/W | -1010 | 0.1% |  | -1000~1000：Inductive（100%
| Q3Krate | charge Q3 |  |  | 0 |  |  | ~ Capacitive（100%）
percentage
344 | uwFreqDerat ingRecoverL owPoint | FreqDeratingRecoverLo wPoint |  | R/W |  | 0.01H
Z
345 | uwFreqIncre asingRecove rHighPoint | FreqIncreasingRecover |  | R/W |  | 0.01H
|  | HighPoint |  |  |  | Z
…….
532 | TurnOffUnlo adSpeed | TurnOffUnloadSpeed |  | W/R | 0-1000 |  | 0.1% | 0 means not enabled, that is, the function is not enabled; 1-1000 means n%Pn/min
533 | LimitDevice | Anti-backflow equipment selection |  | W/R | 0-3 |  |  | 1：Meter
3:CT
other meaningless
534 | PowerSetOn DCSourceMo de | Power settings in dc source mode |  | W/R | 0-90000 |  |  | The unit is W
535 | OUFreqGrad e1En | Over-under-frequency |  | W/R | 0-1 |  |  | 0:disable
|  | Grade1Enable, | [5 empty] | 1:enable
currently only used by
）
）
）
CEI0-21
536 | Country Set | Country settings under the same safety regulations | W/R | 0-200 |  |  | For mobile APP use only
538 | InterlockEna ble | Three-machine communication | W/R | 0-2 |  |  | 0：disable
|  | Interlock function |  |  |  |  | 1: Slave Enable
|  | mode |  |  |  |  | 2. host enable
539 | OvTemperDe | Over temperature derate point | W/R
ratePoint
540 | SafetySetPas sword | Switch between different safety regulations to set the | W/R
password
541 | AFCI Onoff | AFCI Onoff | W/R | 0xA0/0xA |  |  | 0xA0：AFCI off
|  |  |  | 5 |  |  | 0xA5：AFCI on
542 | AfciSelfChec k | AfciSelfCheck | W/R |  |  |  | 0：No self check
1: self check
543 | AfciReset | AfciReset | W/R |  |  |  | 0：Not Reset
1: Reset
544 | AFCIValue1 | AFCIThresholdValue | W/R | 0-65000
（low）
545 | AFCIValue2 | AFCIThresholdValue | W/R | 0-65000
（middle）
546 | AFCIValue3 | AFCIThresholdValue | W/R | 0-65000
（High）
547 | OverThresho ldValueMaxC nt | OverThresholdValueMa xCnt | W/R | 0-255
548 | AFCIScanTyp eEnable | AFCI curve scan type | W/R | 1~4 |  |  | 1：A road strength
2：A road FFT value
3：B road strength
4：B road FFT value
549 | PowerVoltSt opModeEn | PowerVoltStopModeEn | W/R | 0、1 |  |  | 0：disable
1:enable
The power is restored when the voltage is less than the recovery point
550 | VoltWattRec overTime | Voltage active power recovery time | W/R | 0-15000 | 20ms
551 | HVoltDerate | Voltage active cut-off | W/R | -5011
| StopPower | power |  |  | 400
552 | QVTimeExpo nent | QVTimeExponent |  | WR | 1-255 |  |  | Q varies exponentially with time
553 | Volt-Watt | Voltage active V1 point, corresponding active power |  | WR | 0-11400
Watt1
554 | Volt-Watt | Voltage active V2 point, corresponding active power |  | WR | 0-11400
Watt2
……
600 | Volt-Var | Voltage reactive V1 |  | WR | 0-1000 |  |  | 0%~100.0%,US regulations | latest | safety
| Var1 | point,
Corresponding reactive power
percentage(Capacitive
Qmax)
601 | Volt-Var | Voltage reactive point, | V2 | WR | 0-1000 |  |  | 0%~100.0%,US regulations | latest | safety
| Var2 | Corresponding react power percentage | ive
602 | Volt-Var | Voltage reactive point, | V3 | WR | 0-1000 |  |  | 0%~100.0%,US regulations | latest | safety
| Var3 | Corresponding react power percentage | ive
603 | Volt-Var | Voltage reactive point, | V4 | WR | 0-1000 |  |  | 0%~100.0%,US latest safety regulations
| Var4 | Corresponding react power percentage(Inductive | ive
Qmax)
604
605 | OPModEner | Allowed inverter output power |  | R/W | 0/1 |  |  | 0: output power not allowed
| gize | [6 empty] | 1: allowable output power
For US models
608 | OneKeySetB | One key to set battery mode function |  | R/W |  |  |  | 0: self-use
| DCMode | [6 empty] | 1: battery priority
2: Grid priority
255：Disable
Currently used for US models
609 | PowerOutpu tEnable | Zero Power Output | [5 empty] | 0：Zero Power Output
|  | Enable | [5 empty] | 1：Unlimited output power
(default is 1)
610 | DealDebugP araFlag | Flag bit for clearing debug variables |  |  |  |  | Currently only bit0 and bit1 are used bit0 is used to manually clear the Debug data uploaded to the server bit1 is used to manually clear the fault codes that need to be powered off to clear
612 | bAcCoupleE n | AcCoupleEn | R/W | 0-1 |  |  | 0：disable
1：enable
…..
660 | ReloadCmd | M3 remote command |  |  |  |  | 0xA0: Initialize safety defaults
0xAA: Reboot M3 remotely
Six group for Storage Power
Register NO. | Variable | Description | Write or not | Value | Unit | Initial value | Note
Name
1000 | Float charge current limit | When charge current battery need is lower than this value, enter into float charge | W |  | 0.1A | 600 | CC current
1001 | PF CMD | Set the following 19-22 | W | 0or1, |  | 0 | Means these settings will be acting or not when next
| memory | CMD will be memory ornot(1/0), if not, these settings are the initial value. |  |  |  |  | power on(02 repeat)
state
1002 | VbatStartF orDischarg e | LV Vbat | R/W |  | 0.1V |  | Lead-acid battery LV voltage
1003 | VbatlowWa | LoadPercent(only lead-Acid): | W |  | 0.1V |  | Clear battery low voltage error voltage point
| rnClr | 45.5V
<20%
48.0V
20%~50%
49.0V
>50
1004 | Vbatstopfo rdischarge | Should stop discharge when lower than this | W |  | 0.01V
voltage(only lead-Acid):
46.0V
<20%
44.8V
20%~50%
44.2V
>50%
1005 | Vbat stop | Should stop charge when higher than this voltage | W |  | 0.01V | 5800
for charge
1006 | Vbat start | Should not discharge when lower than this | W |  | 0.01V | 4800
| for discharge | voltage
1007 | Vbat constant charge | can charge when lower than this voltage | W |  | 0.01V | 5800 | CV voltage（acid）
1008 | EESysInfo.S ysSetEn | Bit0：Resved; | W |  |  |  | System Enable
Bit1：Resved;
Bit2：Resved;
Bit3：Resved;
Bit4：Resved;
Bit5：bDischargeEn；
Bit6：ForceDischrEn；
Bit7：ChargeEn；
Bit8：bForceChrEn；
Bit9：bBackUpEn；
Bit10：bInvLimitLoadE；
Bit11：bSpLimitLoadEn；
Bit12：bACChargeEn；
Bit13：bPVLoadLimitEn;
Bit14,15:UnUsed;
1009 | Battemp lower limit d | Battery temperature lower limit for discharge | W | 0-200:0-2 | 0.1℃ | 1170
0℃
1000-140
0：-40-0℃
1010 | Bat temp upper limit d | Battery temperature upper limit for discharge | W | 200-1000 | 0.1℃ | 420
1011 | Bat temp lower limit c | Battery temperature lower limit for charge | W | 0-200:0-2 | 0.1℃ | 30 | Lower temperature limit
0℃
1000-140
0：-40-0℃
1012 | Bat temp upper limit c | Battery temperature upper limit for charge | W | 200-1000 | 0.1℃ | 370 | Upper temperature limit
1013 | uwUnderFr eDischarge DelyTime | Under Fre Delay Time | s | 0-20 | 50ms |  | Under Fre Delay Time
1014 | BatMdlSeri alNum | Battery serial number | W | 0:00 |  |  | SPH4-11K used
1015 | BatMdlPara llNum | Battery parallel section | W | 0:00 |  |  | SPH4-11K used
1016 | DRMS_EN | / | / | / | / | / | 0：disable 1：enable
1017 | Bat First | High eight:hours |  | 0-23
| Start Time | Low eight: minutes |  | 0-59
4
1018 | Bat First Stop Time | High eight:hours |  | 0-23
| 4 | Low eight: minutes |  | 0-59
1019 | BatFirst on/off Switch 4 | Enable:1 |  | 0 or 1 |  |  | Battery priority enable 1
Disable:0
1020 | Bat First | High eight:hours |  | 0-23
| Start Time | Low eight: minutes |  | 0-59
5
1021 | Bat First | High eight:hours |  | 0-23
| Stop Time | Low eight: minutes |  | 0-59
5
1022 | BatFirst on/off Switch 5 | Enable:1 |  | 0 or 1 |  |  | Battery priority enable 1
Disable:0
1023 | Bat First | High eight:hours |  | 0-23
| Start Time | Low eight: minutes |  | 0-59
6
1024 | Bat First | High eight:hours |  | 0-23
| Stop Time | Low eight: minutes |  | 0-59
6
1025 | BatFirst on/off Switch 6 | Enable:1 |  | 0 or 1 |  |  | Battery priority enable 1
Disable:0
1026 | Grid First | High eight:hours |  | 0-23
| Start Time | Low eight: minutes |  | 0-59
4
1027 | Grid First | High eight:hours |  | 0-23
| Stop Time | Low eight: minutes |  | 0-59
4
1028 | Grid First | Enable:1 |  | 0 or 1 |  |  | Grid priority enable
| Stop | Disable:0
Switch 4
1029 | Grid First | High eight:hours |  | 0-23
| Start Time | Low eight: minutes |  | 0-59
5
1030 | Grid First | High eight:hours |  | 0-23
| Stop Time | Low eight: minutes |  | 0-59
5
1031 | Grid First | Enable:1 |  | 0 or 1 |  |  | Grid priority enable
| Stop | Disable:0
Switch 5
1032 | Grid First | High eight:hours |  | 0-23
| Start Time | Low eight: minutes |  | 0-59
6
1033 | Grid First | High eight:hours |  | 0-23
| Stop Time | Low eight: minutes |  | 0-59
6
1034 | Grid First | Enable:1 |  | 0 or 1 |  |  | Grid priority enable
| Stop | Disable:0
Switch 6
1035 | Bat First | High eight:hours |  | 0-23
| Start Time | Low eight: minutes |  | 0-59
4
1036 | / | / | / | / | / | / | Reserve
1037 | bCTMode | Use the CTMode to | W | 2:METER 1:cWirele ssCT |  | 0
|  | Choose RFCT \ Cable |  | 0:cWiredC
|  | CT\METER |  | T
1038 | CTAdjust | CTAdjust enable | W | 0:disable |  | 0
1:enable
1039 | / | / | / | / | / | / | Reserve
1040 | / | / |  | / |  |  | / |  | / |  | / | Reserve
1041 | / | / |  | / |  |  | / |  | / |  | / | Reserve
1042 | / | / |  | / |  |  | / |  | / |  |  | Reserve
1043 | / | / |  | / |  |  | / |  | / |  | / | Reserve
1044 | Priority | ForceChrEn/ForceDischr |  | R |  |  | 0.Load(de fault)/1.B attery/2.G rid |  |  |  |  | bForceChrEn/disbForceDischrE n/dis
En
Load first/bat first /grid first
1045 | / | / |  | / |  |  | / |  | / |  | / | Reserve
1046 | / | / |  | / |  |  | / |  | / |  | / | Reserve
1047 | AgingTestSt ep Cmd | Command for aging test |  |  |  |  | 0: default |  |  |  |  | Cmd for aging test
1: charge 2:
discharge
1048 | BatteryTyp e | Battery type choose of buck-boost input |  |  |  |  | 0:Lithium 1:Lead-aci d |  |  |  | 0 | Battery type
2:other
1049 | / | / |  | / |  |  | / |  | / |  |  | Reserve
1050 | / | / |  | / |  |  | / |  | / |  | / | Reserve
1051 | / | / |  | / |  |  | / |  | / |  |  | Reserve
1052 | / | / |  | / |  |  | / |  | / |  |  | Reserve
1053 | / | / |  | / |  |  | / |  | / |  |  | Reserve
1054 | / | / |  | / |  |  | / |  | / |  | / | Reserve
1060 | BuckUpsFunE n |  | Ups function enable |  | or |  |  | 0:disable
|  |  | disable |  |  |  |  | 1:enable
1061 | BuckUPSVoltS et | UPS output voltage |  | 0.15972 |  | 230V
0.18611
0.25
1062 | UPSFreqSet | UPS output frequency |  | 0:50Hz |  | 50Hz
1:60Hz
... | / | / | / | / | / | / | reverse
Priority set
1070 | GridFirstDisch argePowerRat e | Discharge Power Rate | W | 0-100 | 1% | Discharge
|  | when Grid First |  |  |  | Power Rate when Grid
First
1071 | GridFirstStopS | Stop Discharge soc when | W | 0-100 | 1% | Stop Discharge soc when
| OC | Grid First |  |  |  | Grid First
1072… | / | / | / | / | / | / |  | reverse
1079
1080 | Grid First | High eight bit：hour |  | 0-23
| Start Time 1 | Low eight bit：minute |  | 0-59
1081 | Grid First Stop | High eight bit：hour |  | 0-23
| Time 1 | Low eight bit：minute |  | 0-59
1082 | Grid First Stop | Enable :1 |  | 0 or 1 |  | Grid First enable
| Switch 1 | Disable:0
1083 | Grid First | High eight bit：hour |  | 0-23
| Start Time 2 | Low eight bit：minute |  | 0-59
1084 | Grid First Stop | High eight bit：hour |  | 0-23
| Time 2 | Low eight bit：minute |  | 0-59
1085 | Grid First Stop | ForceDischarge.bSwitch&L |  | 0 or 1 |  | Grid First enable |  | ForceDischarge;
| Switch 2 | CD_SET_FORCE_TRUE_2)= | [5 empty] | LCD_SET_FORCE_T
|  | #NAME? | [5 empty] | RUE_2
1086 | Grid First | High eight bit：hour |  | 0-23
| Start Time 3 | Low eight bit：minute |  | 0-59
1087 | Grid First Stop | High eight bit：hour |  | 0-23
| Time 3 | Low eight bit：minute |  | 0-59
1088 | Grid First Stop | Enable :1 |  | 0 or 1 |  | Grid First enable
| Switch 3 | Disable:0
1089 | / | / | / | / | / | / |  | reserve
1090 | BatFirstPower | Charge Power Rate when | W | 0-100 | 1% | Charge
| Rate | Bat First |  |  |  | Power Rate when Bat
First
1091 | wBatFirst stop | Stop Charge soc when Bat | W | 0-100 | 1% | Stop
| SOC | First |  |  |  | Charge soc when Bat
First
1092 | AC charge | When Bat First |  | Enable:1 |  | AC Charge
| Switch | Enable:1 |  | Disable:0 |  | Enable
Disable:0
1093…
1099
1100 | Bat First Start | High eight bit：hour |  | 0-23
| Time 1 | Low eight bit：minute |  | 0-59
1101 | Bat First Stop | High eight bit：hour |  | 0-23
| Time 1 | Low eight bit：minute |  | 0-59
1102 | BatFirst on/off Switch 1 | Enable :1 |  | 0 or 1 |  | Bat First
|  | Disable:0 |  |  |  | Enable1
1103 | Bat First Start | High eight bit：hour |  | 0-23
| Time 2 | Low eight bit：minute |  | 0-59
1104 | Bat First Stop | High eight bit：hour |  | 0-23
| Time 2 | Low eight bit：minute |  | 0-59
1105 | BatFirston/off | Enable :1 |  | 0 or 1 |  | Bat First
| Switch 2 | Disable:0 |  |  |  | Enable2
1106 | Bat First Start | High eight bit：hour |  | 0-23
| Time 3 | Low eight bit：minute |  | 0-59
1107 | Bat First Stop | High eight bit：hour |  | 0-23
| Time 3 | Low eight bit：minute |  | 0-59
1108 | BatFirston/off | Enable :1 |  | 0 or 1 |  | Bat First
| Switch 3 | Disable:0 |  |  |  | Enable3
1109 | / | / | / | / | / | / | reserve
1110 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Start Time 1 | Low eight bit：minute |  | 0-59
1111 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Stop Time 1 | Low eight bit：minute |  | 0-59
1112 | Load First | Enable :1 |  | 0 or 1 |  | Load First | SPA/ reserve
| Switch 1 | Disable:0 |  |  |  | Enable
1113 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Start Time2 | Low eight bit：minute |  | 0-59
1114 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Stop Time 2 | Low eight bit：minute |  | 0-59
1115 | Load First | Enable :1 |  | 0 or 1 |  | Load First | SPA/ reserve
| Switch 2 | Disable:0 |  |  |  | Enable
1116 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Start Time 3 | Low eight bit：minute |  | 0-59
1117 | Load First | High eight bit：hour |  | 0-23 |  |  | SPA/ reserve
| Stop Time 3 | Low eight bit：minute |  | 0-59
1118 | Load First | Enable :1 |  | 0 or 1 |  | Load First | SPA/ reserve
| Switch 3 | Disable:0 |  |  |  | Enable
1119 | NewEPowerC | / | / | / | / | / | 0：The old formula
| alcFlag | [5 empty] | 1 ： The new
formula
1120 | BackUpEn | BackUp Enable |  |  |  |  | MIX US
1121 | SGIPEn | SGIP Enable |  |  |  |  | MIX US
……… | 1122~1124 | / | / | / | / | / | reserve
1125 | BatSerialNO. | Product serial number of the first PACK of energy | / | / | ASCII
| 8 | storage batteries
1126 | BatSerialNO. |  | / | / | ASCII
7
1127 | BatSerialNO. |  | / | / | ASCII
6
1128 | BatSerialNO. |  | / | / | ASCII
5
1129 | BatSerialNO. |  | / | / | ASCII
4
1130 | BatSerialNO. |  | / | / | ASCII
3
1131 | BatSerialNO. |  | / | / | ASCII
2
1132 | BatSerialNO. |  | / | / | ASCII
1
1132 | BatSerialNO. | The serial number of the second to tenth packs of the energy storage battery consists of nine packs, and | / | / | ASCII
~1204 | 8~
BatSerialNO.
1
the format of the serial number of each PACK is
1125 to 1132
……
1244 | Com version |  | Name of the battery main control firmware version |  |  | ASCII
NameH
1245 | Com version |  | Name of the battery main control firmware version |  |  | ASCII
NameL
1246 | Com version |  | Version of the battery main control firmware |  |  | digital
No
1247 | Com version |  | Name of battery monitoring firmware |  |  | ASCII
| NameH |  | version
1248 | Com version |  | Name of battery monitoring firmware |  |  | ASCII
| NameL |  | version
1249 | Com version |  | Battery monitoring |  |  | digital
| No |  | firmware version
Use for TL-X and TL-XH
3000 | ExportLimitFa iledPowerRat e |  | The power rate when | R/W |  | 0.1% |  | The power rate when exportLimit
|  |  | exportLimit failed |  |  |  |  | failed
3001 | New | NO | Serial number 1-2 | R/W |  | ASCII |  | The new model
| Serial | [6 empty] | uses the following registers to record the serial number; The representation is the same as the original: one register holds two characters and the new serial number is 30 characters.
3002 | New | NO | Serial number 3-4 | R/W |  | ASCII
Serial
3003 | New | NO | Serial number 5-6 | R/W |  | ASCII
Serial
3004 | New | NO | Serial number 7-8 | R/W |  | ASCII
Serial
3005 | New | NO | Serial number 9-10 | R/W |  | ASCII
Serial
3006 | New | NO | Serial number 11-12 | R/W |  | ASCII
Serial
3007 | New | NO | Serial number 13-14 | R/W |  | ASCII
Serial
3008 | New | NO | Serial number 15-16 | R/W |  | ASCII
Serial
3009 | New | Serial number 17-18 | R/W |  | ASCII
Serial NO
3010 | New | Serial number 19-20 | R/W |  | ASCII
Serial NO
3011 | New | Serial number 21-22 | R/W |  | ASCII
Serial NO
3012 | New | Serial number 23-24 | R/W |  | ASCII
Serial NO
3013 | New | Serial number 25-26 | R/W |  | ASCII
Serial NO
3014 | New | Serial number 27-28 | R/W |  | ASCII
Serial NO
3015 | New | Serial number 29-30 | R/W |  | ASCII
Serial NO
3016 | DryContactFu ncEn | DryContact function enable | R/W | 0:Disable |  |  | DryContact function enable
1: Enable
3017 | DryContactOn | The power rate of | R/W | 0~1000 | 0.1% |  | The power rate of drycontact turn on
| Rate | drycontact turn on
3018 | bWorkMode | WorkMode----0:default,1: | R/W | 0、1、2 |  |  | MIN2.5~6KTL-XH/ XA Double CT
|  | System Retrofit 2: Multi-Parallel |  |  |  |  | special
3019 | DryContactOf fRate | DryContactOffRate | Dry contact closure power | R/W | 0~100 | 0.1% | Dry contact closure power pe rcentage
0
3020 | BoxCtrlInvOrd er | BoxCtrlInvOrder | Off-net box control instruct ion | R/W
3021 | ExterCommOf fGridEn | External communication setting manual off-network enable | R/W |  |  |  | 0x00: Disable;
（default）
0x01: Enable;
3022 | uwBdcStopW orkOfBusVolt | BdcStopWorkOfBusVolt | R
3023 | bGridType | GridType---0:SinglePhase | R/W | 0、1、2 |  |  | MIN2.5~6KTL-XH/ XA Double CT
|  | 1:ThreePhase |  |  |  |  | special
2:SplitPhase
3024 | Float charge current limit | When charge current battery need is lower than | R/W |  | 0.1A | 600 | CC current
this value, enter into float charge
3025 | VbatWarning | "Battery-low" warning setup voltage | R/W |  | 0.1V | 4800 | Lead acid battery
LV voltage
3026 | VbatlowWarn | "Battery-low" warning clear voltage | R/W |  | 0.1V |  | Clear battery low voltage error voltage point
| Clr | [5 empty] | LoadPercent(only lead-Acid):
45.5V(Load <
20%);
48.0V(20%<=Load
<=50%);
49.0V(Load >
50%);
3027 | Vbatstopfordi scharge | Battery cut off voltage | R/W |  | 0.1V |  | Should stop discharge when lower than this voltage(only lead-Acid):
46.0V(Load <
20%);
44.8V(20%<=Load
<=50%);
44.2V(Load >
50%);
3028 | Vbat stop for charge | Battery over charge voltage | R/W |  | 0.01V | 5800 | Should stop charge when higher than this voltage
3029 | Vbat start for discharge | Battery start discharge voltage | R/W |  | 0.01V | 4800 | Should not discharge when lower than this voltage
3030 | Vbat constant charge | Battery constant charge voltage | R/W |  | 0.01V | 5800 | CV voltage（acid） can charge when lower than this voltage
3031 | Battemp lower limit d | Battery temperature lower limit for discharge | R/W |  | 0.1℃ | 1170 | 0-200:0-20℃
1000-1400：
-40-0℃
3032 | Bat temp upper limit d | Battery temperature upper limit for discharge | R/W |  | 0.1℃ | 420
3033 | Bat temp lower limit c | Battery temperature lower limit for charge | R/W |  | 0.1℃ | 30 | Battery temperature lower
limit
0-200:0-20℃
1000-1400：
-40-0℃
3034 | Bat temp upper limit c | Battery temperature upper limit for charge | R/W |  | 0.1℃ | 370 | Battery temperature upper limit
3035 | uwUnderFreD ischargeDelyT ime | Under Fre Delay Time | R/W |  | 50ms |  | Under Fre Delay
Time
3036 | GridFirstDisch argePowerRat e | Discharge Power Rate when Grid First |  |  |  | 1-255
3037 | GridFirstStopS | Stop Discharge soc when |  |  |  | 1-100
| OC | Grid First
3038 | Time 1(xh) | Period 1: [Start Time ~ End | R/W |  |  |  | Bit0~7: minutes;
|  | Time], [Charge/Discharge], |  |  |  |  | Bit8~12: hour;
|  | [Disable/Enable] |  |  |  |  | Bit13~14,
|  | 3038 enable, charge and discharge, start time, end time 3039 |  |  |  |  | 0: load priority;
1: battery priority;
2: Grid priority;
Bit15,
0: prohibited; 1:
enabled;
3039 |  |  | R/W |  |  |  | Bit0~7: minutes;
Bit8~12: hour;
Bit13~15: reserved
3040 | Time 2(xh) | Time period 2: [start time ~ end time], [charge / | R/W |  |  |  | Bit0~7: minutes;
|  | discharge], [disable / enable] |  |  |  |  | Bit8~12: hour;
|  | 3040 enable, charge and discharge, start time, 3041 |  |  |  |  | Bit13~14,
|  | end time |  |  |  |  | 0: load priority;
1: battery priority;
2: Grid priority;
Bit15,
0: prohibited; 1:
enabled;
3041 |  |  | R/W |  |  |  | Bit0~7: minutes;
Bit8~12: hour;
Bit13~15: reserved
3042 | Time 3(xh) | With Time1 | R/W |  |  |  | With Time1
3043 |  |  | R/W |  |  |  | With Time1
3044 | Time 4(xh) | With Time1 | R/W |  |  |  | With Time1
3045 |  |  | R/W |  |  |  | With Time1
3046 | 预留
3047 | BatFirstPower | Charge Power Rate when |  |  |  | 1-100
| Rate | Bat First
3048 | wBatFirst stop | Stop Charge soc when Bat |  |  |  | 1-100
| SOC | First
3049 | AcChargeEna ble | AcChargeEnable |  |  |  |  | Enable :1
Disable:0
3050 | Time 5(xh) | With Time1 | R/W |  |  |  | With Time1
3051 |  |  | R/W |  |  |  | With Time1
3052 | Time 6(xh) | With Time1 | R/W |  |  |  | With Time1
3053 |  |  | R/W |  |  |  | With Time1
3054 | Time 7(xh) | With Time1 | R/W |  |  |  | With Time1
3055 |  |  | R/W |  |  |  | With Time1
3056 | Time 8(xh) | With Time1 | R/W |  |  |  | With Time1
3057 |  |  | R/W |  |  |  | With Time1
3058 | Time 9(xh) | With Time1 | R/W |  |  |  | With Time1
3059 |  |  | R/W |  |  |  | With Time1
3060~ | Reserved
3069
3070 | BatteryType | Battery type choose of buck-boost input | R/W |  |  |  | Battery type
0:Lithium
1:Lead-acid
2:other
3071 | BatMdlSeria/ | BatMdlSeria/ParalNum | R/W |  |  |  | BatMdlSeria/Paral
| ParalNum | [5 empty] | Num;
SPH4-11K used The upper 8 bits indicate the number of series segments； The lower 8 bits indicate the number of parallel
sections;
3072 | Reserved
3073 | Reserved
3074 | Reserved
3075 | Reserved
3076 | Reserved
3077 | Reserved
3078 | Reserved
3079 | UpsFunEn | Ups function enable or disable | R/W |  |  | 0 | 0:disable
1:enable
3080 | UPSVoltSet | UPS output voltage | R/W |  |  | 0 | 0:230V
1:208V
2:240V
3081 | UPSFreqSet | UPS output frequency | R/W |  |  | 0 | 0:50Hz
1:60Hz
3082 | bLoadFirstSto pSocSet | StopSoc When LoadFirst | R/W |  |  | 13-100 | ratio
3083 | Reserved
3084 | Reserved
3085 | Com Address | Communication addr | R/W |  |  | 1 | 1 : Communication addr=1
1 ~ 254 :
Communication addr=1~254
3086 | BaudRate | Communication BaudRate | R/W |  |  | 0 | 0: 9600 bps
1: 38400 bps
3087 | Serial NO. 1 | Serial Number 1-2 | R/W |  | ASCII |  | For battery
3088 | Serial NO. 2 | Serial Number 3-4 |  | R/W |  | ASCII
3089 | Serial NO. 3 | Serial Number 5-6 |  | R/W |  | ASCII
3090 | Serial NO. 4 | Serial Number 7-8 |  | R/W |  | ASCII
3091 | Serial No. 5 | Serial Number 9-10 |  | R/W |  | ASCII
3092 | Serial No.6 | Serial Number 11-12 |  | R/W |  | ASCII
3093 | Serial No. 7 | Serial Number 13-14 |  | R/W |  | ASCII
3094 | Serial No. 8 | Serial Number 15-16 |  | R/W |  | ASCII
3095 | BdcResetCmd | BDC Reset command |  | R/W |  |  |  | 0：Invalid data 1：Reset setting parameters 2：Reset correction parameter 3：Clear historical power
3096 | ARKM3 Code | BDCMonitoring software code |  | R |  | ASCII |  | ZEBA
3097
3098 | DTC | DTC |  | R
3099 | FW Code | DSP software code |  | R |  | ASCII
3100
3101 | Processor1 | DSP Software Version |  | R |  | ASCII
FW Vision
3102 | BusVoltRef | Minimum BUS voltage for charging and discharging batteries |  | R
3103 | ARKM3Ver | BDC monitoring software version |  | R
3104 | BMS_MCUVer | BMS hardware version | R |  | 1
| sion | information
3105 | BMS_FW | BMS software version information | R |  | 1
3106 | BMS_Info | BMS ManufacturerName | R |  | 1
3107 | BMSCommTy pe | BMSCommType | R |  | 1 |  |  | BMSCommunicati on interface type：
0: RS485;
1: CAN;
3108 | Module 4 | BDCmodel (4) |  | R/W | &*11 |  |  | SxxBxx
3109 | Module 3 | BDCmodel (3) |  | R/W | &*11 |  |  | DxxTxx
3110 | Module 2 | BDCmodel (2) | R/W | &*11 |  |  | PxxUxx
3111 | Module 1 | BDCmodel (1) | R/W | &*11 |  |  | Mxxxx
3112 | Reserved
3113 | unProtocolVe | BDCProtocolVer | R | 1 |  |  | Bit8-bit15 The major version number ranges from 0-256. In principle, it cannot be changed
| r | [5 empty] | Bit0-bit7 Minor version number [0-256]. If the protocol is changed, you need to update this version No.
3114 | uwCertificatio nVer | BDC CertificationVer | R | 1
3115 ~ | Reserved
3124
US Machine type Time Set
3125 | Time Month1 | Use with Time1-9（us） | R/W |  |  |  | bit0~3:month_L； bit4~7: month_H
|  | ，Add month time |  |  |  |  | bit8,
0:disable 1：enable
Bit9~15:reserve
3126 | Time Month2 | Use with Time10-18（us） | R/W |  |  |  | With Time Month1
，Add month time
3127 | Time Month3 | Use with Time19-27（us） | R/W |  |  |  | With Time Month1
，Add month time
3128 | Time Month4 | Use with Time28-36（us） | R/W |  |  |  | With Time Month1
，Add month time
3129 | Time 1（us） | time1：[starttime~endtime] | R/W | [Charge/ discharg |  |  | bit0~6:min； bit7~11:hour； bit12~14, 0:loadfirst;
e/counte
r
|  |  |  | current], [disable/ enable] |  |  | 1:batfirst；
2:gridfirst； 3: anti-reflux bit15, 0:disable;
1:enable;
3130 |  |  | R/W |  |  |  | bit0~6:min； bit7~11:hour； bit12-13, 0:Weekday
1:Weekend 2:WeeK bit14~15：reserve
3131-3 | Time 2（us） | Same as above | R/W |  |  |  | Same as Time 1
132 | [6 empty] | （us）
3133-3 | Time 3（us） | Same as above | R/W |  |  |  | Same as Time 1
134 | [6 empty] | （us）
3135-3 | Time 4（us） | Same as above | R/W |  |  |  | Same as Time 1
136 | [6 empty] | （us）
3137-3 | Time 5（us） | Same as above | R/W |  |  |  | Same as Time 1
138 | [6 empty] | （us）
3139-3 | Time 6（us） | Same as above | R/W |  |  |  | Same as Time 1
140 | [6 empty] | （us）
3141-3 | Time 7（us） | Same as above | R/W |  |  |  | Same as Time 1
142 | [6 empty] | （us）
3143-3 | Time 8（us） | Same as above | R/W |  |  |  | Same as Time 1
144 | [6 empty] | （us）
3145-3 | Time9（us） | Same as above | R/W |  |  |  | Same as Time 1
146 | [6 empty] | （us）
3147-3 | Time 10（us） | Same as above | R/W |  |  |  | Same as Time 1
148 | [6 empty] | （us）
3149-3 | Time 11（us） | Same as above | R/W |  |  |  | Same as Time 1
150 | [6 empty] | （us）
3151-3 | Time 12（us） | Same as above | R/W |  |  |  | Same as Time 1
152 | [6 empty] | （us）
3153-3 | Time 13（us） | Same as above | R/W |  |  |  | Same as Time 1
154 | [6 empty] | （us）
3155-3 | Time 14（us） | Same as above | R/W |  |  |  | Same as Time 1
156 | [6 empty] | （us）
3157-3 | Time15（us） | Same as above | R/W |  |  |  | Same as Time 1
158 | [6 empty] | （us）
3159-3 | Time 16（us） | Same as above | R/W |  |  |  | Same as Time 1
160 | [6 empty] | （us）
3161-3 | Time 17（us） | Same as above | R/W |  |  |  | Same as Time 1
162 | [6 empty] | （us）
3163-3 | Time 18（us） | Same as above | R/W |  |  |  | Same as Time 1
164 | [6 empty] | （us）
3165-3 | Time 19（us） | Same as above | R/W |  |  |  | Same as Time 1
166 | [6 empty] | （us）
3167-3 | Time 20（us） | Same as above | R/W |  |  |  | Same as Time 1
168 | [6 empty] | （us）
3169-3 | Time 21（us） | Same as above | R/W |  |  |  | Same as Time 1
170 | [6 empty] | （us）
3171-3 | Time 22（us） | Same as above | R/W |  |  |  | Same as Time 1
172 | [6 empty] | （us）
3173-3 | Time 23（us） | Same as above | R/W |  |  |  | Same as Time 1
174 | [6 empty] | （us）
3175-3 | Time 24（us） | Same as above | R/W |  |  |  | Same as Time 1
176 | [6 empty] | （us）
3177-3 | Time 25（us） | Same as above | R/W |  |  |  | Same as Time 1
178 | [6 empty] | （us）
3179-3 | Time 26（us） | Same as above | R/W |  |  |  | Same as Time 1
180 | [6 empty] | （us）
3181-3 | Time 27（us） | Same as above | R/W |  |  |  | Same as Time 1
182 | [6 empty] | （us）
3183-3 | Time 28（us） | Same as above | R/W |  |  |  | Same as Time 1
184 | [6 empty] | （us）
3185-3 | Time 29（us） | Same as above | R/W |  |  |  | Same as Time 1
186 | [6 empty] | （us）
3187-3 | Time 30（us） | Same as above | R/W |  |  |  | Same as Time 1
188 | [6 empty] | （us）
3189-3 | Time 31（us） | Same as above | R/W |  |  |  | Same as Time 1
190 | [6 empty] | （us）
3191-3 | Time 32（us） | Same as above | R/W |  |  |  | Same as Time 1
192 | [6 empty] | （us）
3193-3 | Time 33（us） | Same as above | R/W |  |  |  | Same as Time 1
194 | [6 empty] | （us）
3195-3 | Time 34（us） | Same as above | R/W |  |  |  | Same as Time 1
196 | [6 empty] | （us）
3197-3 | Time 35（us） | Same as above | R/W |  |  |  | Same as Time 1
198 | [6 empty] | （us）
3199-3 | Time 36（us） | Same as above | R/W |  |  |  | Same as Time 1
200 | [6 empty] | （us）
3201 | SpecialDay1 | SpecialDay1（month，Day） | R/W |  |  |  | bit0~7:day； bit8~14:month bit15， 0：disable 1： enable
3202 | SpecialDay1_ | Start time | R/W |  |  |  | bit0~6:min； bit7~11:hour； bit12~14, 0:loadfirst;
| Time1 | [5 empty] | 1:batfirst；
2:gridfirst； 3: anti-reflux bit15, 0: disable;
1: enable;
3203 |  | endtime | R/W |  |  |  | bit0~6:min； bit7~11:hour； bit12~15：reserve
3204-3 | SpecialDay1_ | Same as above | R/W |  |  |  | Same as
205 | Time2 | [5 empty] | SpecialDay1_Time
1
3206-3 | SpecialDay1_ | Same as above | R/W |  |  |  | Same as
207 | Time3 | [5 empty] | SpecialDay1_Time
1
3208-3 | SpecialDay1_ | Same as above | R/W |  |  |  | Same as
209 | Time4 | [5 empty] | SpecialDay1_Time
1
3210-3 | SpecialDay1_ | Same as above | R/W |  |  |  | Same as
211 | Time5 | [5 empty] | SpecialDay1_Time
1
3212-3 | SpecialDay1_ | Same as above | R/W |  |  |  | Same as
213 | Time6 | [5 empty] | SpecialDay1_Time
1
3214-3 | SpecialDay1_ | Same as above | R/W |  |  |  | Same as
215 | Time7 | [5 empty] | SpecialDay1_Time
1
3216-3 | SpecialDay1_ | Same as above | R/W |  |  |  | Same as
217 | Time8 | [5 empty] | SpecialDay1_Time
1
3218-3 | SpecialDay1_ | Same as above | R/W |  |  |  | Same as
219 | Time9 | [5 empty] | SpecialDay1_Time
1
3220 | SpecialDay2 | SpecialDay2（month，Day） | R/W |  |  |  | bit0~7:day； bit8~14:month bit15， 0：disable
1：enable
3221 | SpecialDay2_ | Start time | R/W |  |  |  | bit0~6: min； bit7~11: hour； bit12~14,
| Time1 | [5 empty] | 0: loadfirst;
1: batfirst；
2: gridfirst； 3: anti-reflux bit15, 0: disable;
1: enable;
3222 |  | endtime | R/W |  |  |  | bit0~6: min； bit7~11: hour； bit12~15：reserve
3223-3 | SpecialDay2_ | Same as above | R/W |  |  |  | Same as
224 | Time2 | [5 empty] | SpecialDay2_Time
1
3225-3 | SpecialDay2_ | Same as above | R/W |  |  |  | Same as
226 | Time3 | [5 empty] | SpecialDay2_Time
1
3227-3 | SpecialDay2_ | Same as above | R/W |  |  |  | Same as
228 | Time4 | [5 empty] | SpecialDay2_Time
1
3229-3 | SpecialDay2_ | Same as above | R/W |  |  |  | Same as
230 | Time5 | [5 empty] | SpecialDay2_Time
1
3231-3 | SpecialDay2_ | Same as above | R/W |  |  |  | Same as
232 | Time6 | [5 empty] | SpecialDay2_Time
1
3233-3 | SpecialDay2_ | Same as above | R/W |  |  |  | Same as
234 | Time7 | [5 empty] | SpecialDay2_Time
1
3235-3 | SpecialDay2_ | Same as above | R/W |  |  |  | Same as
236 | Time8 | [5 empty] | SpecialDay2_Time
1
3237-3 | SpecialDay2_ | Same as above | R/W |  |  |  | Same as
238 | Time9 | [5 empty] | SpecialDay2_Time
1
3239-3 | Reserve | Reserve | R/W
249
BDC information (support up to 10 parallel BDC)
5000-5039 |  | 1 |  |  | Reference 3085 to 3124 for a total of
40 registers Description
5040-5079 |  | 2
5000+(N-1)*40--- |  | N
5039+(N-1)*40
4.2 Input Reg
NO. | Variable Name |  | Description | Value | Unit | Note
First group
0 |  | Inverter Status | Inverter run state | 0:waiting,
1:normal,
3:fault
1 |  | Ppv H | Input power (high) |  | 0.1W
2 |  | Ppv L | Input power (low) |  | 0.1W
3 |  | Vpv1 | PV1 voltage |  | 0.1V
4 |  | PV1Curr | PV1 input current |  | 0.1A
5 |  | Ppv1 H | PV1 input power(high) |  | 0.1W
6 |  | Ppv1 L | PV1 input power(low) |  | 0.1W
7 |  | Vpv2 | PV2 voltage |  | 0.1V
8 |  | PV2Curr | PV2 input current |  | 0.1A
9 |  | Ppv2 H | PV2 input power (high) |  | 0.1W
10 |  | Ppv2 L | PV2 input power (low) |  | 0.1W
11 |  | Vpv3 | PV3 voltage |  | 0.1V
12 |  | PV3Curr | PV3 input current |  | 0.1A
13 |  | Ppv3 H | PV3 input power (high) |  | 0.1W
14 |  | Ppv3 L | PV3 input power (low) |  | 0.1W
15 |  | Vpv4 | PV4 voltage |  | 0.1V
16 |  | PV4Curr | PV4 input current |  | 0.1A
17 |  | Ppv4 H | PV4 input power (high) |  | 0.1W
18 |  | Ppv4 L | PV4 input power (low) |  | 0.1W
19 |  | Vpv5 | PV5 voltage |  | 0.1V
20 |  | PV5Curr | PV5 input current |  | 0.1A
21 |  | Ppv5H | PV5 input power(high) |  | 0.1W
22 |  | Ppv5 L | PV5 input power(low) |  | 0.1W
23 |  | Vpv6 | PV6 voltage |  | 0.1V
24 |  | PV6Curr | PV6 input current |  | 0.1A
25 | Ppv6 H | PV6 input power (high) |  | 0.1W
26 | Ppv6 L | PV6 input power (low) |  | 0.1W
27 | Vpv7 | PV7 voltage |  | 0.1V
28 | PV7Curr | PV7 input current |  | 0.1A
29 | Ppv7 H | PV7 input power (high) |  | 0.1W
30 | Ppv7 L | PV7 input power (low) |  | 0.1W
31 | Vpv8 | PV8 voltage |  | 0.1V
32 | PV8Curr | PV8 input current |  | 0.1A
33 | Ppv8 H | PV8 input power (high) |  | 0.1W
34 | Ppv8 L | PV8 input power (low) |  | 0.1W
35 | Pac H | Output power (high) |  | 0.1W
36 | Pac L | Output power (low) |  | 0.1W
37 | Fac | Grid frequency |  | 0.01Hz
38 | Vac1 | Three/single phase grid voltage |  | 0.1V
39 | Iac1 | Three/single phase grid output current |  | 0.1A
40 | Pac1 H | Three/single phase grid output watt |  | 0.1VA
VA (high)
41 | Pac1 L | Three/single phase grid output watt |  | 0.1VA
VA(low)
42 | Vac2 | Three phase grid voltage |  | 0.1V
43 | Iac2 | Three phase grid output current |  | 0.1A
44 | Pac2 H | Three phase grid output power (high) |  | 0.1VA
45 | Pac2 L | Three phase grid output power (low) |  | 0.1VA
46 | Vac3 | Three phase grid voltage |  | 0.1V
47 | Iac3 | Three phase grid output current |  | 0.1A
48 | Pac3 H | Three phase grid output power (high) |  | 0.1VA
49 | Pac3 L | Three phase grid output power (low) |  | 0.1VA
50 | Vac_RS | Three phase grid voltage |  | 0.1V | Line voltage
51 | Vac_ST | Three phase grid voltage |  | 0.1V | Line voltage
52 | Vac_TR | Three phase grid voltage |  | 0.1V | Line voltage
53 | Eactoday H | Today generate energy (high) |  | 0.1kWH
54 | Eac today L | Today generate energy (low) |  | 0.1kWH
55 | Eac total H | Total generate energy (high) |  | 0.1kWH
56 | Eac total L | Total generate energy (low) |  | 0.1kWH
57 | Time total H | Work time total (high) |  | 0.5s
58 | Time total L | Work time total (low) |  | 0.5s
59 | Epv1_today H | PV1Energy today(high) |  | 0.1kWh
60 | Epv1_today L | PV1Energy today (low) |  | 0.1kWh
61 | Epv1_total H | PV1Energy total(high) |  | 0.1kWh
62 | Epv1_total L | PV1Energy total (low) |  | 0.1kWh
63 | Epv2_today H | PV2Energy today(high) |  | 0.1kWh
64 | Epv2_today L | PV2Energy today (low) |  | 0.1kWh
65 | Epv2_total H | PV2Energy total(high) |  | 0.1kWh
66 | Epv2_total L | PV2Energy total (low) |  | 0.1kWh
67 | Epv3_today H | PV3 Energy today(high) |  | 0.1kWh
68 | Epv3_today L | PV3 Energy today (low) |  | 0.1kWh
69 | Epv3_total H | PV3 Energy total(high) |  | 0.1kWh
70 | Epv3_total L | PV3 Energy total (low) |  | 0.1kWh
71 | Epv4_today H | PV4Energy today(high) |  | 0.1kWh
72 | Epv4_today L | PV4Energy today (low) |  | 0.1kWh
73 | Epv4_total H | PV4Energy total(high) |  | 0.1kWh
74 | Epv4_total L | PV4Energy total (low) |  | 0.1kWh
75 | Epv5_today H | PV5Energy today(high) |  | 0.1kWh
76 | Epv5_today L | PV5Energy today (low) |  | 0.1kWh
77 | Epv5_total H | PV5Energy total(high) |  | 0.1kWh
78 | Epv5_total L | PV5Energy total (low) |  | 0.1kWh
79 | Epv6_today H | PV6Energy today(high) |  | 0.1kWh
80 | Epv6_today L | PV6Energy today (low) |  | 0.1kWh
81 | Epv6_total H | PV6Energy total(high) |  | 0.1kWh
82 | Epv6_total L | PV6Energy total (low) |  | 0.1kWh
83 | Epv7_today H | PV7Energy today(high) |  | 0.1kWh
84 | Epv7_today L | PV7Energy today (low) |  | 0.1kWh
85 | Epv7_total H | PV7 Energy total(high) |  | 0.1kWh
86 | Epv7_total L | PV7Energy total (low) |  | 0.1kWh
87 | Epv8_today H | PV8Energy today(high) |  | 0.1kWh
88 | Epv8_today L | PV8Energy today (low) |  | 0.1kWh
89 | Epv8_total H | PV8Energy total(high) |  | 0.1kWh
90 | Epv8_total L | PV8Energy total (low) |  | 0.1kWh
91 | Epv_total H | PV Energy total(high) |  | 0.1kWh
92 | Epv_total L | PV Energy total (low) |  | 0.1kWh
93 | Temp1 | Inverter temperature |  | 0.1C
94 | Temp2 | The inside IPM in inverter Temperature |  | 0.1C
95 | Temp3 | Boost temperature |  | 0.1C
96 | Temp4 |  |  |  | reserved
97 | uwBatVolt_DSP | BatVolt_DSP |  | 0.1V | BatVolt(DSP)
98 | P Bus Voltage | P Bus inside Voltage |  | 0.1V
99 | N Bus Voltage | N Bus inside Voltage |  | 0.1V
100 | IPF | Inverter output PF now | 0-20000
101 | RealOPPercent | Real Output power Percent |  | 1%
102 | OPFullwatt H | Output Maxpower Limited high
103 | OPFullwatt L | Output Maxpower Limited low |  | 0.1W
104 | DeratingMode | DeratingMode | 0:no derate;
1:PV;
2:*;
3:Vac;
4:Fac;
5:Tboost;
6:Tinv;
7:Control;
8:*;
9:*OverBack
ByTime;
105 | Fault Maincode | Inverter fault maincode
106
107 | Fault Subcode | Inverter fault subcode
108 | RemoteCtrlEn | / | 0.Load First | / | StoragePow er (SPA)
1.BatFirst
109 | RemoteCtrlPow er | / | 2.Grid | / | StoragePow er (SPA)
110 | Warning bit H | Warning bit H
111 | Warn Subcode | Inverter warn subcode
112 | Warn Maincode | Inverter warn maincode
| EACharge_Today | ACCharge energy today |  | 0.1kwh | Storage
| _H |  |  |  | Power
113 | real Power | real Power Percent | 0-100 | % | MAX
Percent
| EACharge_Today | ACCharge energy today |  | 0.1kwh | Storage
| _L |  |  |  | Power
114 | inv start delay time | inv start delay time |  |  | MAX
| EACharge_Total | ACCharge energy total |  | 0.1kwh | Storage
| _H |  |  |  | Power
115 | bINVAllFaultCod e | bINVAllFaultCode |  |  | MAX
| EACharge_Total | ACCharge energy total |  | 0.1kwh | Storage
| _L |  |  |  | Power
116 | AC charge | Grid power to local load |  | 0.1kwh | Storage
| Power_H |  |  |  | Power
117 | AC charge | Grid power to local load |  | 0.1kwh | Storage
| Power_L |  |  |  | Power
118 | Priority | 0:Load First |  |  | Storage
|  | 1:Battery First | [5 empty] | Power
2:Grid First
119 | Battery Type | 0：Lead-acid | [5 empty] | Storage
|  | 1：Lithium battery | [5 empty] | Power
120 | AutoProofreadC | Aging mode Auto-calibration command | [5 empty] | Storage
| MD | [6 empty] | Power
… | reserved | [6 empty] | reserved
124 | reserved | [6 empty] | reserved
Second group
125 | PID PV1+ Voltage |  | PID PV1PE Volt/ Flyspan voltage |  |  | 0~1000V | 0.1V
(MAX HV)
126 | PID PV1+ Current |  | PID PV1PE Curr |  |  | -10~10mA | 0.1mA
127 | PID PV2+ Voltage |  | PID PV2PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
(MAX HV)
128 | PID PV2+ Current |  | PID PV2PE Curr |  |  | -10~10mA | 0.1mA
129 | PID PV3+ Voltage |  | PID PV3PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
(MAX HV)
130 | PID PV3+ Current |  | PID PV3PE Curr |  |  | -10~10mA | 0.1mA
131 | PID PV4+ Voltage |  | PID PV4PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
(MAX HV)
132 | PID PV4+ Current |  | PID PV4PE Curr |  |  | -10~10mA | 0.1mA
133 | PID PV5+ Voltage |  | PID PV5PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
(MAX HV)
134 | PID PV5+ Current |  | PID PV5PE Curr |  |  | -10~10mA | 0.1mA
135 | PID PV6+ Voltage |  | PID PV6PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
(MAX HV)
136 | PID PV6+ Current |  | PID PV6PE Curr |  |  | -10~10mA | 0.1mA
137 | PID PV7+ Voltage |  | PID PV7PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
(MAX HV)
138 | PID PV7+ Current |  | PID PV7PE Curr |  |  | -10~10mA | 0.1mA
139 | PID PV8+ Voltage |  | PID PV8PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
(MAX HV)
140 | PID PV8+ Current |  | PID PV8PE Curr |  |  | -10~10mA | 0.1mA
141 | PID Status |  | Bit0~7:PID Working Status |  |  | 0~3
1:Wait Status
2:Normal Status
3:Fault Status
Bit8~15:Reversed
142 | V _String1 |  | PV String1 voltage |  |  |  | 0.1V
143 | Curr _String1 |  | PV String1 current |  |  | -15~15A | 0.1A
144 | V _String2 |  | PV String2 voltage |  |  |  | 0.1V
145 | Curr _String2 | PV String2 current | -15~15A | 0.1A
146 | V _String3 | PV String3 voltage |  | 0.1V
147 | Curr _String3 | PV String3 current | -15~15A | 0.1A
148 | V _String4 | PV String4 voltage |  | 0.1V
149 | Curr _String4 | PV String4 current | -15~15A | 0.1A
150 | V _String5 | PV String5 voltage |  | 0.1V
151 | Curr _String5 | PV String5 current | -15~15A | 0.1A
152 | V _String6 | PV String6 voltage |  | 0.1V
153 | Curr _String6 | PV String6 current | -15~15A | 0.1A
154 | V _String7 | PV String7 voltage |  | 0.1V
155 | Curr _String7 | PV String7 current | -15~15A | 0.1A
156 | V _String8 | PV String8 voltage |  | 0.1V
157 | Curr _String8 | PV String8 current | -15A~15A | 0.1A
158 | V _String9 | PV String9 voltage |  | 0.1V
159 | Curr _String9 | PV String9 current | -15A~15A | 0.1A
160 | V _String10 | PV String10 voltage |  | 0.1V
161 | Curr _String10 | PV String10 current | -15~15A | 0.1A
162 | V _String11 | PV String11 voltage |  | 0.1V
163 | Curr _String11 | PV String11 current | -15~15A | 0.1A
164 | V _String12 | PV String12 voltage |  | 0.1V
165 | Curr _String12 | PV String12 current | -15~15A | 0.1A
166 | V _String13 | PV String13 voltage |  | 0.1V
167 | Curr _String13 | PV String13 current | -15A~15A | 0.1A
168 | V _String14 | PV String14 voltage |  | 0.1V
169 | Curr _String14 | PV String14 current | -15~15A | 0.1A
170 | V _String15 | PV String15 voltage |  | 0.1V
171 | Curr _String15 | PV String15 current | -15~15A | 0.1A
172 | V _String16 | PV String16 voltage |  | 0.1V
173 | Curr _String16 | PV String16 current | -15~15A | 0.1A
174 | StrUnmatch | Bit0~15: String1~16 unmatch |  |  | suggestive
175 | StrCurrentUnblan ce | Bit0~15: String1~16 current unblance |  |  | suggestive
176 | StrDisconnect | Bit0~15: String1~16 disconnect |  |  | suggestive
177 | PIDFaultCode | Bit0:Output over voltage
Bit1: ISO fault
Bit2: BUS voltage abnormal
Bit3~15:reserved
178 | String Prompt | String Prompt
Bit0:String Unmatch
Bit1:StrDisconnect
Bit2:StrCurrentUnblance
Bit3~15:reserved
179 | PV Warning Value |  | PV Warning Value
180 | DSP075 | Warning | DSP075 Warning Value
Value
181 | DSP075 | Fault | DSP075 Fault Value
Value
182 | DSP067 | Debug | DSP067 Debug Data1
Data1
183 | DSP067 | Debug | DSP067 Debug Data2
Data2
184 | DSP067 | Debug | DSP067 Debug Data3
Data3
185 | DSP067 | Debug | DSP067 Debug Data4
Data4
186 | DSP067 | Debug | DSP067 Debug Data5
Data5
187 | DSP067 | Debug | DSP067 Debug Data6
Data6
188 | DSP067 | Debug | DSP067 Debug Data7
Data7
189 | DSP067 | Debug | DSP067 Debug Data8
Data8
190 | DSP075 | Debug | DSP075 Debug Data1
Data1
191 | DSP075 | Debug | DSP075 Debug Data2
Data2
192 | DSP075 | Debug | DSP075 Debug Data3
Data3
193 | DSP075 | Debug | DSP075 Debug Data4
Data4
194 | DSP075 | Debug | DSP075 Debug Data5
Data55
195 | DSP075 | Debug | DSP075 Debug Data6
Data6
196 | DSP075 | Debug | DSP075 Debug Data7
Data7
197 | DSP075 | Debug | DSP075 Debug Data8
Data8
198 | bUSBAgingTestOk |  | USBAgingTestOkFlag | 0-1
Flag
199 | bFlashEraseAging |  | FlashEraseAgingOkFlag | 0-1
OkFlag
200 | PVISO | PVISOValue |  |  | KΩ
201 | R_DCI | R DCI Curr |  |  | 0.1mA
202 | S_DCI | S DCI Curr |  |  | 0.1mA
203 | T_DCI | T DCI Curr |  |  | 0.1mA
204 | PID_Bus | PIDBusVolt |  |  | 0.1V
205 | GFCI | GFCI Curr |  |  | mA
206 | SVG/APF | SVG/APF Status+SVGAPFEqualRatio |  | High 8 bit：
| Status+SVGAPFEq ualRatio |  |  | SVGAPFEqua lRatio
Low 8 bit：
SVG/APF
Status
0:None
1:SVG Run
2:APF Run
3:SVG/APF
Run
207 | CT_I _R | R phase load side current for SVG |  |  | 0.1A
208 | CT_I _S | S phase load side current for SVG |  |  | 0.1A
209 | CT_I _T | T phase load side current for SVG |  |  | 0.1A
210 | CT_Q _R H | R phase load side output power for SVG(High) | reactive |  | 0.1Var
211 | CT_Q _R L | R phase load side output power for SVG(low) | reactive |  | 0.1Var
212 | CT_Q _S H | S phase load side output power for SVG(High) | reactive |  | 0.1Var
213 | CT_Q _S L | S phase load side output power for SVG(low) | reactive |  | 0.1Var
214 | CT_Q _T H | T phase load side output power for SVG(High) | reactive |  | 0.1Var
215 | CT_Q _T L | T phase load side output power for SVG(low) | reactive |  | 0.1Var
216 | CT HAR_I_R | R phase load side harmonic |  |  | 0.1A
217 | CT HAR_I_S | S phase load side harmonic |  |  | 0.1A
218 | CT HAR_I_T | T phase load side harmonic |  |  | 0.1A
219 | COMP_Q _R H | R phase compensate reactive power for SVG(High) |  |  | 0.1Var
220 | COMP_Q _R L | R phase compensate reactive power for SVG(low) |  |  | 0.1Var
221 | COMP_Q _S H | S phase compensate reactive power for SVG(High) |  |  | 0.1Var
222 | COMP_Q _S L | S phase compensate reactive power |  |  | 0.1Var
for SVG(low)
223 | COMP_Q _T H |  | T phase compensate reactive power for SVG(High) |  | 0.1Var
224 | COMP_Q _T L |  | T phase compensate reactive power for SVG(low) |  | 0.1Var
225 | COMP HAR_I_R |  | R phase compensate harmonic for |  | 0.1A
SVG
226 | COMP HAR_I_S |  | S phase compensate harmonic for |  | 0.1A
SVG
227 | COMP HAR_I_T |  | T phase compensate harmonic for |  | 0.1A
SVG
228 | bRS232AgingTest |  | RS232AgingTestOkFlag | 0-1
OkFlag
229 | bFanFaultBit |  | Bit0: Fan 1 fault bit
Bit1: Fan 2 fault bit
Bit2: Fan 3 fault bit
Bit3: Fan 4 fault bit
Bit4-7: Reserved
230 | Sac H |  | Output apparent power H |  | 0.1W
231 | Sac L |  | Output apparent power L |  | 0.1W
232 | ReActPowerH |  | Real Output Reactive Power H | Int32 | 0.1W
233 | ReActPowerL |  | Real Output Reactive Power L
234 | ReActPowerMaxH |  | Nominal Output Reactive Power H |  | 0.1var
235 | ReActPowerMaxL |  | Nominal Output Reactive Power L
236 | ReActPower_Total |  | Reactive power generation |  | 0.1kwh
H
237 | ReActPower_Total |  | Reactive power generation
L
238 | bAfciStatus |  | 0：Waiting
1：Self-check state
2：Detect pull arc state
3：Fault
4：Update
239 | uwPresentFFTValu e [CHANNEL_A] |  | PresentFFTValue [CHANNEL_A]
240 | uwPresentFFTValu e [CHANNEL_B] |  | PresentFFTValue [CHANNEL_B]
241 | DSP067 | Debug | DSP067 Debug Data1
Data1
242 | DSP067 | Debug | DSP067 Debug Data2
Data2
243 | DSP067 | Debug | DSP067 Debug Data3
Data3
244 | DSP067 | Debug | DSP067 Debug Data4
Data4
245 | DSP067 | Debug | DSP067 Debug Data5
Data5
246 | DSP067 | Debug | DSP067 Debug Data6
Data6
247 | DSP067 | Debug | DSP067 Debug Data7
Data7
248 | DSP067 | Debug | DSP067 Debug Data8
Data8
249 | [5 empty] | reserved
The eighth group for |  | PV9-PV16 information
875 | Vpv9 |  | PV9 voltage |  | 0.1V
876 | PV9Curr |  | PV9 Input current |  | 0.1A
877 | Ppv9 H |  | PV9 input power (High) |  | 0.1W
878 | Ppv9 L |  | PV9 input power (Low) |  | 0.1W
879 | Vpv10 |  | PV10 voltage |  | 0.1V
880 | PV10Curr |  | PV10 Input current |  | 0.1A
881 | Ppv10 H |  | PV10 input power (High) |  | 0.1W
882 | Ppv10 L |  | PV10 input power (Low) |  | 0.1W
883 | Vpv11 |  | PV11 voltage |  | 0.1V
884 | PV11Curr |  | PV11 Input current |  | 0.1A
885 | Ppv11 H |  | PV11 input power (High) |  | 0.1W
886 | Ppv11 L |  | PV11 input power (Low) |  | 0.1W
887 | Vpv12 |  | PV12 voltage |  | 0.1V
888 | PV12Curr |  | PV12 Input current |  | 0.1A
889 | Ppv12 H |  | PV12 input power (High) |  | 0.1W
890 | Ppv12 L |  | PV12 input power (Low) |  | 0.1W
891 | Vpv13 |  | PV13 voltage |  | 0.1V
892 | PV13Curr |  | PV13 Input current |  | 0.1A
893 | Ppv13H |  | PV13 input power (High) |  | 0.1W
894 | Ppv13 L |  | PV13 input power (Low) |  | 0.1W
895 | Vpv14 |  | PV14 voltage |  | 0.1V
896 | PV14Curr |  | PV14 Input current |  | 0.1A
897 | Ppv14 H |  | PV14 input power (High) |  | 0.1W
898 | Ppv14 L |  | PV14 input power (Low) |  | 0.1W
899 | Vpv15 |  | PV15 voltage |  | 0.1V
900 | PV15Curr |  | PV15 Input current |  | 0.1A
901 | Ppv15 H |  | PV15 input power (High) |  | 0.1W
902 | Ppv15 L |  | PV15 input power (Low) |  | 0.1W
903 | Vpv16 | PV16 voltage |  |  | 0.1V
904 | PV16Curr | PV16 Input current |  |  | 0.1A
905 | Ppv16 H | PV16 input power (High) |  |  | 0.1W
906 | Ppv16 L | PV16 input power (Low) |  |  | 0.1W
907 | Epv9_today H | PV9 energy today (High) |  |  | 0.1kWh
908 | Epv9_today L | PV9 energy today (Low) |  |  | 0.1kWh
909 | Epv9_total H | PV9 energy total (High) |  |  | 0.1kWh
910 | Epv9_total L | PV9 energy total (Low) |  |  | 0.1kWh
911 | Epv10_today H | PV10 energy today (High) |  |  | 0.1kWh
912 | Epv10_today L | PV10 energy today (Low) |  |  | 0.1kWh
913 | Epv10_total H | PV10 energy total (High) |  |  | 0.1kWh
914 | Epv10_total L | PV10 energy total (Low) |  |  | 0.1kWh
915 | Epv11_today H | PV11 energy today (High) |  |  | 0.1kWh
916 | Epv11_today L | PV11 energy today (Low) |  |  | 0.1kWh
917 | Epv11_total H | PV11 energy total (High) |  |  | 0.1kWh
918 | Epv11_total L | PV11 energy total (Low) |  |  | 0.1kWh
919 | Epv12_today H | PV12 energy today (High) |  |  | 0.1kWh
920 | Epv12_today L | PV12 energy today (Low) |  |  | 0.1kWh
921 | Epv12_total H | PV12 energy total (High) |  |  | 0.1kWh
922 | Epv12_total L | PV12 energy total (Low) |  |  | 0.1kWh
923 | Epv13_today H | PV13 energy today (High) |  |  | 0.1kWh
924 | Epv13_today L | PV13 energy today (Low) |  |  | 0.1kWh
925 | Epv13_total H | PV13 energy total (High) |  |  | 0.1kWh
926 | Epv13_total L | PV13 energy total (Low) |  |  | 0.1kWh
927 | Epv14_today H | PV14 energy today (High) |  |  | 0.1kWh
928 | Epv14_today L | PV14 energy today (Low) |  |  | 0.1kWh
929 | Epv14_total H | PV14 energy total (High) |  |  | 0.1kWh
930 | Epv14_total L | PV14 energy total (Low) |  |  | 0.1kWh
931 | Epv15_today H | PV15 energy today (High) |  |  | 0.1kWh
932 | Epv15_today L | PV15 energy today (Low) |  |  | 0.1kWh
933 | Epv15_total H | PV15 energy total (High) |  |  | 0.1kWh
934 | Epv15_total L | PV15 energy total (Low) |  |  | 0.1kWh
935 | Epv16_today H | PV16 energy today (High) |  |  | 0.1kWh
936 | Epv16_today L | PV16 energy today (Low) |  |  | 0.1kWh
937 | Epv16_total H | PV16 energy total (High) |  |  | 0.1kWh
938 | Epv16_total L | PV16 energy total (Low) |  |  | 0.1kWh
939 | PID PV9+ Voltage | PID PV9PE Volt/ Flyspan | voltage | 0~1000V | 0.1V
(MAX HV)
940 | PID PV9+ Current | PID PV9PE Current |  | -10~10mA | 0.1mA
941 | PID PV10+ | PID PV10PE/ Flyspan voltage (MAX |  | 0~1000V | 0.1V
| Voltage | HV)
942 | PID | PV10+ | PID PV10PE Current |  |  | -10~10mA | 0.1mA
Current
943 | PID | PV11+ | PID PV11PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
| Voltage |  | (MAX HV)
944 | PID | PV11+ | PID PV11PE Current |  |  | -10~10mA | 0.1mA
Current
945 | PID | PV12+ | PID PV12PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
| Voltage |  | (MAX HV)
946 | PID | PV12+ | PID PV12PE Current |  |  | -10~10mA | 0.1mA
Current
947 | PID | PV13+ | PID PV13PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
| Voltage |  | (MAX HV)
948 | PID | PV13+ | PID PV13PE Current |  |  | -10~10mA | 0.1mA
Current
949 | PID | PV14+ | PID PV14PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
| Voltage |  | (MAX HV)
950 | PID | PV14+ | PID PV14PE Current |  |  | -10~10mA | 0.1mA
Current
951 | PID | PV15+ | PID PV15PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
| Voltage |  | (MAX HV)
952 | PID | PV15+ | PID PV15PE Current |  |  | -10~10mA | 0.1mA
Current
953 | PID | PV16+ | PID PV16PE Volt/ | Flyspan | voltage | 0~1000V | 0.1V
| Voltage |  | (MAX HV)
954 | PID | PV16+ | PID PV16PE Current |  |  | -10~10mA | 0.1mA
Current
955 | V _String17 |  | PV String 17 voltage |  |  |  | 0.1V
956 | Curr _String17 |  | PV String 17 Current |  |  | -15~15A | 0.1A
957 | V _String18 |  | PV String 18 voltage |  |  |  | 0.1V
958 | Curr _String18 |  | PV String 18 Current |  |  | -15~15A | 0.1A
959 | V _String19 |  | PV String 19 voltage |  |  |  | 0.1V
960 | Curr _String19 |  | PV String 19 Current |  |  | -15~15A | 0.1A
961 | V _String20 |  | PV String 20 voltage |  |  |  | 0.1V
962 | Curr _String20 |  | PV String 20 Current |  |  | -15~15A | 0.1A
963 | V _String21 |  | PV String 21 voltage |  |  |  | 0.1V
964 | Curr _String21 |  | PV String 21 Current |  |  | -15~15A | 0.1A
965 | V _String22 |  | PV String22 voltage |  |  |  | 0.1V
966 | Curr _String22 |  | PV String 22 Current |  |  | -15~15A | 0.1A
967 | V _String23 |  | PV String 23 voltage |  |  |  | 0.1V
968 | Curr _String23 |  | PV String 23 Current |  |  | -15~15A | 0.1A
969 | V _String24 |  | PV String 24 voltage |  |  |  | 0.1V
970 | Curr _String24 | PV String 24 Current |  |  | -15A~15A |  | 0.1A
971 | V _String25 | PV String 25 voltage |  |  |  |  | 0.1V
972 | Curr _String25 | PV String 25 Current |  |  | -15A~15A |  | 0.1A
973 | V _String26 | PV String 26 voltage |  |  |  |  | 0.1V
974 | Curr _String26 | PV String 26 Current |  |  | -15~15A |  | 0.1A
975 | V _String27 | PV String 27 voltage |  |  |  |  | 0.1V
976 | Curr _String27 | PV String 27 Current |  |  | -15~15A |  | 0.1A
977 | V _String28 | PV String 28 voltage |  |  |  |  | 0.1V
978 | Curr _String28 | PV String 28 Current |  |  | -15~15A |  | 0.1A
979 | V _String29 | PV String 29 voltage |  |  |  |  | 0.1V
980 | Curr _String29 | PV String 29 Current |  |  | -15A~15A |  | 0.1A
981 | V _String30 | PV String 30 voltage |  |  |  |  | 0.1V
982 | Curr _String30 | PV String 30 Current |  |  | -15~15A |  | 0.1A
983 | V _String31 | PV String 31 voltage |  |  |  |  | 0.1V
984 | Curr _String31 | PV String 31 Current |  |  | -15~15A |  | 0.1A
985 | V _String32 | PV String 32 voltage |  |  |  |  | 0.1V
986 | Curr _String32 | PV String 32 Current |  |  | -15~15A |  | 0.1A
987 | StrUnmatch2 | Bit0~15: String 17~32 unmatch
988 | StrCurrentUnblan ce2 | Bit0~15:String 17~32 current
unblance
989 | StrDisconnect2 | Bit0~15: String 17~32 disconnect
990 | PV Warning Value | PV Warning Value (PV9-PV16)
Contains PV9~16 abnormal ， 和
Boost9~16 Drive anomalies
991 | StrWaringvalue1 | string1~string16 abnormal
992 | StrWaringvalue2 | string17~string32 abnormal
……
999 | SystemCmd | M3 to DSP system command | [6 empty] | system command
Ninth group for Storage power
1000 | uwSysWorkMode |  | System work mode | 0x00:waiting module |  |  |  | Theworkingmode displayed by the monitoring to the customer is：
|  |  |  | 0x01: Self-test mode, |  |  |  | 0x00: waiting
|  |  |  | optional |  |  |  | module
|  |  |  | 0x02 : |  |  |  | 0x01: Self-test mode,
|  |  |  | Reserved |  |  |  | 0x03:fault module
|  |  |  | 0x03：SysFault module 0x04: Flash module |  |  |  | 0x04:flash
|  |  |  | 0x05 ： |  | module | 0
|  |  |  | PVBATOnline module, |  | 0x05¦0x06¦0x07¦ x08:normal module
0x06 ：
BatOnline module,
0x07 ：
PVOfflineMod e module,
0x08 ：
BatOfflineMo de module,
1001 | Systemfault word0 |  | System fault word0 |  |  | Please refer | to
[6 empty] | thefault description | of
Hybrid
1002 | Systemfault word1 |  | System fault word1
1003 | Systemfault word2 |  | System fault word2
1004 | Systemfault word3 |  | System fault word3
1005 | Systemfault word4 |  | System fault word4
1006 | Systemfault word5 |  | System fault word5
1007 | Systemfault word6 |  | System fault word6
1008 | Systemfault word7 |  | System fault word7
1009 | Pdischarge1 H |  | Discharge power(high) |  | 0.1W
1010 | Pdischarge1 L |  | Discharge power (low) |  | 0.1W
1011 | Pcharge1 H |  | Charge power(high) |  | 0.1W
1012 | Pcharge1 L |  | Charge power (low) |  | 0.1W
1013 | Vbat |  | Battery voltage |  | 0.1V
1014 | SOC |  | State of charge Capacity | 0-100 | 1% | lith/leadacid
1015 | Pactouser R | H | AC power to user H |  | 0.1w
1016 | Pactouser R | L | AC power to user L |  | 0.1w
1017 | Pactouser S | H | Pactouser S H |  | 0.1w
1018 | Pactouser S | L | Pactouser S L |  | 0.1w
1019 | Pactouser T | H | Pactouser T H |  | 0.1w
1020 | Pactouser T | L | Pactouser T H |  | 0.1w
1021 | PactouserTotal H |  | AC power to user total H |  | 0.1w
1022 | PactouserTotal L |  | AC power to user total L |  | 0.1w
1023 | Pac to grid R H |  | AC power to grid H |  | 0.1w | Ac output
1024 | Pac to grid R L |  | AC power to grid L |  | 0.1w
1025 | Pactogrid S H |  |  |  | 0.1w
1026 | Pactogrid S L |  |  |  | 0.1w
1027 |  | Pactogrid T H |  |  |  |  | 0.1w
1028 |  | Pactogrid T L |  |  |  |  | 0.1w
1029 |  | Pactogrid total H |  | AC power to grid total H |  |  | 0.1w
1030 |  | Pactogrid total L |  | AC power to grid total L |  |  | 0.1w
1031 |  | PLocalLoad R H |  | INV power to local load H |  |  | 0.1w
1032 |  | PLocalLoad R L |  | INV power to local load L |  |  | 0.1w
1033 |  | PLocalLoad S H |  |  |  |  | 0.1w
1034 |  | PLocalLoad S L |  |  |  |  | 0.1w
1035 |  | PLocalLoadT H |  |  |  |  | 0.1w
1036 |  | PLocalLoadT L |  |  |  |  | 0.1w
1037 |  | PLocalLoad total H |  | INV power to local load total H |  |  | 0.1w
1038 |  | PLocalLoad total L |  | INV power to local load total |  |  | 0.1w
L
1039 |  | IPM Temperature |  | REC Temperature |  |  | 0.1℃ | No use
1040 |  | Battery |  | Battery Temperature |  |  | 0.1℃ | Lead acid/lithium battery temp
Temperature
1041 |  | SP DSP Status |  | SP state |  |  |  | CHG/DisCHG
1042 |  | SP Bus Volt |  | SP BUS2 Volt |  |  | 0.1V
1043
Power generation data
1044 | Etouser_today H |  | Energy to user today high |  |  | 0.1kWh
1045 | Etouser_today L |  | Energy to user today low |  |  | 0.1kWh
1046 | Etouser_total H |  | Energy to user total high |  |  | 0.1kWh
1047 | Etouser_ total L |  | Energy to user total high |  |  | 0.1kWh
1048 | Etogrid_today H |  | Energy to grid today high |  |  | 0.1kWh
1049 | Etogrid _today L |  | Energy to grid today low |  |  | 0.1kWh
1050 | Etogrid _total H |  | Energy to grid total high |  |  | 0.1kWh
1051 | Etogrid _ total L |  | Energy to grid total high |  |  | 0.1kWh
1052 | Edischarge1_toda |  | Discharge energy1 today |  |  | 0.1kWh
y H
1053 | Edischarge1_toda y L |  | Discharge energy1 today |  |  | 0.1kWh
1054 | Edischarge1_total |  | Total discharge energy1 (high) |  |  | 0.1kWh
H
1055 | Edischarge1_total |  | Total discharge energy1 (low) |  |  | 0.1kWh
L
1056 | Echarge1_today H |  | Charge1 energy today |  |  | 0.1kWh
1057 | Echarge1_today |  | Charge1 energy today |  |  | 0.1kWh
L
1058 | Echarge1_total H |  | Charge1 energy total |  |  | 0.1kWh
1059 | Echarge1_total L |  | Charge1 energy total |  |  | 0.1kWh
1060 |  | ELocalLoad_Today |  |  |  | Local load energy today |  | 0.1kWh
H
1061 |  | ELocalLoad_Today |  |  |  | Local load energy today |  | 0.1kWh
L
1062 |  | ELocalLoad_Total |  |  |  | Local load energy total |  | 0.1kWh
H
1063 |  | ELocalLoad_Total |  |  |  | Local load energy total |  | 0.1kWh
L
1064 |  | dwExportLimitAp parentPower |  |  |  | ExportLimitApparentPower H |  | 0.1kWh | ApparentPower
1065 |  | dwExportLimitAp parentPower |  |  |  | ExportLimitApparentPower L |  | 0.1kWh | ApparentPower
1066 |  | / |  |  |  | / | / | / | reserved
Ups information (offline)
1067 |  | EPS Fac |  |  |  | UPSfrequency | 5000/6000 | 0.01Hz
1068 |  | EPS Vac1 |  |  |  | UPS phase R output voltage | 2300 | 0.1V
1069 |  | EPS Iac1 |  |  |  | UPS phase R output current |  | 0.1A
1070 |  | EPS Pac1 H |  |  |  | UPS phase R output power (H) |  | 0.1VA
1071 |  | EPS Pac1 L |  |  |  | UPS phase R output power (L) |  | 0.1VA
1072 |  | EPS Vac2 |  |  |  | UPS phase S output voltage |  | 0.1V
1073 |  | EPS Iac2 |  |  |  | UPS phase S output current |  | 0.1A | No use
1074 |  | EPS Pac2 H |  |  |  | UPS phase S output power (H) |  | 0.1VA
1075 |  | EPS Pac2 L |  |  |  | UPS phase S output power (L) |  | 0.1VA
1076 |  | EPS Vac3 |  |  |  | UPS phase T output voltage |  | 0.1V
1077 |  | EPS Iac3 |  |  |  | UPS phase T output current |  | 0.1A | No use
1078 |  | EPS Pac3 H |  |  |  | UPS phase T output power (H) |  | 0.1VA
1079 |  | EPS Pac3 L |  |  |  | UPS phase T output power (L) |  | 0.1VA
1080 |  | Loadpercent |  |  |  | Load percent of UPS ouput | 0-100 | 1%
1081 |  | PF |  |  |  | Power factor | 0-2 | 0.1 | Primary Value+1
BMS Infomation
1082 |  |  | BMS_StatusOld |  |  | StatusOld from BMS | Detail information, refer to
1083 |  |  | BMS_Status |  |  | Status from BMS | document:GrowattxxSxx |  | W/R
1084 |  |  | BMS_ErrorOld |  |  | Error info Old from BMS | P ESS Protocol;
1085 |  |  | BMS_Error |  |  | Errorinfomation from BMS
1086 |  |  | BMS_SOC |  |  | SOC from BMS |  |  | R SPH6K
1087 |  |  | BMS_BatteryVol |  |  | Battery voltage from BMS |  |  | R SPH6K
t
1088 |  |  | BMS_BatteryCu |  | r | Battery current from BMS
r
1089 |  |  | BMS_BatteryTe |  |  | Battery temperature from BMS
mp
1090 | BMS_MaxCurr | Max. charge/discharge current from BMS (pylon)
1091 | BMS_GaugeRM | Gauge RM from BMS
1092 | BMS_GaugeFCC | Gauge FCC from BMS
1093 | BMS_FW
1094 | BMS_DeltaVolt | Delta V from BMS
1095 | BMS_CycleCnt | Cycle Count from BMS
1096 | BMS_SOH | SOH from BMS
1097 | BMS_ConstantV | CV voltage from BMS
olt
1098 | BMS_WarnInfoO | Warning info old from BMS
ld
1099 | BMS_WarnInfo | Warning info from BMS
1100 | BMS_GaugeICCu | Gauge IC current from BMS
rr
1101 | BMS_MCUVersi on | MCU Software version from BMS
1102 | BMS_GaugeVers ion | Gauge Version from BMS
1103 | BMS_wGaugeFR | Gauge FR Version L16 from BMS
Version_ L
1104 | BMS_wGaugeFR | Gauge FR Version H16 from BMS
Version_H
1105 | BMS_BMSInfo | BMSInformation from BMS
1106 | BMS_PackInfo | Pack Information from BMS
1107 | BMS_UsingCap | Using Cap from BMS
1108 | uwMaxCellVolt | Maximum single battery voltage |  | 0.001V
1109 | uwMinCellVolt | Lowest single battery voltage |  | 0.001V
1110 | bModuleNum | Battery parallel number |  | 1
1111 |  | Number of batteries |  | 1
1112 | uwMaxVoltCellN o | MaxVoltCellNo |  | 1
1113 | uwMinVoltCellN o | MinVoltCellNo |  | 1
1114 | uwMaxTemprCe | MaxTemprCell_10T |  | 0.1℃
ll_10T
1115 | uwMinTemprCel l_10T | MinTemprCell_10T |  | 0.1℃
1116 | uwMaxTemprCe | MaxVoltTemprCellNo |  | 1
llNo
1117 | uwMinTemprCel | MinVoltTemprCellNo |  | 1
lNo
1118 | Protect pack ID | Faulty Battery Address |  | 1
1119 | MaxSOC | Parallel maximum SOC |  | 1%
1120 | MinSOC | Parallel minimum SOC |  | 1%
1121 | BMS_Error2 | Battery Protection 2 |  | - |  | CAN ID ： 0x323
Byte4~5
1122 | BMS_Error3 | Battery Protection3 |  | - |  | CAN ID ： 0x323
Byte6
1123 | BMS_WarnInfo2 | Battery Warn2 |  | - |  | CAN ID ： 0x323
Byte7
1124 | AC Charge | AC Charge Energy today | kwh |  |  | Energy today
Energy Today H
Ninth group reserved for storage power
1125 | ACCharge | AC Charge Energy today | kwh
Energy TodayL
1126 | AC Charge |  |  |  |  | Energy total
Energy Total H
1127 | ACCharge
Energy Total L
1128 | AC Charge | AC Charge Power | W
Power H
1129 | AC Charge | AC Charge Power | w
Power L
1130 | 70% INV Power | uwGridPower_70_AdjEE_SP | W
adjust
1131 | Extra AC Power to grid_H | Extra inverte AC Power to grid | For SPA connect inverter |  |  | SPA used
High
1132 | Extra AC Power to grid_L | Extrainverte AC Power to grid Low |  |  |  | SPA used
1133 | Eextra_today H | Extra inverter PowerTOUser_Extra today (high) | R |  | 0.1kWh | SPA used
1134 | Eextra_today L | Extra inverter PowerTOUser_Extra today (low) | R |  | 0.1kWh | SPA used
1135 | Eextra_total H | Extra inverter PowerTOUser_Extra total(high) |  |  | 0.1kWh | SPA used
1136 | Eextra_total L | Extra inverter PowerTOUser_Extra total(low) |  |  | 0.1kWh | SPA used
1137 | Esystem_today | System electric energy today H |  |  | 0.1kWh | SPA used
| H |  |  |  |  | System electric energy today H
1138 | Esystem_ today |  |  | System electric energy today L |  |  |  | 0.1kWh |  |  | SPA used
| L | [9 empty] | System electric energy today L
1139 | Esystem_total H |  |  | System electric energy total H |  |  |  | 0.1kWh |  |  | SPA used
System electric energy total H
1140 | Esystem_ total L |  |  | System electric energy total L |  |  |  | 0.1kWh |  |  | SPA used
System electric energy total L
1141 | Eself_today H |  |  | self electric energy today H |  |  |  | 0.1kWh |  |  | self electric energy today H
1142 | Eself_ today L |  |  | self electric energy today L |  |  |  | 0.1kWh |  |  | self electric energy today L
1143 | Eself_total H |  |  | self electric energy total H |  |  |  | 0.1kWh |  |  | self electric energy total H
1144 | Eself_ total L |  |  | self electric energy total L |  |  |  | 0.1kWh |  |  | self electric
energy total L
1145 | PSystem H |  |  | System power H |  |  |  | 0.1w |  |  | System power H
1146 | PSystem L |  |  | System power L |  |  |  | 0.1w |  |  | System power L
1147 | PSelf H |  |  | self power H |  |  |  | 0.1w |  |  | self power H
1148 | PSelf L |  |  | self power L |  |  |  | 0.1w |  |  | self power L
1149 | EPVAll_Today H |  |  | PV electric energy today H
1150 | EPVAll_Today L |  |  | PV electric | energy today L
1151 | AcDischarge |  |  | Discharge number | power pack | serial | R | /
PackSn
1152 |  | Accdischarge power_H |  | Cumulative | discharge power high |  | R |  | 0.1 | kWH
16-bit byte
1153 |  | Accdischarge power_L |  | Cumulative | discharge power low |  | R |  | 0.1 | kWH
16-bit byte
1154 | AccCharge |  |  | charge power pack serial number |  |  | R | /
PackSn
1155 |  | AccCharge power_H |  | Cumulative charge power |  | high |  | R |  | 0.1 | kWH
16-bit byte
1156 |  | AccCharge power_L |  | Cumulative charge power |  | low |  | R |  | 0.1 | kWH
16-bit byte
1157 |  | FirstBattFaultSn |  |  | FirstBattFaultSn |  |  | R | /
1158 |  | Second |  |  | Second |  |  | R | /
|  | BattFaultSn |  |  | BattFaultSn
1159 |  | Third |  |  | Third |  |  | R | /
|  | BattFaultSn |  |  | BattFaultSn
1160 |  | Fourth |  |  | Fourth |  |  | R | /
|  | BattFaultSn |  |  | BattFaultSn
1161 |  | Battery history fault code 1 |  |  | Battery history fault code 1 |  |  | R | /
1162 |  | Battery history fault code 2 |  |  | Battery history fault code 2 |  |  | R | /
1163 |  | Battery history fault code 3 |  |  | Battery history fault code 3 |  |  | R | /
1164 |  | Battery history fault code 4 |  |  | Battery history fault code 4 |  |  | R | /
1165 |  | Battery history fault code 5 |  |  | Battery history fault code 5 |  | R | /
1166 |  | Battery history fault code 6 |  |  | Battery history fault code 6 |  | R | /
1167 |  | Battery history fault code 7 |  |  | Battery history fault code 7 |  | R | /
1168 |  | Battery history fault code 8 |  |  | Battery history fault code 8 |  | R | /
1169 |  | Number of battery codes |  | Number of battery codes PACK number + BIC forward and |  |  | R | /
reverse codes
1170
…… | / |  |  | / |  |  | / | / | reversed
1199 | NewEPowerCalc |  |  | Intelligent reading is used to identify software compatibility features |  |  |  |  | 0 ： Old energy
| Flag | [7 empty] | calculation；
1 ： new energy
calculation
1200 | MaxCellVolt |  |  | Maximum cell voltage |  |  | R | 0.001V
1201 | MinCellVolt |  |  | Minimum cell voltage |  |  | R | 0.001V
1202 | ModuleNum |  |  | Number of Battery modules |  |  | R | /
1203 | TotalCellNum |  |  | Total number of cells |  |  | R | /
1204 | MaxVoltCellNo |  |  | MaxVoltCellNo |  |  | R | /
1205 | MinVoltCellNo |  |  | MinVoltCellNo |  |  | R | /
1206 | MaxTemprCell_ |  |  | MaxTemprCell_10T |  |  | R | 0.1℃
10T
1207 | MinTemprCell_1 |  |  | MinTemprCell_10T |  |  | R | 0.1℃
0T
1208 |  | MaxTemprCellN o | MaxTemprCellNo |  | R |  | /
1209 |  | MinTemprCellN o | MinTemprCellNo |  | R |  | /
1210 |  | ProtectPackID | Fault Pack ID |  | R |  | /
1211 |  | MaxSOC | Parallel maximum SOC |  | R |  | 1%
1212 |  | MinSOC | Parallel minimum SOC |  | R |  | 1%
1213 |  | BatProtect1Add | BatProtect1Add |  | R |  | /
1214 |  | BatProtect2Add | BatProtect2Add |  | R |  | /
1215 |  | BatWarn1Add | BatWarn1Add |  | R |  | /
1216 |  | BMS_HighestSof tVersion | BMS_HighestSoftVersion |  | R |  | /
1217 |  | BMS_Hardware | BMS_HardwareVersion |  | R |  | /
Version
1218 |  | BMS_RequestTy pe | BMS_RequestType |  | R |  | /
…… |  | / | / |  | / |  | / |  | reversed
1248 |  | bKeyAgingTestO kFlag | Success sign of key detection before aging | [5 empty] | 1：Finished test
0 ： test not
completed
1249 |  | / | / |  | / |  | / |  | reversed
thirteen group for Storage power’s SPA
2000 |  | Inverter Status | Inverter run state |  |  | 0:waiting, |  |  |  | SPA
1:normal,
3:fault
…… |  | reversed
2035 |  | Pac H | Output power (high) |  |  |  |  | 0.1W |  | SPA
2036 |  | Pac L | Output power (low) |  |  |  |  | 0.1W |  | SPA
2037 |  | Fac | Grid frequency |  |  |  |  | 0.01Hz |  | SPA
2038 |  | Vac1 | Three/single phase grid voltage |  |  |  |  | 0.1V |  | SPA
2039 |  | Iac1 | Three/single phase grid output current |  |  |  |  | 0.1A |  | SPA
2040 |  | Pac1 H | Three/single phase grid output watt |  |  |  |  | 0.1VA |  | SPA
VA (high)
2041 |  | Pac1 L | Three/single phase grid output watt |  |  |  |  | 0.1VA |  | SPA
VA(low)
…… |  | reversed
2053 |  | Eac today H | Today generate energy (high) |  |  |  |  | 0.1kWH |  | SPA
2054 |  | Eac today L | Today generate energy (low) |  |  |  |  | 0.1kWH |  | SPA
2055 | Eac total H | Total generate energy (high) |  | 0.1kWH | SPA
2056 | Eac total L | Total generate energy (low) |  | 0.1kWH | SPA
2057 | Time total H | Work time total (high) |  | 0.5s | SPA
2058 | Time total L | Work time total (low) |  | 0.5s | SPA
…… | reversed
2093 | Temp1 | Inverter temperature |  | 0.1C | SPA
2094 | Temp2 | The inside IPM in inverter Temperature |  | 0.1C | SPA
2095 | Temp3 | Boost temperature |  | 0.1C | SPA
2096 | Temp4 |  |  |  | reserved
2097 | uwBatVolt_DSP | BatVolt_DSP |  | 0.1V | BatVolt(DSP)
2098 | P Bus Voltage | P Bus inside Voltage |  | 0.1V | SPA
2099 | N Bus Voltage | N Bus inside Voltage |  | 0.1V | SPA
2100 | RemoteCtrlEn | / | 0.Load First | / | Remote setup enable
1.BatFirst
2101 | RemoteCtrlPow er | / | 2.Grid | / | Remotely set power
2102 | Extra AC Power to grid_H | Extra inverte AC Power to grid High | For SPA connect inverter |  | SPA used
2103 | Extra AC Power to grid_L | Extrainverte AC Power to grid Low |  |  | SPA used
2104 | Eextra_today H | Extra inverter PowerTOUser_Extra today (high) | R | 0.1kWh | SPA used
2105 | Eextra_today L | Extra inverter PowerTOUser_Extra today (low) | R | 0.1kWh | SPA used
2106 | Eextra_total H | Extra inverter |  | 0.1kWh | SPA used
PowerTOUser_Extratotal(high)
2107 | Eextra_total L | Extra inverter PowerTOUser_Extra total(low) |  | 0.1kWh | SPA used
2108 | Esystem_today | System electric energy today H |  | 0.1kWh | SPA used
| H |  |  |  | System electric energy today H
2109 | Esystem_ today | System electric energy today L |  | 0.1kWh | SPA used
| L |  |  |  | System electric energy today L
2110 | Esystem_total H | System electric energy total H |  | 0.1kWh | SPA used
System
electric
energy total
H
2111 | Esystem_ total L | System electric energy total L |  | 0.1kWh |  | SPA used
System electric
energy total
L
2112 | EACharge_Today | ACCharge energy today |  | 0.1kwh |  | Storage
| _H |  |  |  |  | Power
2113 | EACharge_Today | ACCharge energy today |  | 0.1kwh |  | Storage
| _L |  |  |  |  | Power
2114 | EACharge_Total | ACCharge energy total |  | 0.1kwh |  | Storage
| _H |  |  |  |  | Power
2115 | EACharge_Total | ACCharge energy total |  | 0.1kwh |  | Storage
| _L |  |  |  |  | Power
2116 | AC charge | Grid power to local load |  | 0.1kwh |  | Storage
| Power_H |  |  |  |  | Power
2117 | AC charge | Grid power to local load |  | 0.1kwh |  | Storage
| Power_L |  |  |  |  | Power
2118 | Priority | 0:Load First |  |  |  | Storage
|  | 1:Battery First |  |  |  | Power
2:Grid First
2119 | Battery Type | 0：Lead-acid |  |  |  | Storage
|  | 1：Lithium battery |  |  |  | Power
2120 | AutoProofreadC | Aging mode |  |  |  | Storage
| MD |  |  |  |  | Power
… | reserved |  |  |  |  | reserved
2124 | reserved |  |  |  |  | reserved
Use for TL-X and TL-XH
3000 | Inverter Status | Inverter run state
High 8 bits mode (specific mode)
0: Waiting module
1: Self-test mode, optional
2: Reserved
3：SysFault module
4: Flash module
5：PVBATOnline module:
6：BatOnline module
7：PVOfflineMode
8：BatOfflineMode
The lower 8 bits indicate the machine status (web page display)
0: StandbyStatus;
1: NormalStatus;
3: FaultStatus
4：FlashStatus;
3001 | Ppv H | PV total power |  | 0.1W
3002 | Ppv L
3003 | Vpv1 | PV1 voltage |  | 0.1V
3004 | Ipv1 | PV1 input current |  | 0.1A
3005 | Ppv1 H | PV1 power |  | 0.1W
3006 | Ppv1 L
3007 | Vpv2 | PV2 voltage |  | 0.1V
3008 | Ipv2 | PV2 input current |  | 0.1A
3009 | Ppv2 H | PV2 power |  | 0.1W
3010 | Ppv2 L
3011 | Vpv3 | PV3 voltage |  | 0.1V
3012 | Ipv3 | PV3 input current |  | 0.1A
3013 | Ppv3 H | PV3 power |  | 0.1W
3014 | Ppv3 L
3015 | Vpv4 | PV4 voltage
3016 | Ipv4 | PV4 input current
3017 | Ppv4H | PV4 power
3018 | Ppv4L
3019 | Psys H | System output power |  | 0.1W
3020 | Psys L
3021 | Qac H | reactive power |  | 0.1Var
3022 | Qac L
3023 | Pac H | Output power |  | 0.1W | Output power
3024 | Pac L
3025 | Fac | Grid frequency |  | 0.01Hz | Grid frequency
3026 | Vac1 | Three/single phase grid voltage |  | 0.1V | Three/single
phase grid
voltage
3027 | Iac1 | Three/single phase grid output current |  | 0.1A | Three/single
phase grid output current
3028 | Pac1 H | Three/single phase grid output watt |  | 0.1VA | Three/single phase grid output watt
3029 | Pac1 L | VA |  |  | VA
3030 | Vac2 | Three phase grid voltage |  | 0.1V | Three phase grid voltage
3031 | Iac2 | Three phase grid output current |  | 0.1A | Three phase grid output current
3032 | Pac2 H | Three phase grid output power |  | 0.1VA | Three phase grid output power
3033 | Pac2 L
3034 | Vac3 | Three phase grid voltage |  | 0.1V | Three phase grid voltage
3035 | Iac3 | Three phase grid output current |  | 0.1A | Three phase grid output current
3036 | Pac3 H | Three phase grid output power |  | 0.1VA | Three phase grid output power
3037 | Pac3 L
3038 | Vac_RS | Three phase grid voltage |  | 0.1V
3039 | Vac_ST | Three phase grid voltage |  | 0.1V
3040 | Vac_TR | Three phase grid voltage |  | 0.1V
3041 | Ptouser total H | Total forward power |  | 0.1W | Total forward power
3042 | Ptouser total L
3043 | Ptogrid total H | Total reverse power |  | 0.1W | Total reverse power
3044 | Ptogrid total L
3045 | Ptoload total H | Total load power |  | 0.1W | Total load power
3046 | Ptoload total L
3047 | Time total H | Work time total |  | 0.5s
3048 | Time total L
3049 | Eac today H | Today generate energy |  | 0.1kWh | Today generate energy
3050 | Eac today L
3051 | Eac total H | Total generate energy |  | 0.1kWh | Total generate
3052 | Eac total L
energy
3053 | Epv_total H | PV energy total |  | 0.1kWh | PV energy
3054 | Epv_total L |  |  |  | total
3055 | Epv1_today H | PV1 energy today |  | 0.1kWh
3056 | Epv1_today L
3057 | Epv1_total H | PV1 energy total |  | 0.1kWh
3058 | Epv1_total L
3059 | Epv2_today H | PV2 energy today |  | 0.1kWh
3060 | Epv2_today L
3061 | Epv2_total H | PV2 energy total |  | 0.1kWh
3062 | Epv2_total L
3063 | Epv3_today H | PV3 energy today |  | 0.1kWh
3064 | Epv3_today L
3065 | Epv3_total H | PV3 energy total |  | 0.1kWh
3066 | Epv3_total L
3067 | Etouser_today H | Today energy to user |  | 0.1kWh | Today energy to user
3068 | Etouser_today L
3069 | Etouser_total H | Total energy to user |  | 0.1kWh | Total energy to user
3070 | Etouser_total L
3071 | Etogrid_today H | Today energy to grid |  | 0.1kWh | Today energy to grid
3072 | Etogrid_today L
3073 | Etogrid_total H | Total energy to grid |  | 0.1kWh | Total energy to grid
3074 | Etogrid_total L
3075 | Eload_today H | Today energy of user load |  | 0.1kWh | Today energy of user load
3076 | Eload_today L
3077 | Eload_total H | Total energy of user load |  | 0.1kWh | Total energy of user load
3078 | Eload_total L
3079 | Epv4_today H | PV4 energy today |  | 0.1kWh
3080 | Epv4_today L
3081 | Epv4_total H | PV4 energy total |  | 0.1kWh
3082 | Epv4_total L
3083 | Epv_today H | PV energy today |  | 0.1kWh
3084 | Epv_today L
3085 | Reserved
3086 | DeratingMode | DeratingMode |  |  | 0:cNOTDerate 1:cPVHighDer ate
2: cPowerCon stantDerate
3: cGridVHigh
Derate 4:cFreqHighD erate
5:cDcSoureM odeDerate 6:cInvTemprD erate 7:cActivePow erOrder
8:cLoadSpeed Process
9:cOverBack byTime
10:cInternalT emprDerate 11:cOutTemp rDerate 12:cLineImpe
CalcDerate 13: cParallelA ntiBackflowD erate
14:cLocalAnti BackflowDera te
15:cBdcLoadP riDerate
16:cChkCTErr
Derate
3087 | ISO | PV ISO value |  | 1KΩ
3088 | DCI_R | R DCI Curr |  | 0.1mA
3089 | DCI_S | S DCI Curr |  | 0.1mA
3090 | DCI_T | T DCI Curr |  | 0.1mA
3091 | GFCI | GFCI Curr |  | 1mA
3092 | Bus Voltage | total bus voltage |  | 0.1V
3093 | Temp1 | Inverter temperature |  | 0.1℃
3094 | Temp2 | The inside IPM in inverter temperature |  | 0.1℃
3095 | Temp3 | Boost temperature |  | 0.1℃
3096 | Temp4 | Reserved |  | 0.1℃
3097 | Temp5 | Commmunication broad temperature |  | 0.1℃
3098 | P Bus Voltage | P Bus inside Voltage |  | 0.1V
3099 | N Bus Voltage | N Bus inside Voltage |  | 0.1V
3100 | IPF | Inverter output PF now |  |  | 0-20000
3101 | RealOPPercent | Real Output power Percent |  | 1% | 1~100
3102 | OPFullwatt H | Output Maxpower Limited |  | 0.1W | Output
Maxpower
3103 | OPFullwatt L |  |  |  | Limited
3104 | StandbyFlag | Inverter standby flag |  | bitfield | bit0:turn | off
[5 empty] | Order； bit1:PV Low bit2:AC Volt/Freq out of scope bit3~bit7 Reserved | ；
；
：
3105 | Fault Maincode | Inverter fault maincode
3106 | Warn Maincode | Inverter Warning maincode
3107 | Fault Subcode | Inverter fault subcode |  | bitfield
3108 | Warn Subcode | Inverter Warning subcode |  | bitfield
3109 |  |  |  | bitfield
3110 |  |  |  | bitfield
3111 | uwPresentFFTVa lue [CHANNEL_A | PresentFFTValue [CHANNEL_A] |  | bitfield
]
3112 | bAfciStatus | AFCI Status |  |  | 0 ： waiting
state
1：self-check 2：Detection of arcing
state
3：fault state
4 ： update
state
3113 | uwStrength[CHA | AFCI Strength[CHANNEL_A]
NNEL_A]
3114 | uwSelfCheckVal ue[CHANNEL_A] | AFCI SelfCheck[CHANNEL_A]
3115 | inv start delay time | inv start delay time |  | 1S | inv start delay time
3116 | Reserved
3117 | Reserved
3118 | BDC_OnOffState | BDC connect state |  |  | 0:No BDC
Connect 1:BDC1
Connect 2:BDC2
Connect
3:BDC1+BDC2
Connect
3119 | DryContactState | Current status of DryContact |  |  | Current
status of
DryContact
0: turn off;
1: turn on;
3120 | Reserved
3121 | Pself H | self-use power |  | 0.1W
3122 | Pself L
3123 | Esys_today H | System energy today |  | 0.1kwh
3124 | Esys_today L
3125 | Edischr_today H | Today discharge energy |  | 0.1kWh | Today discharge energy
3126 | Edischr_today L
3127 | Edischr_total H | Total discharge energy |  | 0.1kWh | Total discharge energy
3128 | Edischr_total L
3129 | Echr_today H | Charge energy today |  | 0.1kWh | Charge energy today
3130 | Echr_today L
3131 | Echr_total H | Charge energy total |  | 0.1kWh | Charge energy total
3132 | Echr_total L
3133 | Eacchr_today H | Today energy of AC charge |  | 0.1kWh | Today energy of AC charge
3134 | Eacchr_today L
3135 | Eacchr_total H | Total energy of AC charge |  | 0.1kWh | Total energy of AC charge
3136 | Eacchr_total L
3137 | Esys_total H
3138 | Esys_total L | Total energy of system output \ |  | 0.1kWh
3139 | Eself_today H | Today energy of Self output |  | 0.1kWh
3140 | Eself_today L
3141 | Eself_total H | Total energy of Self output |  | 0.1kwh
3142 | Eself_ total L
3143 | Reserved
3144 | Priority | Word Mode |  |  | 0 LoadFirst 1
BatteryFirs t
2 GridFirst
3145 | EPS Fac | UPS frequency |  | 0.01Hz
3146 | EPS Vac1 | UPS phase R output voltage |  | 0.1V
3147 | EPS Iac1 | UPS phase R output current |  | 0.1A
3148 | EPS Pac1 H | UPS phase R output power |  | 0.1VA
3149 | EPS Pac1 L
3150 | EPS Vac2 | UPS phase S output voltage |  | 0.1V
3151 | EPS Iac2 | UPS phase S output current |  | 0.1A
3152 | EPS Pac2 H | UPS phase S output power |  | 0.1VA
3153 | EPS Pac2 L
3154 | EPS Vac3 | UPS phase T output voltage |  | 0.1V
3155 | EPS Iac3 | UPS phase T output current |  | 0.1A
3156 | EPS Pac3 H | UPS phase T output power |  | 0.1VA
3157 | EPS Pac3 L
3158 | EPS Pac H | UPS output power |  | 0.1VA
3159 | EPS Pac L
3160 | Loadpercent | Load percent of UPS ouput |  | 0.1%
3161 | PF | Power factor |  | 0.1
3162 | DCV | DC voltage |  | 1mV
3163 | Reserved
3164 | NewBdcFlag | Whether to parse BDC data separately |  |  | 0: Don't need
1：need
3165 | BDCDeratingMo de | BDCDeratingMode：
0: Normal, unrestricted
1：Standby or fault
2：Maximum battery current limit
(discharge)
3：Battery discharge Enable (Discharge)
4：High bus discharge derating
(discharge)
5：High temperature discharge derating (discharge)
6：System warning No discharge
(discharge)
7-15 Reserved (Discharge)
16：Maximum charging current of battery (charging)
17：High Temperature (LLC and
Buckboost) (Charging)
18：Final soft charge
19：SOC setting limits (charging)
20：Battery low temperature (charging)
21：High bus voltage (charging)
22：Battery SOC (charging)
23: Need to charge (charge）
24: System warning not charging
(charging)
25-29：Reserve (charge)
3166 | SysState_Mode | System work State and mode The upper 8 bits indicate the mode; |  |  | BDC1
0：No charge and discharge；
1：charge；
2：Discharge；
The lower 8 bits represent the status;
0: StandbyStatus;
1: NormalStatus;
2: FaultStatus
3：FlashStatus;
3167 | FaultCode | Storge device fault code
3168 | WarnCode | Storge device warning code
3169 | Vbat | Battery voltage |  | 0.01V
3170 | Ibat | Battery current |  | 0.1A
3171 | SOC | State of charge Capacity |  | 1%
3172 | Vbus1 | Total BUS voltage |  | 0.1V
3173 | Vbus2 | On the BUS voltage |  | 0.1V
3174 | Ibb | BUCK-BOOST Current |  | 0.1A
3175 | Illc | LLC Current |  | 0.1A
3176 | TempA | Temperture A |  | 0.1℃
3177 | TempB | Temperture B |  | 0.1℃
3178 | Pdischr H | Discharge power |  | 0.1W
3179 | Pdischr L
3180 | Pchr H | Charge power |  | 0.1W
3181 | Pchr L
3182 | Edischr_total H | Discharge total energy of storge device |  | 0.1kWh
3183 | Edischr_total L
3184 | Echr_total H | Charge total energy of storge device |  | 0.1kWh
3185 | Echr_total L
3186 | Reserved | Reserved
3187 | BDC1_Flag | BDC mark (charge and discharge, fault alarm code)
Bit0: ChargeEn; BDC allows charging Bit1: DischargeEn; BDC allows discharge
Bit2~7: Resvd; reserved Bit8~11: WarnSubCode; BDC sub-warning code
Bit12~15: FaultSubCode; BDC sub-error code
3188 | Vbus2 | Lower BUS voltage |  | 0.1V
3189 | BmsMaxVoltCell | BmsMaxVoltCellNo
No
3190 | BmsMinVoltCell | BmsMinVoltCellNo
No
3191 | BmsBatteryAvgT emp | BmsBatteryAvgTemp
3192 | BmsMaxCellTem p | BmsMaxCellTemp |  | 0.1°C
3193 | BmsBatteryAvgT emp | BmsBatteryAvgTemp |  | 0.1°C
3194 | BmsMaxCellTem p | BmsMaxCellTemp
3195 | BmsBatteryAvgT emp | BmsBatteryAvgTemp
3196 | BmsMaxSOC | BmsMaxSOC |  | 1%
3197 | BmsMinSOC | BmsMinSOC |  | 1%
3198 | ParallelBatteryN | ParallelBatteryNum
um
3199 | BmsDerateReas on | BmsDerateReason
3200 | BmsGaugeFCC | BmsGaugeFCC（Ah）
（Ah）
3201 | BmsGaugeRM | BmsGaugeRM（Ah）
（Ah）
3202 | BmsError | BMS Protect1
3203 | BmsWarn | BMSWarn1
3204 | BmsFault | BMS Fault1
3205 | BmsFault2 | BMS Fault2
3206 | Reserved
3207 | Reserved
3208 | Reserved
3209 | Reserved
3210 | BatIsoStatus | Battery ISO detection status |  |  | 0：Not
detected
1：Detection completed
3211 | BattNeedCharge | battery work request |  | bit0:1： Prohibit chargin g，0：
| RequestFlag |  |  | Allow the chargin g bit1:1： Enable strong charge，
0：
disable strong charge bit2:1： Enable strong charge2
0：
disable strong charge
2
bit8:1: Dischar ge is prohibit
ed， 0：
allow discharg e bit9:1： Turn on power
reductio
n 0：
turn off power
reductio
n；
3212 | BMS_Status | battery working status | R |  | 0: dormancy
1:Charge
2:Discharge
3:free
4:standby
5:Soft start
6:fault
7:update
3213 | BmsError2 | BMS Protect2 | R | 1
3214 | BmsWarn2 | BMS Warn2 | R | 1
3215 | BMS_SOC | BMS SOC | R | 1%
3216 | BMS_BatteryVol | BMS BatteryVolt | R | 0.01V
t
3217 | BMS_BatteryCur | BMS BatteryCurr | R | 0.01A
r
3218 | BMS_BatteryTe | battery cell maximum temperature | R | 0.1℃
mp
3219 | BMS_MaxCurr | Maximum charging current | R | 0.01A
3220 | BMS_MaxDischr | Maximum discharge current | R | 0.01A
Curr
3221 | BMS_CycleCnt | BMSCycleCnt | R | 1
3222 | BMS_SOH | BMS SOH | R | 1
3223 | BMS_ChargeVol | Battery charging voltage limit value | R | 0.01V
tLimit
3224 | BMS_Discharge | Battery discharge voltage limit value
VoltLimit
3225 | Bms Warn3 | BMS Warn 3 | R | 1
3226 | Bms Error3 | BMS Protect3 | R | 1
3227 | Reserved
3228 | Reserved
3229 | Reserved
3230 | BMSSingleVoltM ax | BMS Battery SingleVoltMax | R | 0.001V
3231 | BMSSingleVoltM | BMS Battery SingleVoltMin | R | 0.001V
in
3232 | BatLoadVolt | Battery LoadVolt | R | 0.01V | [0，650.00]
3233
3234 | Debug data1 | Debug data1 | R
3235 | Debug data2 | Debug data2 | R
3236 | Debug data3 | Debug data3 | R
3237 | Debug data4 | Debug data4 | R
3238 | Debug data5 | Debug data5 | R
3239 | Debug data6 | Debug data6 | R
3240 | Debug data7 | Debug data7 | R
3241 | Debug data8 | Debug data8 | R
3242 | Debug data9 | Debug data9 | R
3243 | Debug data10 | Debug data10 | R
3244 | Debug data10 | Debug data10 | R
3245 | Debug data12 | Debug data12 | R
3246 | Debug data13 | Debug data13 | R
3247 | Debug data14 | Debug data14 | R
3248 | Debug data15 | Debug data15 | R
3249 | Debug data16 | Debug data16 | R
3250 | Pex1H | PV inverter 1 output power H | R | 0.1W
3251 | Pex1L | PV inverter 1 output power L | R | 0.1W
3252 | Pex2H | PV inverter 2 output power H | R | 0.1W
3253 | Pex2L | PV inverter 2 output power L | R | 0.1W
3254 | Eex1TodayH | PV inverter 1 energy Today H | R | 0.1kWh
3255 | Eex1TodayL | PV inverter 1 energy Today L | R | 0.1kWh
3256 | Eex2TodayH | PV inverter 2 energy Today H | R | 0.1kWh
3257 | Eex2TodayL | PV inverter 2 energy Today L | R | 0.1kWh
3258 | Eex1TotalH | PV inverter 1 energy Total H | R | 0.1kWh
3259 | Eex1TotalL | PV inverter 1 energy Total L | R | 0.1kWh
3260 | Eex2TotalH | PV inverter 2 energy Total H | R | 0.1kWh
3261 | Eex2TotalL | PV inverter 2 energy Total L | R | 0.1kWh
3262 | uwBatNo | battery pack number | R |  | BDC reports are updated every 15
minutes
3263 | BatSerialNum1 | Battery pack serial numberSN[0]SN[1] | R |  | BDC reports are updated | 15
3264 | BatSerialNum2 | Battery pack serial numberSN[2]SN[3] | R |  | every minutes
3265 | BatSerialNum3 | Battery pack serial numberSN[4]SN[5] | R
3266 | BatSerialNum4 | Battery pack serial numberSN[6]SN[7] | R
3267 | BatSerialNum5 | Battery pack serial numberSN[8]SN[9] | R
3268 | BatSerialNum6 | Battery pack serial numberSN[10]SN[11] | R
3269 | BatSerialNum7 | Battery pack serial numberSN[12]SN[13] | R
3270 | BatSerialNum8 | Battery pack serial numberSN[14]SN[15] | R
3271- | Reserve | Reserve
3279
3280 | bClrTodayDataFl ag | Clear day data flag | R |  | Data of | the day
current
[5 empty] | that server | the
determines
whether to clear.
0:not cleared.
1: Clear.
BDC and BMS information (support up to 10 PARALLEL BDCS)
4000- | 1 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4107
4108- | 2 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4215
…… |  | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4864- | 9 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4971
4972- | 10 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
5079
5 Set address
| Refer to the Inverter user manual. | Always is :
Knock the pv inverter to let the lcd display to the “COM Addr: xxx”, then double knock, if displays “Move”, you should another double knock, until it displays a address number, then you can give a single knock to change the address, this address will be remembered when the lcd backlight off.
6 Notice
1) It can drive mostly 32 pv inverters for one rs485 comport.
2) There are only read input and hold registers commands even the newest version.
3) App user could only care the input register.
4)
App user could not care the holding registers.
5) Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing the other registers;