Growatt Inverter Modbus RTU Protocol_II

V1.05

2018-04-19

Growatt New Energy CO.,LTD

| No. | Version | Date | Notice | Signature |
| --- | --- | --- | --- | --- |
| 1 | V1.00 | 2017-3-27 | The first version | May |
| 2 | V1.01 | 2017-4-28 | Modify max data length to 125 words. Add Input reg50-52 for line voltage | May |
| 3 | V1.02 | 2017-7-18 | Add SP storage and offline inverter message Modify Input reg. First and Second group sequence Modify Holding register First group sequence Modigy stringPID fault code and warning code Modify fifth and sixth group for Gridfault record | May |
| 4 | V1.03 | 2017-8-2 | Modify Hybrid Abnoram/Fault/warning bit definition | Ericxiong |
| 5 | V1.04 | 2018-3-29 | Add Inputing178,179,180,181 for Warning Value1,Warning Value2,Warning Value3 and FaultCode Add Holding240 for aging Check Step Add Inputing112 for INV warn code Add Inputing113 for real Power Percent Add Inputing114 for inv start delay time Add Inputing115 for INV All Fault Code Add holding267-298 for DSP debugdata address Add Inputing182-197 for DSP debugdata value Add Inputing198 for USB Aging Test OK flag Add Inputing199 for USB Flash Aging Test OK flag Add Inputing200 for ISO check value Add holding299 for Active Over load Enable Add Inputing 201-203 for R、S、T DCI Current Add Inputing204 for PID Bus Volt Add Inputing205 for GFCI Curr Add Inputing 206-227 for APF/SVG information Add holding 300 for SVG/APF mode |  |
| 6 | V1.05 | 2018-6-28 | Add InputingReg 525~529 for Setting up GPRS IP Address Add HodlingReg 90 as the step to set up GPRS IP Address | huo.zhao |
| 7 | V1.06 | 2018.7.5 | Add HoldingReg 301 for BDEW LVRT K Factor | Yimin.Yang |  |

V1.00  2017-03-17:

First version

V1.01 2017-4-28

Modify max data length to 125 words. Add Inputreg 50-52 for line voltage

V1.05 2018-6-28

Add InputingReg 525~529 for Setting up GPRS IP Address

Add HodlingReg 90 as the step to set up GPRS IP Address

catalog

- Data format ............................................................................................................................ 4

- Command Format ................................................................................................................... 4

- Device Message Transmission Mode / Framing ..................................................................... 7

- Register map ........................................................................................................................... 8

  - Holding Reg ...................................................................................................................... 8

  - Input Reg ....................................................................................................................... 25

- Set address ........................................................................................................................... 54

- Notice ................................................................................................................................... 55

# 1 Data format

Valid slave device addresses are in the range of 0 – 254 decimal.

The individual slave devices are assigned addresses in the range of 1 – 254.

0 is the broadcast address

It is 16bits (two bytes) unsigned integer for each holding and input register;

# 2 Command Format

Function 3 Read holding register

Response Error:

11 0x80|0x03 Errornum CRC  (Errornum as a byte)

Function 4 Read input  register

Response Error:

11 0x80|0x04 Errornum CRC  (Errornum as a byte)

Function 6 Preset single register

Response Error:

11 0x80|0x06 Errornum CRC  (Errornum as a byte)

Function 16 Preset multiple register

Response Error:

11 0x80|0x10 Errornum CRC  (Errornum as a byte)

# 3 Device Message Transmission Mode / Framing

RTU Mode

When controllers are setup to communicate on a Modbus network using RTU (Remote Terminal Unit) mode, each 8–bit byte in a message contains two 4–bit hexadecimal characters. Each message must be transmitted in a continuous stream.

The format for each byte in RTU mode is:

Coding System: 8–bit binary, hexadecimal 0–9, A–F

Two hexadecimal characters contained in each

8–bit field of the message

Bits per Byte:

1 start bit

8 data bits, least significant bit sent first

None parity

1 stop bit

Error Check Field: Cyclical Redundancy Check (CRC)

The baud rate of the transmission is:

Default Baud Rate: 9600 bps

Can be set through hold register 22

Minimum CMD period (RS485 Time out): 850ms.

Wait for minimum 850ms to send a new CMD after last CMD. Suggestion is 1s;

Maximum Data Length Define:

Maximum read data length is 125 words in read command;

Maximum update data length is 125 words in preset command;

Note:

Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing other registers;

| 09; Fw version H; Firmware version (high); ASCII. 10; Fw version M; Firmware version (middle). 11; Fw version L; Firmware version (low). 12; Fw version2 H; Control Firmware version (high); ASCII. 13; Fw version2 M; Control Firmware version (middle). 14; Fw version2 L; Control Firmware version (low). 15; LCD language; LCD language; W; 0-5. 16; CountrySelec ted; Country Selected or not; W; 0: need to select; 1: have selected. 17; Vpv start; Input start voltage; W; 0.1V. 18; Time start; Start time; W; 1s. 19; RestartDelay Time; Restart Delay Time after fault back;; W; 1s. 20; wPowerStart Slope; Power start slope; W; 1-1000; 0.1%. 21; wPowerResta rtSlopeEE; Power restart slope; W; 1-1000; 0.1%. 22; wSelectBaud rate; Select communication baudrate 0: 9600bps 1:38400bps; W; 0-1; 0. 23; Serial NO. 5; Serial number 5; ASCII. 24; Serial No. 4; Serial number 4. 25; Serial No. 3; Serial number 3. 26; Serial No. 2; Serial number 2. 27; Serial No. 1; Serial number 1. 28; Module H; Inverter Module (high); &*5. 29; Module L; Inverter Module (low); &*5. 30; Com Address; Communicate address; W; 1-254; 1. 31; FlashStart; Update firmware; W; 1. 32; Reset User Info; Reset User Information; W; 0x0001. 33; Reset to factory; Reset to factory; W; 0x0001. 34; Manufacture r Info 8; Manufacturer information (high); ASCII. |  |
| --- | --- |

| 35; Manufacture r Info 7; Manufacturer information (middle). 36; Manufacture r Info 6; Manufacturer information (low). 37; Manufacture r Info 5; Manufacturer information (high). 38; Manufacture r Info 4; Manufacturer information (middle). 39; Manufacture r Info3; Manufacturer information (low). 40; Manufacture r Info 2; Manufacturer information (low). 41; Manufacture r Info 1; Manufacturer information (high). 42; reserved; reserved. 43; DTC; Device Type Code; &*6. 44; TP; Input tracker num and output phase num; Eg:0x0203 is two MPPT and 3ph output. 45; Sys Year; System time-year; W; Year offset is 0; Local time. 46; Sys Month; System time- Month; W. 47; Sys Day; System time- Day; W. 48; Sys Hour; System time- Hour; W. 49; Sys Min; System time- Min; W. 50; Sys Sec; System time- Second; W. 51; Sys Weekly; System Weekly; W; 0-6. 52; Vac low; Grid voltage low limit protect; W; 0.1V. 53; Vac high; Grid voltage high limit protect; W; 0.1V. 54; Fac low; Grid frequency low limit protect; W; 0.01 Hz. 55; Fac high; Grid high frequency limit protect; W; 0.01 Hz. 56; Vac low 2; Grid voltage low limit protect 2; W; 0.1V. 57; Vac high 2; Grid voltage high limit protect 2; W; 0.1V. 58; Fac low 2; Grid frequency low limit; W; 0.01. |  |
| --- | --- |

| protect 2; Hz. 59; Fac high 2; Grid high frequency limit protect 2; W; 0.01 Hz. 60; Vac low 3; Grid voltage low limit protect 3; W; 0.1V. 61; Vac high 3; Grid voltage high limit protect 3; W; 0.1V. 62; Fac low 3; Grid frequency low limit protect 3; W; 0.01Hz. 63; Fac high 3; Grid frequency high limit protect 3; W; 0.01Hz. 64; Vac low C; Grid low voltage limit connect to Grid; W; 0.1V. 65; Vac high C; Grid high voltage limit connect to Grid; W; 0.1V. 66; Fac low C; Grid low frequency limit connect to Grid; W; 0.01 Hz. 67; Fac high C; Grid high frequency limit connect to Grid; W; 0.01 Hz. 68; Vac time; low1; Grid voltage low limit protect time 1; W; Cycle. 69; Vac time; high1; Grid voltage high limit protect time 1; W; Cycle. 70; Vac time; low2; Grid voltage low limit protect time 2; W; Cycle. 71; Vac time; high2; Grid voltage high limit protect time 2; W; Cycle. 72; Fac time; low1; Grid frequency low limit protect time 1; W; Cycle. 73; Fac time; high1; Grid frequency high limit protect time 1; W; Cycle. 74; Fac time; low2; Grid frequency low limit protect time 2; W; Cycle. 75; Fac time; high2; Grid frequency high limit protect time 2; W; Cycle. 76; Vac time; low3; Grid voltage low limit protect time 3; W; Cycle. 77; Vac time; high3; Grid voltage high limit protect time 3; W; Cycle. 78; Fac time; low3; Grid frequency low limit protect time 3; W; Cycle. 79; Fac; high3; Grid frequency high; W; Cycle. |  |
| --- | --- |

| time; limit protect time 3. 80; U10min; Volt protection for 10 min; W; 0.1V; 1.1Vn. 81; PV Voltage High Fault; PV Voltage High Fault; W; 0.1V. 82; FW Build No. 5; FW Build version; ASCII. 83; FW Build No. 4; FW Build version; ASCII. 84; FW Build No. 3; DSP1 FW Build No.; ASCII. 85; FW Build No. 2; DSP2 FW Build No.; ASCII. 86; FW Build No. 1; M3 FW Build No.; ASCII. 87; FW Build No. 0; CPLD FW Build No.; ASCII. 88; ModbusVersi on; Modbus Version; Eg：207 is V2.07; Int(16b its). 89; PFModel; Set PF function Model 0: PF=1 1: PF by set 2: default PF line 3: User PF line 4: UnderExcited (Inda) Reactive Power 5: OverExcited(Capa) Reactive Power 6：Q(v)model; W. 90; GPRS IP Flag; read:1;Set GPRS IP Successed Write:2;Read GPRS IP Successed; W; write:2 read:0~3. 91; FreqDerateSt art; Frequency derating start point; W; 0.01HZ. 92; FLrate; Frequency – load limit rate; W; 0-100; 10time s. 93; V1S; CEI021 V1S Q(v); W; V1S<V2S; 0.1V. 94; V2S; CEI021 V2S Q(v); W; 0.1V. 95; V1L; CEI021 V1L Q(v); W; V1L<V1S; 0.1V. 96; V2L; CEI021 V2L Q(v); W; V2L<V1L; 0.1V. |  |
| --- | --- |

| 97; Qlockinpowe r; Q(v) lock in active power of CEI021; W; 0-100; Percen t. 98; QlockOutpo wer; Q(v) lock Out active power of CEI021; W; 0-100; Percen t. 99; LIGridV; Lock in gird volt of CEI021 PF line; W; nVn; 0.1V. 100; LOGridV; Lock out gird volt of CEI021 PF line; W; nVn; 0.1V. 101; PFAdj1; PF adjust value 1; 4096 is 1. 102; PFAdj2; PF adjust value 2; 4096 is 1. 103; PFAdj3; PF adjust value 3; 4096 is 1. 104; PFAdj4; PF adjust value 4; 4096 is 1. 105; PFAdj5; PF adjust value 5; 4096 is 1. 106; PFAdj6; PF adjust value 6; 4096 is 1. 107; QVRPDelayTi meEE; QV Reactive Power delaytime; W; 0-30; 1S; 3S. 108; OverFDeratD elayTimeEE; Overfrequency deratin g delaytime; W; 0-20; 50ms; 0. 109; QpercentMa x; Qmax for Q(V) curve; W; 0-1000; 0.1%. 110; PFLineP1_LP; PF limit line point 1 load percent; W; 0-255; percen t; 255 means no this point. 111; PFLineP1_PF; PF limit line point 1 power factor; W; 0-20000. 112; PFLineP2_LP; PF limit line point 2 load percent; W; 0-255; percen t; 255 means no this point. 113; PFLineP2_PF; PF limit line point 2power factor; W; 0-20000. 114; PFLineP3_LP; PF limit line point 3 load percent; W; 0-255; percen t; 255 means no this point. 115; PFLineP3_PF; PF limit line point 3 power factor; W; 0-20000. 116; PFLineP4_LP; PF limit line point 4 load percent; W; 0-255; percen t; 255 means no this point. 117; PFLineP4_PF; PF limit line point 4 power factor; W; 0-20000. 118; BLVersion1; Boot loader version1; R; Reserved. 119; BLVersion2; Boot loader version2; R; Reserved. 120; BLVersion3; Boot loader version3; R; Reserved. 121; BLVersion4; Boot loader version4; R; Reserved. 122; INV-Lng; Inverter Longitude; W. |  |
| --- | --- |

| 123; INV-Lat; Inverter Latitude; W. 124; TrakerModel; 2 Traker Model; W; 0,1,2; 0:Inde pende nt 1:DC Source 2:Paral lel. Second group. 125; INV Type-1; Inverter type-1; R; ASCII; Reserved. 126; INV Type-2; Inverter type-2; R; ASCII. 127; INV Type-3; Inverter type-3; R; ASCII. 128; INV Type-4; Inverter type-4; R; ASCII. 129; INV Type-5; Inverter type-5; R; ASCII. 130; INV Type-6; Inverter type-6; R; ASCII. 131; INV Type-7; Inverter type-7; R; ASCII. 132; INV Type-8; Inverter type-8; R; ASCII. ……; Reserved. 200; Reserved. 201; PID Working Model; PID Working Model; W; 0:Automa tic 1: Continual 2: Overnight. 202; PID On/Off Ctrl; PID On/Off Control; W; 0:On 1:Off. 203; PID Volt Option; PID Output Voltage Option; W; 300~1000; V. ……; Reserved. 229; Reserved. 230~249 for growatt debug setting. 230; Island Disable; Island Disable or not. 1:disable 0:Enable; W; 0,1; 0. 231; Fan Check; Start Fan Check; W; 1. 232; EnableNLine; Enable N Line of grid; W; 1; 0. 233; wCheckHard ware; wCheckHardware Bit0: GFCIBreak; Bit1:SPSDamage Bit8:EepromReadWarnin g Bit9:EEWriteWarning. |  |
| --- | --- |

| ……. 234; wCheckHard ware2; reserved. 235; ubNToGNDD etect; Dis/enable N to GND detect function; W; 1:enable 0:disable; 1. 236; NonStdVacEn able; Enable/Disable Nonstandard Grid voltage range; W; 0-1;; 0; 0:Disable; 1:Enable;. 237; uwEnableSpe cSet; Disablse/enable appointed spec setting; W; 1:enable 0:disable; Binary; 0x000 0; Bit 0: Hungary. 238; Fast MPPT enable; About Fast mppt; 0,1,2; 0; Reserved. …. 240; Check Step; W. ……; Reserved. 249; Reserved. 250; Curve analysis; Enable a curve analysis of a road; W; 0~1; 0. 251; Faultrecorder Wave1; Preset Record Waveform Number; W; 1001~199 9; 1001. 252; Faultrecorder Wave2; Preset Record Waveform Number; W; 1001~199 9; 1002. 253; Faultrecorder Wave3; Preset Record Waveform Number; W; 1001~199 9; 1003. 254; Faultrecorder Wave4; Preset Record Waveform Number; W; 1001~199 9; 1004. 255; Faultrecorder Wave5; Preset Record Waveform Number; W; 1~999; 1. 256; Faultrecorder Wave6; Preset Record Waveform Number; W; 1~999; 2. 257; Faultrecorder Wave7; Preset Record Waveform Number; W; 1~999; 3. 258; Faultrecorder Wave8; Preset Record Waveform Number; W; 1~999; 4. 259; FaultRecorde rEnable; FaultRecorderEnable; W; 1~100; 0. 260; recorderWav e1; Preset Record Waveform Number; W; 1~1999; 1. 261; recorderWav e2; Preset Record Waveform Number; W; 1~1999; 2. 262; recorderWav e3; Preset Record Waveform Number; W; 1~1999; 3. |  |
| --- | --- |

| 263; recorderWav e4; Preset Record Waveform Number; W; 1~1999; 4. 264; WaveRecord erEnable; Real-time waveform recording; W; 0~1; 0. 265; Harmonic Check Enable; Harmonic Check Enable; W; 0~1; 0. 266; Impedance Enable; Impedance Enable; W; 0~1; 0. 267; 067 Debug 1 _H; 067 Debug 1 _H. 268; 067 Debug1_L; 067 Debug1_L. 269; 067 Debug2_H; 067 Debug2_H. 270; 067 Debug2_L; 067 Debug2_L. 271; 067 Debug3_H; 067 Debug3_H. 272; 067 Debug3_L; 067 Debug3_L. 273; 067 Debug4_H; 067 Debug4_H. 274; 067 Debug4_L; 067 Debug4_L. 275; 067 Debug5_H; 067 Debug5_H. 276; 067 Debug5_L; 067 Debug5_L. 277; 067 Debug6_H; 067 Debug6_H. 278; 067 Debug6_L; 067 Debug6_L. 279; 067 Debug7_H; 067 Debug7_H. 280; 067 Debug7_L; 067 Debug7_L. 281; 067 Debug8_H; 067 Debug8_H. 282; 067 Debug8_L; 067 Debug8_L. 283; 075 Debug 1; 075 Debug 1 _H. |  |
| --- | --- |

| _H. 284; 075 Debug1_L; 075 Debug1_L. 285; 075 Debug2_H; 075 Debug2_H. 286; 075 Debug2_L; 075 Debug2_L. 287; 075 Debug3_H; 075 Debug3_H. 288; 075 Debug3_L; 075 Debug3_L. 289; 075 Debug4_H; 075 Debug4_H. 290; 075 Debug4_L; 075 Debug4_L. 291; 075 Debug5_H; 075 Debug5_H. 292; 075 Debug5_L; 075 Debug5_L. 293; 075 Debug6_H; 075 Debug6_H. 294; 075 Debug6_L; 075 Debug6_L. 295; 075 Debug7_H; 075 Debug7_H. 296; 075 Debug7_L; 075 Debug7_L. 297; 075 Debug8_H; 075 Debug8_H. 298; 075 Debug8_L; 075 Debug8_L. 299; bActiveOverl oadEnable; Active Over load Enable. 300; bSvgApfMod e; Svg Apf Mode; 低4位：0： SVG/APF， 1 ： APF/SVG, 2：SVG, 3： APF 高 4 位：0：全天模式 1：夜间模. |  |
| --- | --- |

| 式. 301; bBdewLvrtKF actor; BDEW LVRT K Factor; 0-4. 待确定部分. 360; 232T485Ena; 232T485Enable; W; 0: Disable;. ble; 1: Enable. 361; Decrease; Decrease output watt; W. Power H. 362; Decrease; Decrease output watt; W; 0.1W. Power L. 363; Increase; Increase output watt; W. Power H. 364; Increase; Increase output watt; W; 0.1W. Power L. 365; Factory; The ODM Info code. 366; Vac start b; y; Vac start adjust by pf; W; 0.1V. pf. 367; PF of va; c; Max pf of adjust Vac; W; 10000. limit. 368; LCMDTest; Local command test; W; 1 to test. 369; ReactiveRate; Reactive Rate in LVFRT; W; 0-100; 2. 370; LVFRT_LV1; LVFRT low fault value 1; W; 0.1V. 371; LVFRT_LT1; LVFRT low fault time; 1; W; 1ms. 372; LVFRT_LV2; LVFRT low fault value 2; W; 0.1V. 373; LVFRT_LT2; LVFRT low fault time; 2; W; 1ms. 374; LVFRT_LV3; LVFRT low fault value 3; W; 0.1V. 375; LVFRT_LT3; LVFRT low fault time; 3; W; 1ms. 376; LVFRT_LV4; LVFRT low fault value 4; W; 0.1V. 377; LVFRT_LT4; LVFRT low fault time; 4; W; 1ms. 378; LVFRT_HV1; LVFRT high fault value 1; W; 0.1V. 379; LVFRT_HT1; LVFRT high fault time 1; W; 1ms. 380; wLoadDerate; Load derate start ac; 1.05Vn~1.; 0.1V. StartVolt; voltage; 2Vn. 381; SpecPasswor; Unlock or set; W; 0:unlock ,; k; 2. dType; Specpassword; auto loc. in 5. minute;. 1:change. pw. (should. unlock. first)，. |  |
| --- | --- |

| 2：lock; ,. &*7. 382; SpecPasswor; SpecPassword3; W; For the; ASCII; XX. d3; spec. setting. change. 383; SpecPasswor; SpecPassword2; W; ..; ASCII; XX. d2. 384; SpecPasswor; SpecPassword1; W; ..; ASCII; XX. d1. 385; DCIshift; DCI offset; Center is; Reserved. 30000. 386; DCIAdj; DCI adjust; Center is; Reserved. 2000. 387; IniEEPROM; IniEEPROM; W; 0xFF; Reserved. 388; Balance 1; Phaseflag¦ErrorCode; W; Reserved. 389; Balance 2; Power H; W; Reserved. 390; Balance 3; Power L; W; Reserved. 391; bHighACVDe; r; High ac voltage; load; W; 20; 0-100. ateSlope; derating slope. 392; BlaneceMod; BlaneceModel; W; 1-3. el. 393; BalencePhas; BalencePhase; W; 1-3. e. 394; DCIshift; 2; DCI offset 2; W; Center is; Reserved. 30000. 395; DCIshift; 3; DCI offset 3; W; Center is; Reserved. 30000. 396; EnergyLimitE; Output Energy L; imit; R; 1 is; Reserved. nable; Enable; enable. 397; EnergyRemai; Output Energy L; imit; W; 0.1kWh; Reserved. n H; value High. 398; EnergyRemai; Output Energy L; imit; W; 0.1kWh; Reserved. n L; value low. 399; TrakerModel; 2 Traker Model; W; 0,1,2; Reserved. 400; PMchec; k; Growatt Resaved; W; Reserved. 401; INVWorkMo; INV work mode set; W; 0:default; 0. de; 1:CV. Mode. 2:CC. Mode. 3:CP. |  |
| --- | --- |

| Mode. 402; PV1VoltSet; pv1 voltage set when CV; W; StartPVVo. Mode was chosed; lt-HighPV. Volt. 403; PV2VoltSet; Pv2 voltage set when CV; W; StartPVVo. Mode was chosed; lt-HighPV. Volt. 404; BT1CurrRefS; BT1 current set when CC; W; 0-MaxBTC. et; Mode was chosed; urrent. 405; BT2CurrRefS; BT2current set when CC; W; 0-MaxBTC. et; Mode was chosed; urrent. 406; WattACVRec; Delay time for powe; r c; W; 3-90S. overDelayT; i; recovering when a. me; voltage getting normal. 407; TxDataInterv; TxDataInterval; W; 1~600; 0.1. 50; 5mins. al; mins. 408; ChkCode; Datalogger Check Code; R; ASCII. NO.1; 1. 409; ChkCode; Datalogger Check Code; R; ASCII. NO.2; 2. 500; ChkCode; Datalogger Check Code; R; ASCII. NO.3; 3. 501; bISLDShiftDel; Growatt Resaved; W; Reserved. taEE. 502; bLowPointer; Growatt Resaved; W; Reserved. 505; GPRSIP Addr; GPRSIP Addr No.1; W; 0~65536; ASCII. 506; GPRSIP Addr; GPRSIP Addr No.2; W; 0~65536; ASCII. 507; GPRSIP Addr; GPRSIP Addr No.3; W; 0~65536; ASCII. 508; GPRSIP Addr; GPRSIP Addr No.4; W; 0~65536; ASCII. 509; GPRSIP Addr; GPRSIP Addr No.5; W; 0~65536; ASCII. 510; GPRSIP Addr; GPRSIP Addr No.6; W; 0~65536; ASCII. 511; GPRSIP Addr; GPRSIP Addr No.7; W; 0~65536; ASCII. 512; GPRSIP Addr; GPRSIP Addr No.8; W; 0~65536; ASCII. 513; GPRSIP Addr; GPRSIP Addr No.9; W; 0~65536; ASCII. 514; GPRSIP Addr; GPRSIP Addr No.10; W; 0~65536; ASCII. 515; GPRSIP Addr; GPRSIP Addr No.11; W; 0~65536; ASCII. 516; GPRSIP Addr; GPRSIP Addr No.12; W; 0~65536; ASCII. 517; GPRSIP Addr; GPRSIP Addr No.13; W; 0~65536; ASCII. 518; GPRSIP Addr; GPRSIP Addr No.14; W; 0~65536; ASCII. 519; GPRSIP Addr; GPRSIP Addr No.15; W; 0~65536; ASCII. 520; GPRSIP Addr; GPRSIP Addr No.16; W; 0~65536; ASCII. |  |
| --- | --- |

| 521; GPRSIP Addr; GPRSIP Addr No.17; W; 0~65536; ASCII. 522; GPRSIP Addr; GPRSIP Addr No.18; W; 0~65536; ASCII. 523; GPRSIP Addr; GPRSIP Addr No.19; W; 0~65536; ASCII. 524; GPRSIP Addr; GPRSIP Addr No.20; W; 0~65536; ASCII. 525; GPRSIP Addr; GPRSIP Addr No.21; W; 0~65536; ASCII. 526; GPRSIP Addr; GPRSIP Addr No.22; W; 0~65536; ASCII. 527; GPRSIP Addr; GPRSIP Addr No.23; W; 0~65536; ASCII. 528; GPRSIP Addr; GPRSIP Addr No.24; W; 0~65536; ASCII. 529; GPRSIP Addr; GPRSIP Addr No.25; W; 0~65536; ASCII. Six group for Storage Power. Register NO.; Variable Name; Description; Write or not; Value; Unit; Initial value; Note. 1000.; Float charge current limit; When charge current battery need is lower than this value, enter into float charge; W; 0.1A; 600; CC current. 1001.; PF CMD memory state; Set the following 19-22 CMD will be memory or not(1/0), if not, these settings are the initial value.; W; 0or1,; 0; Means these settings will be acting or not when next power on. 1002.; VbatWarning; LoadPercent(only lead-Acid): <20% 20%~50% >50%; W; 0.1V; <20% 48.0VD C [20%,5 0%] 47.0VD C >50% 45.0V. 1003.; VbatWarnClr; LoadPercent(only lead-Acid): <20% 20%~50% >50%; W; 0.1V; <20% 49.0VD C [20%,5 0%] 48.0VD C >50% 45.5V. 1004.; Vbat stop for discharge; Should stop discharge when lower than this voltage(only lead-Acid):; W; 0.01V; <20% 46.0VD C. |  |
| --- | --- |

| <20% 20%~50% >50%; [20%,5 0%] 44.8VD C >50% 44.2V. 1005.; Vbat stop for charge; Should stop charge when higher than this voltage; W; 0.01V; 5800. 1006.; Vbat start for discharge; Should not discharge when lower than this voltage; W; 0.01V; 4800. 1007.; Vbat start for charge; Should charge when lower than this voltage; W; 0.01V; 5300; reserved. 1008.; FlashStart; Update firmware; W; 0x0001:o wn 0X0100: TIC2000. 1009.; Bat temp lower limit d; Battery temperature lower limit for discharge; W; 0-200:0-2 0℃ 1000-140 0：-40-0℃; 0.1℃; 1170. 1010.; Bat temp upper limit d; Battery temperature upper limit for discharge; W; 200-1000; 0.1℃; 420. 1011.; Bat temp lower limit c; Battery temperature lower limit for charge; W; 0-200:0-2 0℃ 1000-140 0：-40-0℃; 0.1℃; 30. 1012.; Bat temp upper limit c; Battery temperature upper limit for charge; W; 200-1000; 0.1℃; 370. 1013.; ForcedDischa rge Min Start1; time- Min; W; 0-60; 1; 0. 1014.; ForcedDischa rge Hour Start1; time- Hour; W; 0-24; 1; 0. 1015.; ForcedDischa rge Min Start2; time- Min; W; 0-60; 1; 0. 1016.; ForcedDischa rge Hour; time- Hour; W; 0-24; 1; 0. |  |
| --- | --- |

| Start2. 1017.; ForcedDischa rge Min Start3; time- Min; W; 0-60; 1; 0. 1018.; ForcedDischa rge Hour Start3; time- Hour; W; 0-24; 1; 0. 1019.; ForcedDischa rge Min Stop1; time- Min; W; 0-60; 0. 1020.; ForcedDischa rge Hour Stop1; time- Hour; W; 0-24; 0. 1021.; ForcedDischa rge Min Stop2; time- Min; W; 0-60; 0. 1022.; ForcedDischa rge Hour Stop2; time- Hour; W; 0-24; 0. 1023.; ForcedDischa rge Min Stop3; time- Min; W; 0-60; 0. 1024.; ForcedDischa rge Hour Stop3; time- Hour; W; 0-24; 0. 1025.; ForcedCharg e Min Start1; time- Min; W; 0-60; 1; 0. 1026.; ForcedCharg e Hour Start1; time- Hour; W; 0-24; 1; 0. 1027.; ForcedCharg e Min Start2; time- Min; W; 0-60; 1; 0. 1028.; ForcedCharg e Hour Start2; time- Hour; W; 0-24; 1; 0. 1029.; ForcedCharg e Min Start3; time- Min; W; 0-60; 1; 0. 1030.; ForcedCharg e Hour Start3; time- Hour; W; 0-24; 1; 0. 1031.; ForcedCharg e Min Stop1; time- Min; W; 0-60; 1; 0. |  |
| --- | --- |

| 1032.; ForcedCharg e Hour Stop1; time- Hour; W; 0-24; 1; 0. 1033.; ForcedCharg e Min Stop2; time- Min; W; 0-60; 1; 0. 1034.; ForcedCharg e Hour Stop2; time- Hour; W; 0-24; 1; 0. 1035.; ForcedCharg e Min Stop3; time- Min; W; 0-60; 1; 0. 1036.; ForcedCharg e Hour Stop3; time- Hour; W; 0-24; 1; 0. 1037.; bCTMode; Use the CTMode to Choose RFCT \ Cable CT\METER; W; 2:METER 1:cWirele ssCT 0:cWiredC T; 0. 1038.; bCTAdjust; CTAdjust enable; W; 0:disable 1:enable; 0. 1039.; wDisChargeS OCLowLimit1; Stop soc1 when discharge; W; 0-10; 1%; 5; Load first Mode. 1040.; wDisChargeS OCLowLimit2; Stop soc2 when discharge; W; 0-10; 1%; 5; grid first Mode. 1041.; wChargeSOC LowLimit1; Stop soc1 when charge; W; 50-100; 1%; 100; Load first Mode. 1042.; wChargeSOC LowLimit2; Stop soc2 when charge; W; 50-100; 1%; 100; battery first Mode. 1043.; AC Charge Enable; AC Charge Enable; W/R; 0:disable 1:enable; 0. 1044.; Priority choose; Load(default)/Battery/G rid; W/R; 0:Load 1:Battery 2:Grid; 0. 1045.; ChargePower Command; Free Mode Charging Power Percent; 0~100; 1%; 100. 1046.; DisChargePo werComman d; Free Mode DisCharging Power Percent; 0~100; 1%; 100. 1047.; bAgingTestSt ep; Command for aging test; 0: default 1: charge 2: discharge. |  |
| --- | --- |

| 26 / 55 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 13. | Ppv3 H | PV3 input power (high) |  | 0.1W |  |  |  |
| 14. | Ppv3 L | PV3 input power (low) |  | 0.1W |  |  |  |
| 15. | Vpv4 | PV4 voltage |  | 0.1V |  |  |  |
| 16. | PV4Curr | PV4 input current |  | 0.1A |  |  |  |
| 17. | Ppv4 H | PV4 input power (high) |  | 0.1W |  |  |  |
| 18. | Ppv4 L | PV4 input power (low) |  | 0.1W |  |  |  |
| 19. | Vpv5 | PV5 voltage |  | 0.1V |  |  |  |
| 20. | PV5Curr | PV5 input current |  | 0.1A |  |  |  |
| 21. | Ppv5H | PV5 input power(high) |  | 0.1W |  |  |  |
| 22. | Ppv5 L | PV5 input power(low) |  | 0.1W |  |  |  |
| 23. | Vpv6 | PV6 voltage |  | 0.1V |  |  |  |
| 24. | PV6Curr | PV6 input current |  | 0.1A |  |  |  |
| 25. | Ppv6 H | PV6 input power (high) |  | 0.1W |  |  |  |
| 26. | Ppv6 L | PV6 input power (low) |  | 0.1W |  |  |  |
| 27. | Vpv7 | PV7 voltage |  | 0.1V |  |  |  |
| 28. | PV7Curr | PV7 input current |  | 0.1A |  |  |  |
| 29. | Ppv7 H | PV7 input power (high) |  | 0.1W |  |  |  |
| 30. | Ppv7 L | PV7 input power (low) |  | 0.1W |  |  |  |
| 31. | Vpv8 | PV8 voltage |  | 0.1V |  |  |  |
| 32. | PV8Curr | PV8 input current |  | 0.1A |  |  |  |
| 33. | Ppv8 H | PV8 input power (high) |  | 0.1W |  |  |  |
| 34. | Ppv8 L | PV8 input power (low) |  | 0.1W |  |  |  |
| 35. | Pac H | Output power (high) |  | 0.1W |  |  |  |
| 36. | Pac L | Output power (low) |  | 0.1W |  |  |  |
| 37. | Fac | Grid frequency |  | 0.01Hz |  |  |  |
| 38. | Vac1 | Three/single phase grid voltage |  | 0.1V |  |  |  |
| 39. | Iac1 | Three/single phase grid output current |  | 0.1A |  |  |  |
| 40. | Pac1 H | Three/single phase grid output watt (high) |  | 0.1VA |  |  |  |
| 41. | Pac1 L | Three/single phase grid output watt (low) |  | 0.1VA |  |  |  |
| 42. | Vac2 | Three phase grid voltage |  | 0.1V |  |  |  |
| 43. | Iac2 | Three phase grid output current |  | 0.1A |  |  |  |
| 44. | Pac2 H | Three phase grid output power (high) |  | 0.1VA |  |  |  |
| 45. | Pac2 L | Three phase grid output power (low) |  | 0.1VA |  |  |  |
| 46. | Vac3 | Three phase grid voltage |  | 0.1V |  |  |  |
| 47. | Iac3 | Three phase grid output current |  | 0.1A |  |  |  |
| 48. | Pac3 H | Three phase grid output power (high) |  | 0.1VA |  |  |  |
| 49. | Pac3 L | Three phase grid output power (low) |  | 0.1VA |  |  |  |
| 50. | Vac_RS | Three phase grid voltage |  | 0.1V | Line volt | age |  |
| 51. | Vac_ST | Three phase grid voltage |  | 0.1V | Line volt | age |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |

| 27 / 55 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 52. | Vac_TR | Three phase grid voltage |  | 0.1V | Line volt | age |  |
| 53. | Eac today H | Today generate energy (high) |  | 0.1kWH |  |  |  |
| 54. | Eac today L | Today generate energy (low) |  | 0.1kWH |  |  |  |
| 55. | Eac total H | Total generate energy (high) |  | 0.1kWH |  |  |  |
| 56. | Eac total L | Total generate energy (low) |  | 0.1kWH |  |  |  |
| 57. | Time total H | Work time total (high) |  | 0.5s |  |  |  |
| 58. | Time total L | Work time total (low) |  | 0.5s |  |  |  |
| 59. | Epv1_today H | PV1 Energy today (high) |  | 0.1kWh |  |  |  |
| 60. | Epv1_today L | PV1 Energy today (low) |  | 0.1kWh |  |  |  |
| 61. | Epv1_total H | PV1 Energy total (high) |  | 0.1kWh |  |  |  |
| 62. | Epv1_total L | PV1 Energy total (low) |  | 0.1kWh |  |  |  |
| 63. | Epv2_today H | PV2 Energy today (high) |  | 0.1kWh |  |  |  |
| 64. | Epv2_today L | PV2 Energy today (low) |  | 0.1kWh |  |  |  |
| 65. | Epv2_total H | PV2 Energy total (high) |  | 0.1kWh |  |  |  |
| 66. | Epv2_total L | PV2 Energy total (low) |  | 0.1kWh |  |  |  |
| 67. | Epv3_today H | PV3 Energy today (high) |  | 0.1kWh |  |  |  |
| 68. | Epv3_today L | PV3 Energy today (low) |  | 0.1kWh |  |  |  |
| 69. | Epv3_total H | PV3 Energy total (high) |  | 0.1kWh |  |  |  |
| 70. | Epv3_total L | PV3 Energy total (low) |  | 0.1kWh |  |  |  |
| 71. | Epv4_today H | PV4 Energy today (high) |  | 0.1kWh |  |  |  |
| 72. | Epv4_today L | PV4 Energy today (low) |  | 0.1kWh |  |  |  |
| 73. | Epv4_total H | PV4 Energy total (high) |  | 0.1kWh |  |  |  |
| 74. | Epv4_total L | PV4 Energy total (low) |  | 0.1kWh |  |  |  |
| 75. | Epv5_today H | PV5 Energy today (high) |  | 0.1kWh |  |  |  |
| 76. | Epv5_today L | PV5 Energy today (low) |  | 0.1kWh |  |  |  |
| 77. | Epv5_total H | PV5 Energy total (high) |  | 0.1kWh |  |  |  |
| 78. | Epv5_total L | PV5 Energy total (low) |  | 0.1kWh |  |  |  |
| 79. | Epv6_today H | PV6 Energy today (high) |  | 0.1kWh |  |  |  |
| 80. | Epv6_today L | PV6Energy today (low) |  | 0.1kWh |  |  |  |
| 81. | Epv6_total H | PV6 Energy total (high) |  | 0.1kWh |  |  |  |
| 82. | Epv6_total L | PV6 Energy total (low) |  | 0.1kWh |  |  |  |
| 83. | Epv7_today H | PV7 Energy today (high) |  | 0.1kWh |  |  |  |
| 84. | Epv7_today L | PV7 Energy today (low) |  | 0.1kWh |  |  |  |
| 85. | Epv7_total H | PV7 Energy total (high) |  | 0.1kWh |  |  |  |
| 86. | Epv7_total L | PV7 Energy total (low) |  | 0.1kWh |  |  |  |
| 87. | Epv8_today H | PV8 Energy today (high) |  | 0.1kWh |  |  |  |
| 88. | Epv8_today L | PV8Energy today (low) |  | 0.1kWh |  |  |  |
| 89. | Epv8_total H | PV8 Energy total (high) |  | 0.1kWh |  |  |  |
| 90. | Epv8_total L | PV8 Energy total (low) |  | 0.1kWh |  |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |

| 28 / 55 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 91. | Epv_total H | PV Energy total (high) |  | 0.1kWh |  |  |  |
| 92. | Epv_total L | PV Energy total (low) |  | 0.1kWh |  |  |  |
| 93. | Temp1 | Inverter temperature |  | 0.1C |  |  |  |
| 94. | Temp2 | The inside IPM in inverter Temperature |  | 0.1C |  |  |  |
| 95. | Temp3 | Boost temperature |  | 0.1C |  |  |  |
| 96. | Temp4 |  |  |  | reserved |  |  |
| 97. | Temp5 |  |  |  | reserved |  |  |
| 98. | P Bus Voltage | P Bus inside Voltage |  | 0.1V |  |  |  |
| 99. | N Bus Voltage | N Bus inside Voltage |  | 0.1V |  |  |  |
| 100. | IPF | Inverter output PF now | 0-20000 |  |  |  |  |
| 101. | RealOPPercent | Real Output power Percent |  | 1% |  |  |  |
| 102. | OPFullwatt H | Output Maxpower Limited high |  |  |  |  |  |
| 103. | OPFullwatt L | Output Maxpower Limited low |  | 0.1W |  |  |  |
| 104. | DeratingMode | DeratingMode | 0:no derate; 1:PV; 2:*; 3:Vac; 4:Fac; 5:Tboost; 6:Tinv; 7:Control; 8:*; 9:*OverBack ByTime; |  | “*”is Res | erved |  |
| 105. | Fault code | Inverter fault code | &*1 |  |  |  |  |
| 106. | Fault Bitcode H | Inverter fault code high | &*8 |  |  |  |  |
| 107. | Fault Bitcode L | Inverter fault code low |  |  |  |  |  |
| 108. | Fault Bit_II H | Inverter fault code_II high | --预留 mix，待定义 |  |  |  |  |
| 109. | Fault Bit_II L | Inverter fault code_II low |  |  |  |  |  |
| 110. | Warning bit H | Warning bit H | &*8 |  |  |  |  |
| 111. | Warning bit L | Warning bit L |  |  |  |  |  |
| 112. | bINVWarnCode | bINVWarnCode |  |  |  |  |  |
| 113. | real Power Percent | real Power Percent | 0-100 | % |  |  |  |
| 114. | inv start delay time | inv start delay time |  |  |  |  |  |
| 115. | bINVAllFaultCod e | bINVAllFaultCode |  |  |  |  |  |
| … | reserved |  |  |  | reserved |  |  |
| 124. | reserved |  |  |  | reserved |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |

| 29 / 55 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Second group |  |  |  |  |  |  |
| 125. | PID PV1+ Voltage | PID PV1PE Volt | 0~1000V | 0.1V |  |  |
| 126. | PID PV1+ Current | PID PV1PE Curr | -10~10mA | 0.1mA |  |  |
| 127. | PID PV2+ Voltage | PID PV2PE Volt | 0~1000V | 0.1V |  |  |
| 128. | PID PV2+ Current | PID PV2PE Curr | -10~10mA | 0.1mA |  |  |
| 129. | PID PV3+ Voltage | PID PV3PE Volt | 0~1000V | 0.1V |  |  |
| 130. | PID PV3+ Current | PID PV3PE Curr | -10~10mA | 0.1mA |  |  |
| 131. | PID PV4+ Voltage | PID PV4PE Volt | 0~1000V | 0.1V |  |  |
| 132. | PID PV4+ Current | PID PV4PE Curr | -10~10mA | 0.1mA |  |  |
| 133. | PID PV5+ Voltage | PID PV5PE Volt | 0~1000V | 0.1V |  |  |
| 134. | PID PV5+ Current | PID PV5PE Curr | -10~10mA | 0.1mA |  |  |
| 135. | PID PV6+ Voltage | PID PV6PE Volt | 0~1000V | 0.1V |  |  |
| 136. | PID PV6+ Current | PID PV6PE Curr | -10~10mA | 0.1mA |  |  |
| 137. | PID PV7+ Voltage | PID PV7PE Volt | 0~1000V | 0.1V |  |  |
| 138. | PID PV7+ Current | PID PV7PE Curr | -10~10mA | 0.1mA |  |  |
| 139. | PID PV8+ Voltage | PID PV8PE Volt | 0~1000V | 0.1V |  |  |
| 140. | PID PV8+ Current | PID PV8PE Curr | -10~10mA | 0.1mA |  |  |
| 141. | PID Status | Bit0~7:PID Working Status 1:Wait Status 2:Normal Status 3:Fault Status Bit8~15:Reversed | 0~3 |  |  |  |
| 142. | V _String1 | PV String1 voltage |  | 0.1V |  |  |
| 143. | Curr _String1 | PV String1 current | -15~15A | 0.1A |  |  |
| 144. | V _String2 | PV String2 voltage |  | 0.1V |  |  |
| 145. | Curr _String2 | PV String2 current | -15~15A | 0.1A |  |  |
| 146. | V _String3 | PV String3 voltage |  | 0.1V |  |  |
| 147. | Curr _String3 | PV String3 current | -15~15A | 0.1A |  |  |
| 148. | V _String4 | PV String4 voltage |  | 0.1V |  |  |
| 149. | Curr _String4 | PV String4 current | -15~15A | 0.1A |  |  |
| 150. | V _String5 | PV String5 voltage |  | 0.1V |  |  |
| 151. | Curr _String5 | PV String5 current | -15~15A | 0.1A |  |  |
| 152. | V _String6 | PV String6 voltage |  | 0.1V |  |  |
| 153. | Curr _String6 | PV String6 current | -15~15A | 0.1A |  |  |
| 154. | V _String7 | PV String7 voltage |  | 0.1V |  |  |
| 155. | Curr _String7 | PV String7 current | -15~15A | 0.1A |  |  |
| 156. | V _String8 | PV String8 voltage |  | 0.1V |  |  |
| 157. | Curr _String8 | PV String8 current | -15A~15A | 0.1A |  |  |
| 158. | V _String9 | PV String9 voltage |  | 0.1V |  |  |
| 159. | Curr _String9 | PV String9 current | -15A~15A | 0.1A |  |  |
| 160. | V _String10 | PV String10 voltage |  | 0.1V |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |

| 30 / 55 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 161. | Curr _String10 |  | PV String10 current | -15~15A | 0.1A |  |  |  |
| 162. | V _String11 |  | PV String11 voltage |  | 0.1V |  |  |  |
| 163. | Curr _String11 |  | PV String11 current | -15~15A | 0.1A |  |  |  |
| 164. | V _String12 |  | PV String12 voltage |  | 0.1V |  |  |  |
| 165. | Curr _String12 |  | PV String12 current | -15~15A | 0.1A |  |  |  |
| 166. | V _String13 |  | PV String13 voltage |  | 0.1V |  |  |  |
| 167. | Curr _String13 |  | PV String13 current | -15A~15A | 0.1A |  |  |  |
| 168. | V _String14 |  | PV String14 voltage |  | 0.1V |  |  |  |
| 169. | Curr _String14 |  | PV String14 current | -15~15A | 0.1A |  |  |  |
| 170. | V _String15 |  | PV String15 voltage |  | 0.1V |  |  |  |
| 171. | Curr _String15 |  | PV String15 current | -15~15A | 0.1A |  |  |  |
| 172. | V _String16 |  | PV String16 voltage |  | 0.1V |  |  |  |
| 173. | Curr _String16 |  | PV String16 current | -15~15A | 0.1A |  |  |  |
| 174. | StrUnmatch |  | Bit0~15: String1~16 unmatch |  |  | suggestiv | e |  |
| 175. | StrCurrentUnblan ce |  | Bit0~15: String1~16 current unblance |  |  | suggestiv | e |  |
| 176. | StrDisconnect |  | Bit0~15: String1~16 disconnect |  |  | suggestiv | e |  |
| 177. | PIDFaultCode |  | Bit0:Output over voltage Bit1: ISO fault Bit2: BUS voltage abnormal Bit3~15:reserved |  |  |  |  |  |
| 178. | String Prompt |  | String Prompt Bit0: String Unmatch Bit1: StrDisconnect Bit2:StrCurrentUnblance Bit3~15:reserved |  |  |  |  |  |
| 179 | PV Warning Value |  | PV Warning Value |  |  |  |  |  |
| 180 | DSP075 Value | Warning | DSP075 Warning Value |  |  |  |  |  |
| 181 | DSP075 Value | Fault | DSP075 Fault Value |  |  |  |  |  |
| 182 | DSP067 Data1 | Debug | DSP067 Debug Data1 |  |  |  |  |  |
| 183 | DSP067 Data2 | Debug | DSP067 Debug Data2 |  |  |  |  |  |
| 184 | DSP067 Data3 | Debug | DSP067 Debug Data3 |  |  |  |  |  |
| 185 | DSP067 Data4 | Debug | DSP067 Debug Data4 |  |  |  |  |  |
| 186 | DSP067 Data5 | Debug | DSP067 Debug Data5 |  |  |  |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |  |

| 31 / 55 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 187 | DSP067 Data6 | Debug | DSP067 Debug Data6 |  |  |  |  |
| 188 | DSP067 Data7 | Debug | DSP067 Debug Data7 |  |  |  |  |
| 189 | DSP067 Data8 | Debug | DSP067 Debug Data8 |  |  |  |  |
| 190 | DSP075 Data1 | Debug | DSP075 Debug Data1 |  |  |  |  |
| 191 | DSP075 Data2 | Debug | DSP075 Debug Data2 |  |  |  |  |
| 192 | DSP075 Data3 | Debug | DSP075 Debug Data3 |  |  |  |  |
| 193 | DSP075 Data4 | Debug | DSP075 Debug Data4 |  |  |  |  |
| 194 | DSP075 Data55 | Debug | DSP075 Debug Data5 |  |  |  |  |
| 195 | DSP075 Data6 | Debug | DSP075 Debug Data6 |  |  |  |  |
| 196 | DSP075 Data7 | Debug | DSP075 Debug Data7 |  |  |  |  |
| 197 | DSP075 Data8 | Debug | DSP075 Debug Data8 |  |  |  |  |
| 198 | bUSBAgingTestOk Flag |  | USB Aging Test Ok Flag | 0-1 |  |  |  |
| 199 | bFlashEraseAging OkFlag |  | Flash Erase Aging Ok Flag | 0-1 |  |  |  |
| 200 | PV ISO |  | PV ISO Value |  | KΩ |  |  |
| 201 | R_DCI |  | R DCI Curr |  | 0.1mA |  |  |
| 202 | S_DCI |  | S DCI Curr |  | 0.1mA |  |  |
| 203 | T_DCI |  | T DCI Curr |  | 0.1mA |  |  |
| 204 | PID_Bus |  | PID Bus Volt |  | 0.1V |  |  |
| 205 | GFCI |  | GFCI Curr |  | mA |  |  |
| 206 | SVG/APF Status |  | SVG/APF Status | 0-3 |  |  |  |
| 207 | CT_I _R |  | R phase load side current for SVG |  | 0.1A |  |  |
| 208 | CT_I _S |  | S phase load side current for SVG |  | 0.1A |  |  |
| 209 | CT_I _T |  | T phase load side current for SVG |  | 0.1A |  |  |
| 210 | CT_Q _R H |  | R phase load side output reactive power for SVG(High) |  | 0.1Var |  |  |
| 211 | CT_Q _R L |  | R phase load side output reactive power for SVG(low) |  | 0.1Var |  |  |
| 212 | CT_Q _S H |  | S phase load side output reactive power for SVG(High) |  | 0.1Var |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |

| 33 / 55 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | – year¦ month |  | 2000 |  |  |  |
| 257. | Grid Fault record 2 – day¦ hour | Grid Fault record 2 – day¦ hour |  |  |  |  |
| 258. | Grid Fault record 2 – min¦ sec | Grid Fault record 2 – min¦ sec |  |  |  |  |
| 259. | Grid Fault record 2-value | Grid Fault record 2-value |  |  |  |  |
| 260. | Grid Fault record 3 – code | Grid Fault record 3 – code |  |  |  |  |
| 261. | Grid Fault record 3 – year¦ month | Grid Fault record 3 – year¦ month | Year offset is 2000 |  |  |  |
| 262. | Grid Fault record 3 – day¦ hour | Grid Fault record 3 – day¦ hour |  |  |  |  |
| 263. | Grid Fault record 3 – min¦ sec | Grid Fault record 3 – min¦ sec |  |  |  |  |
| 264. | Grid Fault record 3-value | Grid Fault record 3-value |  |  |  |  |
| 265. | Grid Fault record 4 – code | Grid Fault record 4 – code |  |  |  |  |
| 266. | Grid Fault record 4 – year¦ month | Grid Fault record 4 – year¦ month | Year offset is 2000 |  |  |  |
| 267. | Grid Fault record 4 – day¦ hour | Grid Fault record 4 – day¦ hour |  |  |  |  |
| 268. | Grid Fault record 4 – min¦ sec | Grid Fault record 4 – min¦ sec |  |  |  |  |
| 269. | Grid Fault record 4-value | Grid Fault record 4-value |  |  |  |  |
| 270. | Grid Fault record 5 – code | Grid Fault record 5 – code |  |  |  |  |
| 271. | Grid Fault record 5 – year¦ month | Grid Fault record 5 – year¦ month | Year offset is 2000 |  |  |  |
| 272. | Grid Fault record 5 – day¦ hour | Grid Fault record 5 – day¦ hour |  |  |  |  |
| 273. | Grid Fault record 5 – min¦ sec | Grid Fault record 5 – min¦ sec |  |  |  |  |
| 274. | Grid Fault record 5-value | Grid Fault record 5-value |  |  |  |  |
| 275. | bTestProcess<<8 ¦ bAutoTestStep | Auto test process or auto test step | &*3 |  |  |  |
| 276. | wAutoTestResult | Auto test result | &*4 |  |  |  |
| 277. | cTestStepStop | Auto test stop step | &*4 |  |  |  |
| 278. | Value Limit | Safety voltage/frequency limit value |  | 0.1V |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |

| 34 / 55 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 279. | Time Limit | Safety time limit value |  | 1ms |  |  |
| 280. | Real value | Real voltage/frequency value |  | 0.1V |  |  |
| 281. | Test value | Auto testing voltage/frequency value |  | 0.1V |  |  |
| 282. | Test treat value | Auto test voltage/frequency treat value |  | 0.1V |  |  |
| 283. | Test treat time | Auto test treat time |  | 1ms |  |  |
| 284. | E_hour0 H | Energy hourly of this day |  |  |  |  |
| 285. | E_hour0 L | Energy hourly of this day |  |  |  |  |
| 286. | E_hour1 H | Energy hourly of this day |  |  |  |  |
| 287. | E_hour1 L | Energy hourly of this day |  |  |  |  |
| … | E_hour | … |  |  |  |  |
| … | E_hour | … |  |  |  |  |
| 330. | E_hour23 H | Energy hourly of this day |  |  |  |  |
| 331. | E_hour23 L | Energy hourly of this day |  |  |  |  |
| 332. | E_ day0 H | Energy of latest day |  |  |  |  |
| 333. | E_day0 L | Energy of latest day |  |  |  |  |
| 334. | E_ day1 H | Energy of latest 1st day |  |  |  |  |
| 335. | E_ day1 L | Energy of latest 1st day |  |  |  |  |
| … | E_ day | … |  |  |  |  |
| … | E_ day | … |  |  |  |  |
| 344. | E_ day 6 H | Energy of latest 6th day |  |  |  |  |
| 345. | E_ day 6L | Energy of latest 6th day |  |  |  |  |
| 346. | E_ month0 H | Energy of latest month |  |  |  |  |
| 347. | E_ month0 L | Energy of latest month |  |  |  |  |
|  | E_ month1 H | Energy of latest 1st month |  |  |  |  |
|  | E_ month1 L | Energy of latest 1st month |  |  |  |  |
| … | E_ month | … |  |  |  |  |
| … | E_ month | … |  |  |  |  |
| 368. | E_ month11 H | Energy of latest 11th month |  |  |  |  |
| 369. | E_ month11L | Energy of latest 11th month |  |  |  |  |
| … |  |  |  |  | reserved |  |
| 374. |  |  |  |  | reserved |  |
| Fouth group |  |  |  |  |  |  |
| 375. | E_ year0 H | Energy of latest year |  |  |  |  |
| 376. | E_ year 0 L | Energy of latest year |  |  |  |  |
| 377. | E_ year 1 H | Energy of latest 1st year |  |  |  |  |
| 378. | E_ year 1 L | Energy of latest 1st year |  |  |  |  |
| … | E_ year | … |  |  |  |  |
| … | E_ year | … |  |  |  |  |
| 413. | E_ year 18 H | Energy of latest 18th year |  |  |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |

| 35 / 55 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 414. | E_ year18 L |  | Energy of latest 18th year |  |  |  |  |
| … |  |  |  |  |  |  |  |
| 499. |  |  |  |  |  | reserved |  |
| Fifth group and sixth |  |  |  |  |  |  |  |
| 500. |  | Inverter Error record 1 – code | Inverter Error record 1 – code |  |  |  |  |
| 501. |  | Inverter Error record 1 – year¦ month | Inverter Error record 1 – year¦ month | Year offset is 2000 |  |  |  |
| 502. |  | Inverter Error record 1 – day¦ hour | Inverter Error record 1 – day¦ hour |  |  |  |  |
| 503. |  | Inverter Error record 1 – min¦ sec | Inverter Error record 1 – min¦ sec |  |  |  |  |
| 504. |  | Inverter Error record 1-value | Inverter Error record 1-value |  |  |  |  |
| 505. |  | Inverter Error record 2 – code | Inverter Error record 2 – code |  |  |  |  |
| 506. |  | Inverter Error record 2 – year¦ month | Inverter Error record 2 – year¦ month | Year offset is 2000 |  |  |  |
| 507. |  | Inverter Error record 2 – day¦ hour | Inverter Error record 2 – day¦ hour |  |  |  |  |
| 508. |  | Inverter Error record 2 – min¦ sec | Inverter Error record 2 – min¦ sec |  |  |  |  |
| 509. |  | Inverter Error record 2-value | Inverter Error record 2-value |  |  |  |  |
| 510. |  | Inverter Error record 2 – code | Inverter Error record 2 – code |  |  |  |  |
| … |  | Inverter Error record…… | Inverter Error record…… |  |  |  |  |
| 740. |  | Inverter Error record49 – code | Inverter Error record 49- code |  |  |  |  |
| 741. |  | Inverter Error record49 – year¦ month | Inverter Error record49 – year¦ month | Year offset is 2000 |  |  |  |
| 742. |  | Inverter Error record49 – day¦ hour | Inverter Error record49 – day¦ hour |  |  |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |

| 36 / 55 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 743. | Inverter Error record49 – min¦ sec | Inverter Error record49 – min¦ sec |  |  |  |  |  |
| 744. | Inverter Error record49-value | Inverter Error record49-value |  |  |  |  |  |
| 745. | Inverter Error record50 – code | Inverter Error record 50- code |  |  |  |  |  |
| 746. | Inverter Error record50 – year¦ month | Inverter Error record50 – year¦ month | Year offset is 2000 |  |  |  |  |
| 747. | Inverter Error record50 – day¦ hour | Inverter Error record50 – day¦ hour |  |  |  |  |  |
| 748. | Inverter Error record50 – min¦ sec | Inverter Error record50 – min¦ sec |  |  |  |  |  |
| 749. | Inverter Error record50-value | Inverter Error record50-value |  |  |  |  |  |
| Seventh group for debug |  |  |  |  |  |  |  |
| 750. | ISO fault Value | ISO Fault value |  | 0.1V |  |  |  |
| 751. | GFCI fault Value | GFCI fault Value |  | 1mA |  |  |  |
| 752. | DCI fault Value | DCI fault Value |  | 0.01A |  |  |  |
| 753. | Vpv fault Value | PV voltage fault value |  | 0.1V |  |  |  |
| 754. | Vac fault Value | AC voltage fault value |  | 0.1V |  |  |  |
| 755. | Fac fault Value | AC frequency fault value |  | 0.01 Hz |  |  |  |
| 756. | Temperature fault Value | Temperature fault value |  | 0.1C |  |  |  |
| 757. | WarningValue1 | Warning Value1 of slave CPU | &*9 |  |  |  |  |
| 758. | WarningValue2 | Warning Value2 of slave CPU | &*9 |  |  |  |  |
| 759. | WarningValue3 | Warning Value3 of main CPU or STM32 | &*9 |  |  |  |  |
| 760. | FaultValue | Inverter fault value | &*10 |  |  |  |  |
| ... |  |  |  |  |  |  |  |
| 799. |  |  |  |  |  |  |  |
| 800. | Debug Reserved | Debug Reserved |  |  | Reserved |  |  |
| …… |  |  |  |  |  |  |  |
| 874. | Debug Reserved | Debug Reserved |  |  | Reserved |  |  |
| Eighth group for reserved |  |  |  |  |  |  |  |
| …… |  |  |  |  |  |  |  |
| 999. |  |  |  |  | Reserved |  |  |
| Ninth group for Storage power |  |  |  |  |  |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |

| 37 / 55 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1000. | uwSysWorkMod e | System work mode | 0x00:等待模式 0x01: 自 检 模式，可选 0x02 : 保留 0x03：SysFault 模式 0x04: Flash 模式 0x05 ： PVBATOnline 模式: 0x06 ： BatOnline 模式 0x07 ： PVOfflineMod e 模式 0x08 ： BatOfflineMo de 模式 |  | 监控层 显示的式为： 0x00:等待 0x01:自检 0x03:故障 0x04:升级 0x05¦0x06 ¦0x08:正 | 给客户 工作模 模式模式模式中 ¦0x07 常模式 |  |
| 1001. |  | System fault word0 |  |  | 详见一障说明 | 体机故 |  |
| 1002. |  | System fault word1 |  |  |  |  |  |
| 1003. |  | System fault word2 |  |  |  |  |  |
| 1004. |  | System fault word3 |  |  |  |  |  |
| 1005. |  | System fault word4 |  |  |  |  |  |
| 1006. |  | System fault word5 |  |  |  |  |  |
| 1007. |  | System fault word6 |  |  |  |  |  |
| 1008. |  | System fault word7 |  |  |  |  |  |
| 1009. | Pdischarge1 H | Discharge power(high) |  | 0.1W |  |  |  |
| 1010. | Pdischarge1 L | Discharge power (low) |  | 0.1W |  |  |  |
| 1011. | Pcharge1 H | Charge power(high) |  | 0.1W |  |  |  |
| 1012. | Pcharge1 L | Charge power (low) |  | 0.1W |  |  |  |
| 1013. | Vbat | Battery voltage |  | 0.1V |  |  |  |
| 1014. | SOC | State of charge Capacity | 0-100 | 1% |  |  |  |
| 1015. | Pactouser R H | AC power to user H |  | 0.1w |  |  |  |
| 1016. | Pactouser R L | AC power to user L |  | 0.1w |  |  |  |
| 1017. | Pactouser S H |  |  | 0.1w |  |  |  |
| 1018. | Pactouser S L |  |  | 0.1w |  |  |  |
| 1019. | Pactouser T |  |  | 0.1w |  |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |

| 42 / 55 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1303. | Ed_ month1 L | Energy Disharge of latest 1st month |  | 0.1kwh |  |  |
| … | Ed_ month | … |  | 0.1kwh |  |  |
| … | Ed_ month | … |  | 0.1kwh |  |  |
| 1322. | Ed_ month11 H | Energy Disharge of latest 11th month |  | 0.1kwh |  |  |
| 1323. | Ed_ month11L | Energy Disharge of latest 11th month |  | 0.1kwh |  |  |
| 1324. | Ed_ year0 H | Energy Disharge of latest year |  | 0.1kwh |  |  |
| 1325. | Ed_ year 0 L | Energy Disharge of latest year |  | 0.1kwh |  |  |
| 1326. | Eg_ day0 H | Energy to grid of latest day |  | 0.1kwh |  |  |
| 1327. | Eg_day0 L | Energy to grid of latest day |  | 0.1kwh |  |  |
| 1328. | Eg_ day1 H | Energy to grid of latest 1st day |  | 0.1kwh |  |  |
| 1329. | Eg_ day1 L | Energy to grid of latest 1st day |  | 0.1kwh |  |  |
| … | Eg_ day | … |  | 0.1kwh |  |  |
| … | Eg_ day | … |  | 0.1kwh |  |  |
| 1337. | Eg_ day 6 H | Energy to grid of latest 6th day |  | 0.1kwh |  |  |
| 1338. | Eg_ day 6L | Energy to grid of latest 6th day |  | 0.1kwh |  |  |
| 1339. | Eg_ month0 H | Energy to grid of latest month |  | 0.1kwh |  |  |
| 1340. | Eg_ month0 L | Energy to grid of latest month |  | 0.1kwh |  |  |
| 1341. | Eg_ month1 H | Energy to grid of latest 1st month |  | 0.1kwh |  |  |
| 1342. | Eg_ month1 L | Energy to grid of latest 1st month |  | 0.1kwh |  |  |
| … | Eg_ month | … |  | 0.1kwh |  |  |
| … | Eg_ month | … |  | 0.1kwh |  |  |
| 1361. | Eg_ month11 H | Energy to grid of latest 11th month |  | 0.1kwh |  |  |
| 1362. | Eg_ month11L | Energy to grid of latest 11th month |  | 0.1kwh |  |  |
| 1363. | Eg_ year0 H | Energy to grid of latest year |  | 0.1kwh |  |  |
| 1364. | Eg_ year 0 L | Energy to grid of latest year |  | 0.1kwh |  |  |
| 1365. | Eu_ day0 H | Energy to user of latest day |  | 0.1kwh |  |  |
| 1366. | Eu_day0 L | Energy to user of latest day |  | 0.1kwh |  |  |
| 1367. | Eu_ day1 H | Energy to user of latest 1st day |  | 0.1kwh |  |  |
| 1368. | Eu_ day1 L | Energy to user of latest 1st day |  | 0.1kwh |  |  |
| … | Eu_ day | … |  | 0.1kwh |  |  |
| … | Eu_ day | … |  | 0.1kwh |  |  |
| Eleventh group for Storage power |  |  |  |  |  |  |
| 1375. | Eu_ day 6 H | Energy to user of latest 6th day |  | 0.1kwh |  |  |
| 1376. | Eu_ day 6L | Energy to user of latest 6th day |  | 0.1kwh |  |  |
| 1377. | Eu_ month0 H | Energy to user of latest month |  | 0.1kwh |  |  |
| 1378. | Eu_ month0 L | Energy to user of latest month |  | 0.1kwh |  |  |
| 1379. | Eu_ month1 H | Energy to user of latest 1st month |  | 0.1kwh |  |  |
| 1380. | Eu_ month1 L | Energy to user of latest 1st month |  | 0.1kwh |  |  |
| … | Eu_ month | … |  | 0.1kwh |  |  |
| … | Eu_ month | … |  | 0.1kwh |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |

| 43 / 55 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1399. | Eu_ month11 H | Energy to user of latest 11th month |  |  | 0.1kwh |  |  |
| 1400. | Eu_ month11L | Energy to user of latest 11th month |  |  | 0.1kwh |  |  |
| 1401. | Eu_ year0 H | Energy to user of latest year |  |  | 0.1kwh |  |  |
| 1402. | Eu_ year 0 L | Energy to user of latest year |  |  | 0.1kwh |  |  |
| Twelfth group for buck-boost debug |  |  |  |  |  |  |  |
| 1500. | CurrentRecord_0x 22 | OCD Date & Time(L) R |  | 0-5:Second 6-11:minute 12-16:hour 17-21:day 22-25:month 26-31:year |  |  |  |
| 1501. | CurrentRecord_0x 23 | OCD Date & Time(H) | R |  |  |  |  |
| 1502. | CurrentRecord_0x 24 | Current SCD Protection Counts in Discharge | R | 0-65534 |  |  |  |
| 1503. | CurrentRecord_0x 25 | SCD Date & Time(L) | R | 0-5:Second 6-11:minute 12-16:hour 17-21:day 22-25:month 26-31:year |  |  |  |
| 1504. | CurrentRecord_0x 26 | SCD Date & Time(H) | R |  |  |  |  |
| 1505. | CurrentRecordUp date |  | R | 0: unrefreshed 1: refreshed |  |  |  |
| 1506. | CurrentRecord_0x 28 |  | R | reversed |  |  |  |
| 1507. | CurrentRecord_0x 29 |  | R | reversed |  |  |  |
| 1508. | CurrentRecord_0x 2A |  | R | reversed |  |  |  |
| 1509. | CurrentRecord_0x 2B |  | R | reversed |  |  |  |
| 1510. | CurrentRecord_0x 2C |  | R | reversed |  |  |  |
| 1511. | CurrentRecord_0x 2D |  | R | reversed |  |  |  |
| 1512. | CurrentRecord_0x 2E |  | R | reversed |  |  |  |
| 1513. | CurrentRecord_0x |  | R | reversed |  |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |

| 44 / 55 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2F |  |  |  |  |  |  |
| 1514. | VoltageRecord_0x 31 | High Voltage Protection Counts in Charge | R |  |  |  |  |
| 1515. | VoltageRecord_0x 32 | High Voltage Protection Counts in Discharge | R |  |  |  |  |
| 1516. | VoltageRecord_0x 33 | OVC Date & Time(L) | R |  |  |  |  |
| 1517. | VoltageRecord_0x 34 | OVC Date & Time(H) | R |  |  |  |  |
| 1518. | VoltageRecord_0x 35 | OVD Date & Time(L) |  |  |  |  |  |
| 1519. | VoltageRecord_0x 36 | OVD Date & Time(H) |  |  |  |  |  |
| 1520. | VoltageRecord_0x 37 | Low Voltage Protection Counts in Charge |  |  |  |  |  |
| 1521. | VoltageRecord_0x 38 | Low Voltage Protection Counts in Discharge |  |  |  |  |  |
| 1522. | VoltageRecord_0x 39 | UVC Date & Time(L) |  |  |  |  |  |
| 1523. | VoltageRecord_0x 3A | UVC Date & Time(H) |  |  |  |  |  |
| 1524. | VoltageRecord_0x 3B | UVD Date & Time(L) |  |  |  |  |  |
| 1525. | VoltageRecord_0x 3C | UVD Date & Time(H) |  |  |  |  |  |
| 1526. | VoltageRecordUpd ate |  |  | 0: unrefreshed 1: refreshed |  |  |  |
| 1527. | VoltageRecord_0x 3E |  |  | reversed |  |  |  |
| 1528. | VoltageRecord_0x 3F |  |  | reversed |  |  |  |
| 1529. | TemperatureRecor d_0x41 | High Temperature Protection Counts in Charge |  |  |  |  |  |
| 1530. | TemperatureRecor d_0x42 | High Temperature Protection Counts in Discharge |  |  |  |  |  |
| 1531. | TemperatureRecor d_0x43 | OTC Date & Time(L) |  |  |  |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |

| 45 / 55 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1532. | TemperatureRecor d_0x44 | OTC Date & Time(H) |  |  |  |  |  |
| 1533. | TemperatureRecor d_0x45 | OTD Date & Time(L) |  |  |  |  |  |
| 1534. | TemperatureRecor d_0x46 | OTD Date & Time(H) |  |  |  |  |  |
| 1535. | TemperatureRecor d_0x47 | Low Temperature Protection Counts in Charge |  |  |  |  |  |
| 1536. | TemperatureRecor d_0x48 | Low Temperature Protection Counts in Discharge |  |  |  |  |  |
| 1537. | TemperatureRecor d_0x49 | UTC Date & Time(L) |  |  |  |  |  |
| 1538. | TemperatureRecor d_0x4A | UTC Date & Time(H) |  |  |  |  |  |
| 1539. | TemperatureRecor d_0x4B | UTD Date & Time(L) |  |  |  |  |  |
| 1540. | TemperatureRecor d_0x4C | UTD Date & Time(H) |  |  |  |  |  |
| 1541. | TemperatureRecor dUpdate |  |  | reversed | 0: unrefresh ed 1: refreshed |  |  |
| 1542. | TemperatureRecor d_0x4E |  |  | reversed |  |  |  |
| 1543. | TemperatureRecor d_0x4F |  |  | reversed |  |  |  |
| 1544. | ChargeRecordUpd ate |  | W/R | 0: unrefreshed 1: refreshed | default:0 |  |  |
| 1545. | ChargeRecord_0x 51 | Charge Counts (more than 60s) |  | 0~65534 |  |  |  |
| 1546. | ChargeRecord_0x 52 | Last charge Date & Time(L) |  |  |  |  |  |
| 1547. | ChargeRecord_0x 53 | Last charge Date & Time(H) |  |  |  |  |  |
| 1548. | ChargeRecord_0x 54 | Full Charge Counts |  | 0~65534 |  |  |  |
| 1549. | ChargeRecord_0x | Last full charge Date & |  |  |  |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |

| 46 / 55 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 55 | Time(L) |  |  |  |  |  |
| 1550. | ChargeRecord_0x 56 | Last full charge Date & Time(H) |  |  |  |  |  |
| 1551. | ChargeRecord_0x 57 | 2nd Protection Active Date & Time(L) |  |  |  |  |  |
| 1552. | ChargeRecord_0x 58 | 2nd Protection Active Date & Time(H) |  |  |  |  |  |
| 1553. | ChargeRecord_0x 59 |  |  | reversed |  |  |  |
| 1554. | ChargeRecord_0x 5A |  |  | reversed |  |  |  |
| 1555. | StatusInfo_0x11 | Date&Time(L) |  |  |  |  |  |
| 1556. | StatusInfo_0x12 | Date&Time(H) |  |  |  |  |  |
| 1557. | StatusInfo_0x13 | status |  | bit0-1:00-pre -charge; 01-standby; 10-charging; 11-dischargi ng bit2: 0-no error; 1-error bit3: 0-unbalanc; 1-balance bit4: 0-wake; 1-sleep bit5: 0-mosfet off; 1-mosfet on bit6-8:revers ed |  |  |  |
| 1558. | StatusInfo_0x14 | Error code |  | bit0: OCD bit1: SCD bit2: OV bit3: UV bit4: OTD bit5: OTC bit6: UTD bit7: UTC |  |  |  |
| Growatt New Energy Technology Co., Ltd. 古瑞瓦特新能源股份有限公司 Tel: 86 75529515888 #28 Guangming Road , LongTeng community, 中国深圳市宝安区石岩街道办龙腾 www.growatt.com District, Shenzhen, P.R. China. 社区光明路28号 P.C. 518000 |  |  |  |  |  |  |  |

|  |  |  |  | 4 | Testing grid frequency low pro |  |
| --- | --- | --- | --- | --- | --- | --- |

&*4: The variable “wAutoTestResult” and “cTestStepStop”: wAutoTestResult is the step test time         counter, when it reach cTestStepStop, this step test will stop and fail.

&*5: Inverter Model: A , could be show: “A1 B0 D0 T0 PF U1 M5 S1” or “1000F151”

Ax=(A&0XF00000000)>>28

Bx=(A&0XF0000000)>>24

Dx=(A&0XF000000)>>20

Tx=(A&0XF00000)>>16

Px=(A&0x00F000)>>12

Ux=(A&0x000F00)>>8

Mx=(A&0x0000F0)>>4

Sx=(A&0x00000F)

&*6: DTC(Device type code)

| Code No. | Device type | Note |
| --- | --- | --- |
| 001xx | Inverter | 1 tracker and 1phase Grid connect PV inverter TL |
| 002xx | Inverter | 2 tracker and 1phase Grid connect PV inverter TL |
| 003xx | Inverter | 1 tracker and 1phase Grid connect PV inverter HF |
| 004xx | Inverter | 2 tracker and 1phase Grid connect PV inverter HF |
| 005xx | Inverter | 1 tracker and 1phase Grid connect PV inverter LF |
| 006xx | Inverter | 2 tracker and 1phase Grid connect PV inverter LF |
| 007xx | Inverter | 1 tracker and 3phase Grid connect PV inverter TL |
| 008xx | Inverter | 2 tracker and 3phase Grid connect PV inverter TL |
| 009xx | Inverter | 1 tracker and 3phase Grid connect PV inverter LF |
| 010xx | Inverter | 2 tracker and 3phase Grid connect PV inverter LF |
| …… |  |  |
| 10001 | Data logger | RF-ShineVersion |
| 10002 | Data logger | Web-ShinePano |
| 10003 | Data logger | Web-ShineWebBox |
| 10004 | Data logger | WL-WIFI Module |
| …… |  |  |
| 11001 | Confluence box | Confluence box 1 |
| …… |  |  |

&*7: Grid network power control command password:

Inverter is in lock state after power on; change the power control by network command should unlock   	inverter first; default pw is XXXXXX;

Unlock: send 0 to 3-135, then send password to 3-136~138; inverter will auto lock in 5min after

unlocked;

Change PW: unlock first, then send 1 to 3-135, then send new password to 3-136~138;

Lock: send 0 or 2 to 3-135;

&*8: Inverter fault code and warning code

| Fault code |  |  |  | Warning code |
| --- | --- | --- | --- | --- |
| 0x00000001 | \ |  | 0x0001 | Fan warning |
| 0x00000002 | Communication error |  | 0x0002 | String communication abnormal |
| 0x00000004 | \ |  | 0x0004 | StrPID config Warning |
| 0x00000008 | StrReverse or StrShort fault |  | 0x0008 | \ |
| 0x00000010 | Model Init fault |  | 0x0010 | DSP and COM firmware unmatch |
| 0x00000020 | Grid Volt Sample diffirent |  | 0x0020 | \ |
| 0x00000040 | ISO Sample diffirent |  | 0x0040 | SPD abnormal |
| 0x00000080 | GFCI Sample diffirent |  | 0x0080 | GND and N connect abnormal |
| 0x00000100 | \ |  | 0x0100 | PV1 or PV2 circuit short |
| 0x00000200 | \ |  | 0x0200 | PV1 or PV2 boost driver broken |
| 0x00000400 | \ |  | 0x0400 | \ |
| 0x00000800 | \ |  | 0x0800 | \ |
| 0x00001000 | AFCI Fault |  | 0x1000 | \ |
| 0x00002000 | \ |  | 0x2000 | \ |
| 0x00004000 | AFCI Module fault |  | 0x4000 | \ |
| 0x00008000 | \ |  | 0x8000 | \ |
| 0x00010000 | \ |  |  |  |
| 0x00020000 | Relay check fault |  |  |  |
| 0x00040000 | \ |  |  |  |
| 0x00080000 | \ |  |  |  |
| 0x00100000 | \ |  |  |  |
| 0x00200000 | Communication error |  |  |  |
| 0x00400000 | Bus Voltage error |  |  |  |
| 0x00800000 | AutoTest fail |  |  |  |
| 0x01000000 | No Utility |  |  |  |
| 0x02000000 | PV Isolation Low |  |  |  |
| 0x04000000 | Residual I High |  |  |  |
| 0x08000000 | Output High DCI |  |  |  |
| 0x10000000 | PV Voltage high |  |  |  |
| 0x20000000 | AC V Outrange |  |  |  |
| 0x40000000 | AC F Outrange |  |  |  |
| 0x80000000 | TempratureHigh |  |  |  |

&*9 Warning Value

|  | Warning Value 1 | Warning Value 2 | Warning Value 3 |
| --- | --- | --- | --- |
| 0x0001 | String1abnormal | PV1ShortCircuit | AC SPD abnormal |
| 0x0002 | String2abnormal | PV2ShortCircuit | DC SPD abnormal |

# 6 Notice

- It can drive mostly 32 pv inverters for one rs485 comport.

- There are only read input and hold registers commands even the newest version.

- App user could only care the input register.

- App user could not care the holding registers.

- Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing the other registers;