Growatt Inverter Modbus RTU Protocol

V1.24

Make： weiwei.shi

Check： qixing.ren

Authorize： liangcai.wu

Effective date：

Change Record

| Index | Version | Change Content | Make | Make date |
| --- | --- | --- | --- | --- |
| 1 | 00 | First Republic | Weiwei.shi | 2020.4.28 |

Instruction：Register range for various types of inverter

TL-X/TL-XH/TL-XHUS（MINType）：03registerrange：0~124,3000~3124，

3125~3249(TL-XHUS)；04 register range：3000~3124,3125~3249， 3250~3374（TL-XH）

TL3-X(MAX、MID、MAC Type)：03 register range：0~124,125~249； 04 register range：0~124,125~249

MAX1500V、MAX-XLV:03registerrange：0~124,125~249；04register range：0~124,125~249,875~999

MODTL3-XH:03registerrange：0~124,3000~3124；04registerrange：

3000~3124,3125~3249

Storage(MIXType)：03registerrange：0~124,1000~1124；04register range：0~124,1000~1124

Storage(SPAType)：03registerrange：0~124,1000~1124；04register range：1000~1124,2000~2124，1125~1249

Storage(SPHType)：03registerrange：0~124,1000~1124；04register range：0~124,1000~1124，1125~1249

catalog

1 Data format	5

2 Command Format	5

3 Device Message Transmission Mode / Framing	8

4 Register map	9

4.1 Holding Reg	9

4.2 Input Reg	47

5 Set address	84

6 Notice	84

# Data format

Valid slave device addresses are in the range of 0 – 254 decimal.

The individual slave devices are assigned addresses in the range of 1 – 254.

0 is the broadcast address

It is 16bits (two bytes) unsigned integer for each holding and input register;

# Command Format

Function 3 Read holding register

Response Error:

11 0x80|0x03 ErrornumCRC(Errornum as a byte)

Function 4 Read input	register

Response Error:

11 0x80|0x04 ErrornumCRC	(Errornum as a byte)

Function 6 Preset single register

Response Error:

11 0x80|0x06 ErrornumCRC	(Errornum as a byte)

Function 16 Preset multiple register

Response Error:

11 0x80|0x10 ErrornumCRC	(Errornum as a byte)

# Device Message Transmission Mode / Framing

RTU Mode

When controllers are setup to communicate on a Modbus network using RTU (Remote Terminal Unit) mode, each 8–bit byte in a message contains two 4–bit hexadecimal characters. Each message must be transmitted in a continuous stream.

The format for each byte in RTU mode is:

Coding System: 8–bit binary, hexadecimal 0–9, A–F

Two hexadecimal characters contained in each

8–bit field of the message

Bits per Byte:

1 start bit

8 data bits, least significant bit sent first

None parity

1 stop bit

Error Check Field: Cyclical Redundancy Check (CRC)

The baud rate of the transmission is:

Default Baud Rate: 9600 bps

Can be set through hold register 22

Minimum CMD period (RS485 Time out): 850ms.

Wait for minimum850ms to send a new CMD after last CMD. Suggestion is 1s;

Maximum Data Length Define:

Maximum read data length is 125 words in read command;

Maximum update data length is 125 words in preset command;

Note:

Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing other registers;

# Register map

It is 16bits (two bytes) unsigned integer for each holding and input register;

## Holding Reg

| Registe r NO. | Variable Name | Description | Write or not | Value | Unit | Initial value | Note |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| First group |  |  |  |  |  |  |  |  |
| 00 | OnOff | Remote On/Off . On（1）；Off（0）Inverter On（3）；Off（2）BDC | W | 0、1、2、 3 |  | 1 | The inverter can be switched on and off, and the BDC can be switched on and off for the batt ready function. |  |
| 01 | SaftyFuncEn | Bit0: SPI enable Bit1: AutoTestStart Bit2: LVFRT enable Bit3:FreqDerating Enable Bit4: Softstart enable Bit5: DRMS enable Bit6:PowerVoltFunc Enable Bit7: HVFRT enable Bit8:ROCOF enable Bit9: Recover FreqDeratingMode Enable | W | 0 : disable 1: enable |  |  | SPI: system interface Bit0~3:for CEI0-21 Bit4~6:for SAA | protection |
|  |  | Bit10：Split phase enable |  |  |  |  |  |  |
|  |  | Bit10~15:预留 |  |  |  |  |  |  |
| 02 | PF CMD memory state | Set Holding register3,4,5,99 CMD will be memory or not(1/0), if not, these settings are the initial value. | W | 0or1 |  | 0 | Means these settings will be acting or not when next power on |  |
| 03 | Active P Rate | Inverter Max output active power percent | W | 0-100 or 255 | % | 255 | 255: power is not be limited |  |

| 04 | Reactive P Rate | Inverter max output reactive power percent | W | -100-100 or 255 |  | % | 255 | 255: power is not be limited |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 05 | Power factor | Inverter output power factor’s 10000 times | W | 0-20000, 0-10000 is underexci ted, other is overexcit ed |  |  | 0 |  |
| 06 | Pmax H | Normal power (high) |  |  |  | 0.1VA |  |  |
| 07 | Pmax L | Normal power (low) |  |  |  | 0.1VA |  |  |
| 08 | Vnormal | Normal work PV voltage |  |  |  | 0.1V |  |  |
| 09 | Fw version H | Firmware version (high) |  |  |  | ASCII |  |  |
| 10 | Fw version M | Firmware version (middle) |  |  |  |  |  |  |
| 11 | Fw version L | Firmware version (low) |  |  |  |  |  |  |
| 12 | Fw version2 H | Control Firmware version (high) |  |  |  | ASCII |  |  |
| 13 | Fw version2 M | Control Firmware version (middle) |  |  |  |  |  |  |
| 14 | Fw version2 L | Control Firmware version (low) |  |  |  |  |  |  |
| 15 | LCD language | LCD language | W | 0-5 |  |  |  | 0: Italian; 1: English; 2: German; 3: Spanish; 4: French; 5: Chinese; 6：Polish 7：Portugues 8：Hungary |
| 16 | CountrySele cted | Country Selected or not | W | 0: need to select; 1: have selected |  |  |  |  |
| 17 | Vpv start | Input start voltage | W |  |  | 0.1V |  |  |
| 18 | Time start | Start time | W |  |  | 1s |  |  |
| 19 | RestartDelay Time | Restart Delay Time after fault back; | W |  |  | 1s |  |  |

| 20 | wPowerStart Slope | Power start slope | W | 1-1000 | 0.1% |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 21 | wPowerRest artSlopeEE | Power restart slope | W | 1-1000 | 0.1% |  |  |
| 22 | wSelectBaud rate | Select communicationbaudrat e 0: 9600bps 1:38400bps | W | 0-1 |  | 0 |  |
| 23 | Serial NO | Serial number 1-2 |  |  | ASCII |  |  |
| 24 | Serial NO | Serial number 3-4 |  |  |  |  |  |
| 25 | Serial NO | Serial number 5-6 |  |  |  |  |  |
| 26 | Serial NO | Serial number 7-8 |  |  |  |  |  |
| 27 | Serial NO | Serial number 9-10 |  |  |  |  |  |
| 28 | Module H | Inverter Module (high) |  | &*5 |  |  |  |
| 29 | Module L | Inverter Module (low) |  | &*5 |  |  |  |
| 30 | Com Address | Communicate address | W | 1-254 |  | 1 |  |
| 31 | FlashStart | Update firmware | W | 1 |  |  |  |
| 32 | Reset User Info | Reset User Information | W | 0x0001 |  |  |  |
| 33 | Reset to factory | Reset to factory | W | 0x0001 |  |  |  |
| 34 | Manufacture r Info 8 | Manufacturer information (high) |  |  | ASCII |  |  |
| 35 | Manufacture r Info 7 | Manufacturer information (middle) |  |  |  |  |  |
| 36 | Manufacture r Info 6 | Manufacturer information (low) |  |  |  |  |  |
| 37 | Manufacture r Info 5 | Manufacturer information (high) |  |  |  |  |  |
| 38 | Manufacture r Info 4 | Manufacturer information (middle) |  |  |  |  |  |
| 39 | Manufacture r Info3 | Manufacturer information (low) |  |  |  |  |  |
| 40 | Manufacture r Info 2 | Manufacturer information (low) |  |  |  |  |  |
| 41 | Manufacture r Info 1 | Manufacturer information (high) |  |  |  |  |  |
| 42 | bfailsafeEn; | G100 fail safe | W | Enable:1 Disable:0 |  |  | English G100 fail safe set |
| 43 | DTC | Device Type Code |  | &*6 |  |  |  |

| 44 | TP | Input tracker num and output phase num |  |  |  | Eg:0x020 3 is two MPPT and 3ph output |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 45 | Sys Year | System time-year |  |  | W | Year offset is 0 |  |  | Local time |
| 46 | Sys Month | System time- Month |  |  | W |  |  |  |  |
| 47 | Sys Day | System time- Day |  |  | W |  |  |  |  |
| 48 | Sys Hour | System time- Hour |  |  | W |  |  |  |  |
| 49 | Sys Min | System time- Min |  |  | W |  |  |  |  |
| 50 | Sys Sec | System time- Second |  |  | W |  |  |  |  |
| 51 | Sys Weekly | System Weekly |  |  | W | 0-6 |  |  |  |
| 52 | Vac low | Grid voltage low limit protect |  |  | W |  | 0.1V |  |  |
| 53 | Vac high | Grid voltage high limit protect |  |  | W |  | 0.1V |  |  |
| 54 | Fac low | Grid frequency low limit protect |  |  | W |  | 0.01 Hz |  |  |
| 55 | Fac high | Grid high frequencylimit protect |  |  | W |  | 0.01 Hz |  |  |
| 56 | Vac low 2 | Grid voltage low limit protect 2 |  |  | W |  | 0.1V |  |  |
| 57 | Vac high 2 | Grid voltage high limit protect 2 |  |  | W |  | 0.1V |  |  |
| 58 | Fac low 2 | Grid frequency low limit protect 2 |  |  | W |  | 0.01 Hz |  |  |
| 59 | Fac high 2 | Grid high frequency limit protect 2 |  |  | W |  | 0.01 Hz |  |  |
| 60 | Vac low 3 | Grid voltage protect 3 | low | limit | W |  | 0.1V |  |  |
| 61 | Vac high 3 | Grid voltage protect 3 | high | limit | W |  | 0.1V |  |  |
| 62 | Fac low 3 | Grid frequency limit protect 3 |  | low | W |  | 0.01Hz |  |  |
| 63 | Fac high 3 | Grid frequency limit protect 3 |  | high | W |  | 0.01Hz |  |  |
| 64 | Vac low C | Grid low voltage limit connect to Grid |  |  | W |  | 0.1V |  |  |
| 65 | Vac high C | Grid high voltage limit connect to Grid |  |  | W |  | 0.1V |  |  |
| 66 | Fac low C | Grid low frequency |  |  | W |  | 0.01 |  |  |

|  |  |  | limit connect to Grid |  |  |  |  | Hz |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 67 | Fac high C |  | Grid high frequency limit connect to Grid |  |  | W |  | 0.01 Hz |  |  |
| 68 | Vac time | low1 | Grid voltage low protect time 1 |  | limit | W |  | Cycle |  |  |
| 69 | Vac time | high1 | Grid voltage protect time | high 1 | limit | W |  | Cycle |  |  |
| 70 | Vac time | low2 | Grid voltage protect time | low 2 | limit | W |  | Cycle |  |  |
| 71 | Vac time | high2 | Grid voltage protect time | high 2 | limit | W |  | Cycle |  |  |
| 72 | Fac time | low1 | Grid frequency limit protect time |  | low 1 | W |  | Cycle |  |  |
| 73 | Fac time | high1 | Grid frequency limit protect time |  | high 1 | W |  | Cycle |  |  |
| 74 | Fac time | low2 | Grid frequency limit protect time |  | low 2 | W |  | Cycle |  |  |
| 75 | Fac time | high2 | Grid frequency limit protect time |  | high 2 | W |  | Cycle |  |  |
| 76 | Vac time | low3 | Grid voltage protect time | low 3 | limit | W |  | Cycle |  |  |
| 77 | Vac time | high3 | Grid voltage protect time | high 3 | limit | W |  | Cycle |  |  |
| 78 | Fac time | low3 | Grid frequency limit protect time |  | low 3 | W |  | Cycle |  |  |
| 79 | Fac time | high3 | Grid frequency limit protect time |  | high 3 | W |  | Cycle |  |  |
| 80 | U10min |  | Volt protection for 10 min |  |  | W |  | 0.1V | 1.1Vn |  |
| 81 | PV Voltage High Fault |  | PV Voltage High Fault |  |  | W |  | 0.1V |  |  |
| 82 | FW Build No. 5 |  | Model letter version number (TJ) |  |  |  |  | ASCII |  |  |
| 83 | FW Build No. 4 |  | Model letter version number (AA) |  |  |  |  | ASCII |  |  |
| 84 | FW Build No. 3 |  | DSP1 FW Build No. |  |  |  |  | ASCII |  |  |
| 85 | FW Build No. 2 |  | DSP2/M0 FW Build No. |  |  |  |  | ASCII |  |  |
| 86 | FW Build No. 1 |  | CPLD/AFCI FW Build No. |  |  |  |  | ASCII |  |  |
| 87 | FW Build No. |  | M3 FW Build No. |  |  |  |  | ASCII |  |  |

|  | 0 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 88 | ModbusVers ion | Modbus Version |  | Eg：207 is V2.07 | Int(16 bits) |  |  |
| 89 | PFModel | Set PF function Model 0: PF=1 1: PF by set 2: default PF line 3: User PF line 4: UnderExcited (Inda) Reactive Power 5: OverExcited(Capa) Reactive Power 6：Q(v)model 7：Direct Control mode | W |  |  |  |  |
|  |  | - Static capacitive QV mode - Static inductive QV mode |  |  |  |  |  |
| 90 | GPRS IP Flag | Bit0-3:read:1;Set GPRS IP Successed Write:2;Read GPRS IP Successed Bit4-7:GPRS status | W | Bit0-3:ab out GPRS IP SET Bit4-7:ab out GRPRS Status |  |  |  |
| 91 | FreqDerateS tart | Frequency derating start point | W |  | 0.01H Z |  |  |
| 92 | FLrate | Frequency – load limit rate | W | 0-100 | 10tim es |  |  |
| 93 | V1S | CEI021 V1S Q(v) | W | V1S<V2S | 0.1V |  |  |
| 94 | V2S | CEI021 V2S Q(v) | W |  | 0.1V |  |  |
| 95 | V1L | CEI021 V1L Q(v) | W | V1L<V1S | 0.1V |  |  |
| 96 | V2L | CEI021 V2L Q(v) | W | V2L<V1L | 0.1V |  |  |
| 97 | Qlockinpow er | Q(v) lock in active power of CEI021 | W | 0-100 | Percen t |  |  |
| 98 | QlockOutpo wer | Q(v) lock Out active power of CEI021 | W | 0-100 | Percen t |  |  |
| 99 | LIGridV | Lock in gird volt of CEI021 PF line | W | nVn | 0.1V |  |  |
| 100 | LOGridV | Lock out gird volt of CEI021 PF line | W | nVn | 0.1V |  |  |

| 101 | PFAdj1 | PF adjust value 1 |  | 4096 is 1 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 102 | PFAdj2 | PF adjust value 2 |  | 4096 is 1 |  |  |  |
| 103 | PFAdj3 | PF adjust value 3 |  | 4096 is 1 |  |  |  |
| 104 | PFAdj4 | PF adjust value 4 |  | 4096 is 1 |  |  |  |
| 105 | PFAdj5 | PF adjust value 5 |  | 4096 is 1 |  |  |  |
| 106 | PFAdj6 | PF adjust value 6 |  | 4096 is 1 |  |  |  |
| 107 | QVRPDelayTi meEE | QV Reactive Power delaytime | W | 0-30 | 1S | 3S |  |
| 108 | OverFDeratD elayTimeEE | Overfrequency derati ngdelaytime | W | 0-20 | 50ms | 0 |  |
| 109 | QpercentMa x | Qmax for Q(V) curve | W | 0-1000 | 0.1% |  |  |
| 110 | PFLineP1_LP | PF limit line point 1 load percent | W | 0-255 | percen t |  | 255 means no this point |
| 111 | PFLineP1_PF | PF limit line point 1 power factor | W | 0-20000 |  |  |  |
| 112 | PFLineP2_LP | PF limit line point 2 load percent | W | 0-255 | percen t |  | 255 means no this point |
| 113 | PFLineP2_PF | PF limit line point 2power factor | W | 0-20000 |  |  |  |
| 114 | PFLineP3_LP | PF limit line point 3 load percent | W | 0-255 | percen t |  | 255 means no this point |
| 115 | PFLineP3_PF | PF limit line point 3 power factor | W | 0-20000 |  |  |  |
| 116 | PFLineP4_LP | PF limit line point 4 load percent | W | 0-255 | percen t |  | 255 means no this point |
| 117 | PFLineP4_PF | PF limit line point 4 power factor | W | 0-20000 |  |  |  |
| 118 | Module 4 | Inverter Module (4) |  | &*11 |  |  | SxxBxx |
| 119 | Module 3 | Inverter Module (3) |  | &*11 |  |  | DxxTxx |
| 120 | Module 2 | Inverter Module (2) |  | &*11 |  |  | PxxUxx |
| 121 | Module 1 | Inverter Module (1) |  | &*11 |  |  | Mxxxx Power |
| 122 | ExportLimit_ En/dis | ExportLimit_En/dis | R/W | 1/0 |  |  | ExportLimit enable, 0: Disable exportLimit; 1: Enable 485 exportLimit; 2: Enable 232 exportLimit; 3: Enable CT exportLimit; |
| 123 | ExportLimitP owerRate | ExportLimitPowerRate | R/W | -1000~+1 000 | 0.1% |  | ExportLimit PowerRate |
| 124 | TrakerModel | Traker Model | W | 0,1,2 |  |  | 0:Independent 1:DC Source 2:Parallel |

| Second group |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 125 | INV Type-1 | Inverter type-1 | R |  | ASCII |  | Reserved |
| 126 | INV Type-2 | Inverter type-2 | R |  | ASCII |  |  |
| 127 | INV Type-3 | Inverter type-3 | R |  | ASCII |  |  |
| 128 | INV Type-4 | Inverter type-4 | R |  | ASCII |  |  |
| 129 | INV Type-5 | Inverter type-5 | R |  | ASCII |  |  |
| 130 | INV Type-6 | Inverter type-6 | R |  | ASCII |  |  |
| 131 | INV Type-7 | Inverter type-7 | R |  | ASCII |  |  |
| 132 | INV Type-8 | Inverter type-8 | R |  | ASCII |  |  |
| 133 | BLVersion1 | Boot loader version1 | R |  |  |  | Reserved |
| 134 | BLVersion2 | Boot loader version2 | R |  |  |  | Reserved |
| 135 | BLVersion3 | Boot loader version3 | R |  |  |  | Reserved |
| 136 | BLVersion4 | Boot loader version4 | R |  |  |  | Reserved |
| 137 | Reactive P ValueH | Reactive PowerH | R/W |  | 0.1var |  |  |
| 138 | Reactive P ValueL | Reactive PowerL | R/W |  | 0.1var |  |  |
| 139 | ReactiveOut putPriorityE nable | ReactiveOutput Priority Enable | R/W |  | 0/1 |  | 0：disable 1：enable |
| 140 | Reactive P Value(Ratio) | Reactive Power Ratio | R/W |  | 0.1 |  |  |
| …… |  |  |  |  |  |  |  |
| 141 | SvgFunction Enable | Svg enable on night | R/W |  | 0/1 |  | 0：disable 1：enable |
| 142 | uwUnderFU ploadPoint | UnderF Upload Point | R/W |  | 0.01H Z |  |  |
| 143 | uwOFDerate RecoverPoin t | OFDerate RecoverPoint | R/W |  | 0.01H Z |  |  |
| 144 | uwOFDerate RecoverDela yTime | OFDerate RecoverDelayTime | R/W | 0-30000 | 50ms |  |  |
| 145 | ZeroCurrent Enable | ZeroCurrent Enable | R/W | 0-1 |  |  |  |
| 146 | uwZeroCurre ntStaticlowV olt | ZeroCurrent StaticlowVolt | R/W | 46-230V | 0.1V | 115V |  |
| 147 | uwZeroCurre ntStaticHigh Volt | ZeroCurrent StaticHighVolt | R/W | 230-276V | 0.1V | 276V |  |
| 148 | uwHVoltDer | HVoltDerate HighPoint | R/W | 0-1000V | 0.1V |  |  |

|  | ateHighPoint |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 149 | uwHVoltDer ateLowPoint | HVoltDerate LowPoint | R/W | 0-1000V | 0.1V |  |  |
| 150 | uwQVPower StableTime | QVPower Stable Time | R/W | 0-60S | 0.1S |  |  |
| 151 | uwUnderFU ploadStopPo int | UnderF Upload StopPoint | R/W |  | 0.01H Z |  |  |
| 152 | fUnderFreqP oint | Underfrequency load start point | R/W | 46.00-50. 00 | 0.01Hz | 49.80 | CEI |
| 153 | fUnderFreqE ndPoint | Underfrequency down load end point | R/W | 46.00-50. 00 | 0.01Hz | 49.10 | CEI |
| 154 | fOverFreqPo int | Over frequency loading start point | R/W | 50.00-52. 00 | 0.01Hz | 50.20 | CEI |
| 155 | fOverFreqEn dPoint | Over frequency loading end point | R/W | 50.00-52. 00 | 0.01Hz | 51.50 | CEI |
| 156 | fUnderVoltP oint | Undervoltage load shedding start point | R/W | 160-300 | 0.1V | 220.0 | CEI |
| 157 | fUnderVoltE ndPoint | Undervoltage derating end point | R/W | 160-300 | 0.1V | 207.0 | CEI |
| 158 | fOverVoltPoi nt | Overvoltage loading start point | R/W | 160-300 | 0.1V | 230.0 | CEI |
| 159 | fOverVoltEn dPoint | Overvoltage loading end point | R/W | 160-300 | 0.1V | 245.0 | CEI |
| 160 | uwNominal GridVolt | NominalGridVolt Select | R/W | 0~3 |  |  | UL |
| 161 | uwGridWatt Delay | GridWatt DelayTime | R/W | 0~3000 | 20ms |  | UL |
| 162 | uwReconnec tStartSlope | Reconnect StartSlope | R/W | 1~1000 | 0.1 |  | UL |
| 163 | uwLFRTEE | LFRT1 Freq | R/W | 5500~650 0 | 0.01Hz |  | UL |
| 164 | uwLFRTTime EE | LFRT1 Time | R/W |  | 20ms |  | UL |
| 165 | uwLFRT2EE | LFRT2 Freq | R/W | 5500~650 0 | 0.01Hz |  | UL |
| 166 | uwLFRTTime 2EE | LFRT2 Time | R/W |  | 20ms |  | UL |
| 167 | uwHFRTEE | HFRT1 Freq | R/W | 5500~650 0 | 0.01Hz |  | UL |
| 168 | uwHFRTTim eEE | HFRT1 Time | R/W |  | 20ms |  | UL |

| 169 | uwHFRT2EE | HFRT2 Freq | R/W | 5500~650 0 | 0.01Hz |  | UL |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 170 | uwHFRTTim e2EE | HFRT2 Time | R/W |  | 20ms |  | UL |
| 171 | uwHVRTEE | HVRT1 Volt | R/W |  | 0.001 Un |  | UL |
| 172 | uwHVRTTim eEE | HVRT1 Time | R/W |  | 20ms |  | UL |
| 173 | uwHVRT2EE | HVRT2 Volt | R/W |  | 0.001 Un |  | UL |
| 174 | uwHVRTTim e2EE | HVRT2 Time | R/W |  | 0.001 Un |  | UL |
| 175 | uwUnderFU ploadDelayTi me | UnderF UploadDelayTime | R/W | 0-2s | 50ms | 0s | 50549 |
| 176 | uwUnderFU ploadRateEE | UnderF UploadRate | R/W |  |  |  | 50549 |
| 177 | uwGridResta rt_H_Freq | GridRestart HighFreq | R/W |  | 0.01Hz |  | 50549 |
| 178 | OverFDeratR esponseTim e | OverFDerat ResponseTime | W/R | 0-500 |  |  |  |
| 179 | UnderFUplo adResponse Time | UnderFUpload ResponseTime | W/R | 0-500 |  |  |  |
| Intelligent control reads relevant data, used to identify the logo 180-200 |  |  |  |  |  |  |  |
| 180 | MeterLink | Whether to elect the meter | R/W |  |  |  | 0: Missed, 1: Received |
| 181 | OPT Number | Number of connection optimizers | R/W | 0-64 |  |  | The total number of optimizers connected to the inverter |
| 182 | OPT ConfigOK Flag | Optimizer configuration completion flag | R/W |  |  |  | 0x00:Not configured success 0x01:Configuration is complete |
| 183 | PvStrScan | String Num | R/W | 0、8、16、 32 |  |  | 0：Not support Other：PvString Num |
| 184 | BDCLinkNum | BDC parallel Num | R/W |  |  |  | The number of BDCs connected to the current machine Default is 0 |

| 185 | PackNum |  | Number of battery modules | R |  |  |  | Total number of battery modules currently associated with all BDCs |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 186 | Reserved |  |  |  |  |  |  |  |
| 187 | VPP function enable status |  | VPP function enable status | R |  |  |  | 0：Disable 1：Enable |
| 188 | dataLog Connect Server status |  | dataLog Connect Server status |  |  |  |  | 0：connection succeeded 1：Connection failed |
| …… |  |  |  |  |  |  |  |  |
| 200 | Reserved |  |  |  |  |  |  | Reserved |
| 201 | PID Working Model |  | PID Operating mode | W | 0: automati c 1: continuo us 2: All night |  |  |  |
| 202 | PID On/Off Ctrl |  | PID Break control | W | 0:On 1:Off |  |  |  |
| 203 | PID Option | Volt | PID Output voltage option | W | 300~1000 | V |  |  |
| …… |  |  |  |  |  |  |  | Reserved |
| 209 | New Serial | NO | Serial number 1-2 |  |  | ASCII |  |  |
| 210 | New Serial | NO | Serial number 3-4 |  |  | ASCII |  |  |
| 211 | New Serial | NO | Serial number 5-6 |  |  | ASCII |  |  |
| 212 | New Serial | NO | Serial number 7-8 |  |  | ASCII |  |  |
| 213 | New Serial | NO | Serial number 9-10 |  |  | ASCII |  |  |
| 214 | New Serial | NO | Serial number 11-12 |  |  | ASCII |  |  |
| 215 | New Serial | NO | Serial number 13-14 |  |  | ASCII |  |  |

| 216 | New Serial | NO | Serial number 15-16 |  |  | ASCII |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 217 | New Serial | NO | Serial number 17-18 |  |  | ASCII |  |  |
| 218 | New Serial | NO | Serial number 19-20 |  |  | ASCII |  |  |
| 219 | New Serial | NO | Serial number 21-22 |  |  | ASCII |  |  |
| 220 | New Serial | NO | Serial number 23-24 |  |  | ASCII |  |  |
| 221 | New Serial | NO | Serial number 25-26 |  |  | ASCII |  |  |
| 222 | New Serial | NO | Serial number 27-28 |  |  | ASCII |  |  |
| 223 | New Serial | NO | Serial number 29-30 |  |  | ASCII |  |  |
| …… |  |  |  |  |  |  |  | Reserved |
| 229 | EnergyAdjus t |  | Power generation incremental calibration coefficient | W/R |  | 0.1% |  | 1-1000,(Percent ratio) |
| 230~249 for growatt debug setting |  |  |  |  |  |  |  |  |
| 230 | IslandDisabl e |  | Island Disable or not. 1:disable 0:Enable | W | 0,1 |  | 0 |  |
| 231 | FanCheck |  | Start Fan Check | W | 1 |  |  |  |
| 232 | EnableNLine |  | Enable N Line of grid | W | 1 |  | 0 |  |
| 233 | wCheckHard ware |  | wCheckHardware Bit0: GFCIBreak; Bit1:SPSDamage Bit8:EepromReadWarni ng Bit9:EEWriteWarning …… |  |  |  |  |  |
| 234 | wCheckHard ware2 |  |  |  |  |  |  | reserved |
| 235 | ubNToGNDD etect |  | Dis/enable N to GND detect function | W | 1:enable 0:disable |  | 1 |  |
| 236 | NonStdVacE nable |  | Enable/Disable Nonstandard Grid voltage range | W | 0-2 |  | 0 | 0:Disable; 1:Enable Voltgrade1 2:Enable Voltgrade2 |
| 237 | uwEnableSp ecSet |  | Disablse/enable appointed spec setting | W | 1:enable 0:disable | Binary | 0x000 0 | Bit 0: Hungary |

| 238 | Fast MPPT enable | About Fast mppt |  | 0,1,2 |  | 0 | Reserved |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 239 | / | / | / | / |  | / | Reserved |
| 240 | Check Step |  | W |  |  |  |  |
| 241 | INV-Lng | Inverter Longitude | W |  |  |  | Longitude |
| 242 | INV-Lat | Inverter Latitude | W |  |  |  | Latitude |
| …… |  |  |  |  |  |  | Reserved |
| 303 |  |  |  |  |  |  | Reserved |
| 304 | uwAntiBackf lowFailPowe rLimitEE | Anti-backflow failure power percentage | R/W | 0-1000 | 0.1% |  | Anti-backflow failure default setting power percentage |
| 305 | Qloadspeed | Reactive loading speed | R/W | 0-100 | 1% |  | Reactive power adjustment speed setting item, n%Pn/s, 0 means that the loading speed is not enabled, that is, it is directly loaded to the set value |
| 306 | bParallelAnti BackflowEna ble | ParallelAnti-Backflow Enable | R/W | 0-1 |  |  | Parallel anti-Backflow open enable bit 1: enable 0:disable |
| 307 | uwAntiBackf lowFailureRe sponseTime | AntiBackflowFailure ResponseTime | R/W | 1-5000 | 1s |  | AntiBackflow Failure Response Time |
| 308 | uwParallelAn tiBackflowPo werLimitEE | ParallelAntiBackflowPo wer | R/W | 0-1000 | 0.1% |  | Parallel AntiBackflow Power |
|  |  |  |  |  |  |  | limit value setting |
| 309 | bISOCheckC md | ISO detection command | R/W | 0-1 | 1 |  | ISO detection command |
| 310 | bGPRSStatus | GPRS Status 1: module not working 2: no sim card 3: No internet - TCP not connecting to server - TCP connection succeeded | R/W | 0-255 | 1 |  |  |
| 311 | uwQmax_In ductive | The inductive Qmax of the Q(V) curve | R/W | 0-1000 | 0.1% |  |  |
| 312 | uwQmax_Ca | The Capactive Qmax of | R/W | 0-1000 | 0.1% |  |  |

|  | pactive | the Q(V) curve |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 313 | uwReactiveP owerAdjustF ailureRespon seTime | ReactivePowerAdjust Failur ResponseTime | R/W | 0-5000 | S |  |  |
| 314 | bSuperAntiB ackflowEnab le | SuperAntiBackflow Enable | R/W |  |  |  | 0：disable，1：enable |
| 315 | uwReactiveP owerStableT ime | ReactivePowerStableTi me | R/W | 0-200 | S |  |  |
| 316 | uwQpStable Time | QpStableTime | R/W | 0-200 | S |  |  |
| 317 | uwPuDerate Time | PuDerateTime | R/W | 0-200 | S |  |  |
| 318 | uwQVModel Q2Point | QV mode Q2 set point reactive power percentage | R/W | 0-2000 | 0.1% |  | Capacitive 30% （ The corresponding setting is 700)； Inductive 30% (The corresponding setting is 1300)； used for IEE1547 |
| 319 | uwQVModel Q3Point | QV mode Q3 set point reactive power percentage | R/W | 0-2000 | 0.1% |  |  |
| 320 | bVrefModel Enable | VrefModelEnable | R/W | - ： Vref mode for QV curve is not active - ： Vref mode for QV curve is active |  |  | When the Vref mode is not activated, the V1~V4 and Q1~Q4 upper computer of the QV curve can be adjusted; When Vref mode is activated, V1~V4 of the QV curve are determined with Vref and cannot be changed, and Q1~Q4 can be modified by the host computer .used for IEE1547 |
| 321 | uwVrefMod elFilterTime | VrefModelFilterTime | R/W | 0-5000 | S |  | Activate Vref mode, the output filter value is equal to Vref with in the set time .used for IEE1547 |
| 322 | uwUserQPM odeP1Krate | Active power P1 set point percentage for QP mode | R/W | 0-1000 | 0.1% |  | used for IEE1547 |

| 323 | uwUserQPM odeP2Krate | Active power P2 point percentage QP mode | set for | R/W | 0-1000 | 0.1% |  | used for IEE1547 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 324 | uwUserQPM odeP3Krate | Active power P3 point percentage QP mode | set for | R/W | 0-1000 | 0.1% |  | used for IEE1547 |
| 325 | uwUserQPM odeQ1Krate | Reactive power Q1 set point percentage for QP mode |  | R/W | -1000-10 00 | 0.1% |  | -1000~1000：Inductive（100% ~ Capacitive（100%） |
| 326 | uwUserQPM odeQ2Krate | Reactive power Q2 set point percentage for QP mode |  | R/W | -1000-10 00 | 0.1% |  | -1000~1000：Inductive（100% ~ Capacitive（100%） |
| 327 | uwUserQPM odeQ3Krate | Reactive power Q3 set point percentage for QP mode |  | R/W | -1000-10 00 | 0.1% |  | -1000~1000：Inductive（100% ~ Capacitive（100%） |
| 328 | uwAcVoltHig hDeratPowe rLimit | AcVoltHighDeratPower Limit |  | R/W | 0-1000 | 0.1% |  |  |
| 329 | BackflowSin gleCtrl | BackflowSingleCtrl |  | R/W | 0: disable 1: enable |  |  |  |
| 330 | bAntiBackflo wProtectMo de | AntiBackflowProtectM ode |  | R/W | 0-3 |  |  | Used for Australian |
| 331 | uwUnderFU ploadZeroPo werPoint | UnderfreqUploadZeroP owerPoint |  | W |  | 0.01H Z |  |  |
| 332 | FreqDerateZ eroPowerPoi nt | FreqDerateZeroPowerP oint |  | W |  | 0.01H Z |  |  |
| 333 | bFreqDerati ngStopMode Enable | FreqDeratingStopMode Enable |  | R/W | 0-1 |  |  |  |
| 334 | bFreqIncreas ingEnable | FreqIncreasingEnable |  | R/W | 0-1 |  |  |  |
| 335 | uwFreqIncre asingRecove rTime | FreqIncreasingRecover Time |  | R/W |  | 50ms |  |  |
| 336 | uwFreqIncre asingEndLow | FreqIncreasingEndLow Point |  | R/W |  | 0.01H Z |  |  |

）

）

）

|  | Point |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 337 | bFreqIncreas ingStopMod eEnable | FreqIncreasingStopMo deEnable |  | R/W | 0-1 |  |  |  |
| 338 | uwUserQpC hrP1Krate | User QP charge P1 percentage | function, set point | R/W | 0-1000 | 0.1% |  |  |
| 339 | uwUserQpC hrP2Krate | User QP charge P2 percentage | function, set point | R/W | 0-1000 | 0.1% |  |  |
| 340 | uwUserQpC hrP3Krate | User QP charge P3 percentage | function, set point | R/W | 0-1000 | 0.1% |  |  |
| 341 | wUserQpChr Q1Krate | User QP charge Q1 percentage | function, set point | R/W | -1000-10 00 | 0.1% |  | -1000~1000：Inductive（100% ~ Capacitive（100%） |
| 342 | wUserQpChr Q2Krate | User QP charge Q2 percentage | function, set point | R/W | -1000-10 00 | 0.1% |  | -1000~1000：Inductive（100% ~ Capacitive（100%） |
| 343 | wUserQpChr Q3Krate | User QP charge Q3 percentage | function, set point | R/W | -1000-10 00 | 0.1% |  | -1000~1000：Inductive（100% ~ Capacitive（100%） |
| 344 | uwFreqDerat ingRecoverL owPoint | FreqDeratingRecoverLo wPoint |  | R/W |  | 0.01H Z |  |  |
| 345 | uwFreqIncre asingRecove rHighPoint | FreqIncreasingRecover HighPoint |  | R/W |  | 0.01H Z |  |  |
| ……. |  |  |  |  |  |  |  |  |
| 532 | TurnOffUnlo adSpeed | TurnOffUnloadSpeed |  | W/R | 0-1000 |  | 0.1% | 0 means not enabled, that is, the function is not enabled; 1-1000 means n%Pn/min |
| 533 | LimitDevice | Anti-backflow equipment selection |  | W/R | 0-3 |  |  | 1：Meter 3:CT |
|  |  |  |  |  |  |  |  | other meaningless |
| 534 | PowerSetOn DCSourceMo de | Power settings in dc source mode |  | W/R | 0-90000 |  |  | The unit is W |
| 535 | OUFreqGrad e1En | Over-under-frequency |  | W/R | 0-1 |  |  | 0:disable 1:enable |
|  |  | Grade1Enable, |  |  |  |  |  |  |
|  |  | currently only used by |  |  |  |  |  |  |

）

）

）

|  |  | CEI0-21 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 536 | Country Set | Country settings under the same safety regulations | W/R | 0-200 |  |  | For mobile APP use only |
| 538 | InterlockEna ble | Three-machine communication Interlock function mode | W/R | 0-2 |  |  | 0：disable |
|  |  |  |  |  |  |  | 1: Slave Enable 2. host enable |
| 539 | OvTemperDe ratePoint | Over temperature derate point | W/R |  |  |  |  |
| 540 | SafetySetPas sword | Switch between different safety regulations to set the password | W/R |  |  |  |  |
| 541 | AFCI Onoff | AFCI Onoff | W/R | 0xA0/0xA 5 |  |  | 0xA0：AFCI off 0xA5：AFCI on |
| 542 | AfciSelfChec k | AfciSelfCheck | W/R |  |  |  | 0：No self check 1: self check |
| 543 | AfciReset | AfciReset | W/R |  |  |  | 0：Not Reset 1: Reset |
| 544 | AFCIValue1 | AFCIThresholdValue （low） | W/R | 0-65000 |  |  |  |
| 545 | AFCIValue2 | AFCIThresholdValue （middle） | W/R | 0-65000 |  |  |  |
| 546 | AFCIValue3 | AFCIThresholdValue （High） | W/R | 0-65000 |  |  |  |
| 547 | OverThresho ldValueMaxC nt | OverThresholdValueMa xCnt | W/R | 0-255 |  |  |  |
| 548 | AFCIScanTyp eEnable | AFCI curve scan type | W/R | 1~4 |  |  | 1：A road strength |
|  |  |  |  |  |  |  | 2：A road FFT value 3：B road strength 4：B road FFT value |
| 549 | PowerVoltSt opModeEn | PowerVoltStopModeEn | W/R | 0、1 |  |  | 0：disable 1:enable |
|  |  |  |  |  |  |  | The power is restored when the voltage is less than the recovery point |
| 550 | VoltWattRec overTime | Voltage active power recovery time | W/R | 0-15000 | 20ms |  |  |
| 551 | HVoltDerate | Voltage active cut-off | W/R | -5000-11 |  |  |  |

|  | StopPower | power |  |  | 400 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 552 | QVTimeExpo nent | QVTimeExponent |  | WR | 1-255 |  |  | Q varies exponentially with time |  |  |
| 553 | Volt-Watt Watt1 | Voltage active V1 point, corresponding active power |  | WR | 0-11400 |  |  |  |  |  |
| 554 | Volt-Watt Watt2 | Voltage active V2 point, corresponding active power |  | WR | 0-11400 |  |  |  |  |  |
| …… |  |  |  |  |  |  |  |  |  |  |
| 600 | Volt-Var Var1 | Voltage reactive V1 point, Corresponding reactive power percentage(Capacitive |  | WR | 0-1000 |  |  | 0%~100.0%,US regulations | latest | safety |
|  |  | Qmax) |  |  |  |  |  |  |  |  |
| 601 | Volt-Var Var2 | Voltage reactive point, Corresponding react power percentage | V2 ive | WR | 0-1000 |  |  | 0%~100.0%,US regulations | latest | safety |
| 602 | Volt-Var Var3 | Voltage reactive point, Corresponding react power percentage | V3 ive | WR | 0-1000 |  |  | 0%~100.0%,US regulations | latest | safety |
| 603 | Volt-Var Var4 | Voltage reactive point, Corresponding react power percentage(Inductive Qmax) | V4 ive | WR | 0-1000 |  |  | 0%~100.0%,US latest safety regulations |  |  |
| 604 |  |  |  |  |  |  |  |  |  |  |
| 605 | OPModEner gize | Allowed inverter output power |  | R/W | 0/1 |  |  | 0: output power not allowed 1: allowable output power For US models |  |  |
| 608 | OneKeySetB DCMode | One key to set battery mode function |  | R/W |  |  |  | 0: self-use 1: battery priority 2: Grid priority 255：Disable Currently used for US models |  |  |
| 609 | PowerOutpu tEnable | Zero Power Output Enable |  |  |  |  |  | 0：Zero Power Output |  |  |
|  |  |  |  |  |  |  |  | 1：Unlimited output power (default is 1) |  |  |

| 610 | DealDebugP araFlag | Flag bit for clearing debug variables |  |  |  |  | Currently only bit0 and bit1 are used bit0 is used to manually clear the Debug data uploaded to the server bit1 is used to manually clear the fault codes that need to be powered off to clear |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 612 | bAcCoupleE n | AcCoupleEn | R/W | 0-1 |  |  | 0：disable 1：enable |
| ….. |  |  |  |  |  |  |  |
| 660 | ReloadCmd | M3 remote command |  |  |  |  | 0xA0: Initialize safety defaults 0xAA: Reboot M3 remotely |
| Six group for Storage Power |  |  |  |  |  |  |  |
| Register NO. | Variable Name | Description | Write or not | Value | Unit | Initial value | Note |
| 1000. | Float charge current limit | When charge current battery need is lower than this value, enter into float charge | W |  | 0.1A | 600 | CC current |
| 1001. | PF CMD memory state | Set the following 19-22 CMD will be memory ornot(1/0), if not, these settings are the initial value. | W | 0or1, |  | 0 | Means these settings will be acting or not when next power on(02 repeat) |
| 1002. | VbatStartF orDischarg e | LV Vbat | R/W |  | 0.1V |  | Lead-acid battery LV voltage |
| 1003. | VbatlowWa rnClr | LoadPercent(only lead-Acid): 45.5V <20% 48.0V 20%~50% 49.0V >50 | W |  | 0.1V |  | Clear battery low voltage error voltage point |
| 1004. | Vbatstopfo rdischarge | Should stop discharge when lower than this | W |  | 0.01V |  |  |

|  |  | voltage(only lead-Acid): 46.0V <20% 44.8V 20%~50% 44.2V >50% |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1005. | Vbat stop for charge | Should stop charge when higher than this voltage | W |  | 0.01V | 5800 |  |
| 1006. | Vbat start for discharge | Should not discharge when lower than this voltage | W |  | 0.01V | 4800 |  |
| 1007. | Vbat constant charge | can charge when lower than this voltage | W |  | 0.01V | 5800 | CV voltage（acid） |
| 1008. | EESysInfo.S ysSetEn | Bit0：Resved; Bit1：Resved; Bit2：Resved; Bit3：Resved; Bit4：Resved; Bit5：bDischargeEn； Bit6：ForceDischrEn； Bit7：ChargeEn； Bit8：bForceChrEn； Bit9：bBackUpEn； Bit10：bInvLimitLoadE； Bit11：bSpLimitLoadEn； Bit12：bACChargeEn； Bit13：bPVLoadLimitEn; Bit14,15:UnUsed; | W |  |  |  | System Enable |
| 1009. | Battemp lower limit d | Battery temperature lower limit for discharge | W | 0-200:0-2 0℃ 1000-140 0：-40-0℃ | 0.1℃ | 1170 |  |
| 1010. | Bat temp upper limit d | Battery temperature upper limit for discharge | W | 200-1000 | 0.1℃ | 420 |  |
| 1011. | Bat temp lower limit c | Battery temperature lower limit for charge | W | 0-200:0-2 0℃ 1000-140 0：-40-0℃ | 0.1℃ | 30 | Lower temperature limit |

| 1012. | Bat temp upper limit c | Battery temperature upper limit for charge | W | 200-1000 | 0.1℃ | 370 | Upper temperature limit |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1013. | uwUnderFr eDischarge DelyTime | Under Fre Delay Time | s | 0-20 | 50ms |  | Under Fre Delay Time |
| 1014. | BatMdlSeri alNum | Battery serial number | W | 00:00 |  |  | SPH4-11K used |
| 1015. | BatMdlPara llNum | Battery parallel section | W | 00:00 |  |  | SPH4-11K used |
| 1016. | DRMS_EN | / | / | / | / | / | 0：disable 1：enable |
| 1017. | Bat First Start Time 4 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1018. | Bat First Stop Time 4 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1019. | BatFirst on/off Switch 4 | Enable:1 Disable:0 |  | 0 or 1 |  |  | Battery priority enable 1 |
| 1020. | Bat First Start Time 5 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1021. | Bat First Stop Time 5 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1022. | BatFirst on/off Switch 5 | Enable:1 Disable:0 |  | 0 or 1 |  |  | Battery priority enable 1 |
| 1023. | Bat First Start Time 6 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1024. | Bat First Stop Time 6 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1025. | BatFirst on/off Switch 6 | Enable:1 Disable:0 |  | 0 or 1 |  |  | Battery priority enable 1 |
| 1026. | Grid First Start Time | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |

|  | 4 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1027. | Grid First Stop Time 4 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1028. | Grid First Stop Switch 4 | Enable:1 Disable:0 |  | 0 or 1 |  |  | Grid priority enable |
| 1029. | Grid First Start Time 5 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1030. | Grid First Stop Time 5 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1031. | Grid First Stop Switch 5 | Enable:1 Disable:0 |  | 0 or 1 |  |  | Grid priority enable |
| 1032. | Grid First Start Time 6 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1033. | Grid First Stop Time 6 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1034. | Grid First Stop Switch 6 | Enable:1 Disable:0 |  | 0 or 1 |  |  | Grid priority enable |
| 1035. | Bat First Start Time 4 | High eight:hours Low eight: minutes |  | 0-23 0-59 |  |  |  |
| 1036. | / | / | / | / | / | / | Reserve |
| 1037. | bCTMode | Use the CTMode to Choose RFCT \ Cable CT\METER | W | 2:METER 1:cWirele ssCT 0:cWiredC T |  | 0 |  |
| 1038. | CTAdjust | CTAdjust enable | W | 0:disable 1:enable |  | 0 |  |
| 1039. | / | / | / | / | / | / | Reserve |

| 1040. | / | / |  | / |  |  | / |  | / |  | / | Reserve |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1041. | / | / |  | / |  |  | / |  | / |  | / | Reserve |  |
| 1042. | / | / |  | / |  |  | / |  | / |  |  | Reserve |  |
| 1043. | / | / |  | / |  |  | / |  | / |  | / | Reserve |  |
| 1044. | Priority | ForceChrEn/ForceDischr En Load first/bat first /grid first |  | R |  |  | 0.Load(de fault)/1.B attery/2.G rid |  |  |  |  | bForceChrEn/disbForceDischrE n/dis |  |
| 1045. | / | / |  | / |  |  | / |  | / |  | / | Reserve |  |
| 1046. | / | / |  | / |  |  | / |  | / |  | / | Reserve |  |
| 1047. | AgingTestSt ep Cmd | Command for aging test |  |  |  |  | 0: default 1: charge 2: discharge |  |  |  |  | Cmd for aging test |  |
| 1048. | BatteryTyp e | Battery type choose of buck-boost input |  |  |  |  | 0:Lithium 1:Lead-aci d 2:other |  |  |  | 0 | Battery type |  |
| 1049. | / | / |  | / |  |  | / |  | / |  |  | Reserve |  |
| 1050. | / | / |  | / |  |  | / |  | / |  | / | Reserve |  |
| 1051. | / | / |  | / |  |  | / |  | / |  |  | Reserve |  |
| 1052. | / | / |  | / |  |  | / |  | / |  |  | Reserve |  |
| 1053. | / | / |  | / |  |  | / |  | / |  |  | Reserve |  |
| 1054. | / | / |  | / |  |  | / |  | / |  | / | Reserve |  |
| 1060. | BuckUpsFunE n |  | Ups function enable disable |  | or |  |  | 0:disable 1:enable |  |  |  |  |  |

| 1061. | BuckUPSVoltS et | UPS output voltage |  | 0:230 1:208 2:240 |  | 230V |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1062. | UPSFreqSet | UPS output frequency |  | 0:50Hz 1:60Hz |  | 50Hz |  |  |
| ... | / | / | / | / | / | / | reverse |  |
| Priority set |  |  |  |  |  |  |  |  |
| 1070. | GridFirstDisch argePowerRat e | Discharge Power Rate when Grid First | W | 0-100 | 1% | Discharge Power Rate when Grid First |  |  |
| 1071. | GridFirstStopS OC | Stop Discharge soc when Grid First | W | 0-100 | 1% | Stop Discharge soc when Grid First |  |  |
| 1072… 1079 | / | / | / | / | / | / |  | reverse |
| 1080. | Grid First Start Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |  |
| 1081. | Grid First Stop Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |  |
| 1082. | Grid First Stop Switch 1 | Enable :1 Disable:0 |  | 0 or 1 |  | Grid First enable |  |  |
| 1083. | Grid First Start Time 2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |  |
| 1084. | Grid First Stop Time 2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |  |
| 1085. | Grid First Stop Switch 2 | ForceDischarge.bSwitch&L CD_SET_FORCE_TRUE_2)= =LCD_SET_FORCE_TRUE_2 |  | 0 or 1 |  | Grid First enable |  | ForceDischarge; LCD_SET_FORCE_T RUE_2 |
| 1086. | Grid First Start Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |  |
| 1087. | Grid First Stop Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |  |
| 1088. | Grid First Stop Switch 3 | Enable :1 Disable:0 |  | 0 or 1 |  | Grid First enable |  |  |
| 1089. | / | / | / | / | / | / |  | reserve |

| 1090. | BatFirstPower Rate | Charge Power Rate when Bat First | W | 0-100 | 1% | Charge Power Rate when Bat First |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1091. | wBatFirst stop SOC | Stop Charge soc when Bat First | W | 0-100 | 1% | Stop Charge soc when Bat First |  |
| 1092. | AC charge Switch | When Bat First Enable:1 Disable:0 |  | Enable:1 Disable:0 |  | AC Charge Enable |  |
| 1093… 1099 |  |  |  |  |  |  |  |
| 1100. | Bat First Start Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1101. | Bat First Stop Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1102. | BatFirst on/off Switch 1 | Enable :1 Disable:0 |  | 0 or 1 |  | Bat First Enable1 |  |
| 1103. | Bat First Start Time 2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1104. | Bat First Stop Time 2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1105. | BatFirston/off Switch 2 | Enable :1 Disable:0 |  | 0 or 1 |  | Bat First Enable2 |  |
| 1106. | Bat First Start Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1107. | Bat First Stop Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  |  |
| 1108. | BatFirston/off Switch 3 | Enable :1 Disable:0 |  | 0 or 1 |  | Bat First Enable3 |  |
| 1109. | / | / | / | / | / | / | reserve |
| 1110. | Load First Start Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| 1111. | Load First Stop Time 1 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| 1112. | Load First Switch 1 | Enable :1 Disable:0 |  | 0 or 1 |  | Load First Enable | SPA/ reserve |

| 1113. | Load First Start Time2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1114. | Load First Stop Time 2 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| 1115. | Load First Switch 2 | Enable :1 Disable:0 |  | 0 or 1 |  | Load First Enable | SPA/ reserve |
| 1116. | Load First Start Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| 1117. | Load First Stop Time 3 | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 |  |  | SPA/ reserve |
| 1118. | Load First Switch 3 | Enable :1 Disable:0 |  | 0 or 1 |  | Load First Enable | SPA/ reserve |
| 1119. | NewEPowerC alcFlag | / | / | / | / | / | 0：The old formula 1 ： The new formula |
| 1120. | BackUpEn | BackUp Enable |  |  |  |  | MIX US |
| 1121. | SGIPEn | SGIP Enable |  |  |  |  | MIX US |
| ……… | 1122~1124 | / | / | / | / | / | reserve |
| 1125 | BatSerialNO. 8 | Product serial number of the first PACK of energy storage batteries | / | / | ASCII |  |  |
| 1126 | BatSerialNO. 7 |  | / | / | ASCII |  |  |
| 1127 | BatSerialNO. 6 |  | / | / | ASCII |  |  |
| 1128 | BatSerialNO. 5 |  | / | / | ASCII |  |  |
| 1129 | BatSerialNO. 4 |  | / | / | ASCII |  |  |
| 1130 | BatSerialNO. 3 |  | / | / | ASCII |  |  |
| 1131 | BatSerialNO. 2 |  | / | / | ASCII |  |  |
| 1132 | BatSerialNO. 1 |  | / | / | ASCII |  |  |
| 1132 ~1204 | BatSerialNO. 8~ BatSerialNO. 1 | The serial number of the second to tenth packs of the energy storage battery consists of nine packs, and | / | / | ASCII |  |  |

|  |  |  | the format of the serial number of each PACK is 1125 to 1132 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| …… |  |  |  |  |  |  |  |  |
| 1244 | Com version NameH |  | Name of the battery main control firmware version |  |  | ASCII |  |  |
| 1245 | Com version NameL |  | Name of the battery main control firmware version |  |  | ASCII |  |  |
| 1246 | Com version No |  | Version of the battery main control firmware |  |  | digital |  |  |
| 1247 | Com version NameH |  | Name of battery monitoring firmware version |  |  | ASCII |  |  |
| 1248 | Com version NameL |  | Name of battery monitoring firmware version |  |  | ASCII |  |  |
| 1249 | Com version No |  | Battery monitoring firmware version |  |  | digital |  |  |
| Use for TL-X and TL-XH |  |  |  |  |  |  |  |  |
| 3000 | ExportLimitFa iledPowerRat e |  | The power rate when exportLimit failed | R/W |  | 0.1% |  | The power rate when exportLimit failed |
| 3001 | New Serial | NO | Serial number 1-2 | R/W |  | ASCII |  | The new model uses the following registers to record the serial number; The representation is the same as the original: one register holds two characters and the new serial number is 30 characters. |
| 3002 | New Serial | NO | Serial number 3-4 | R/W |  | ASCII |  |  |
| 3003 | New Serial | NO | Serial number 5-6 | R/W |  | ASCII |  |  |
| 3004 | New Serial | NO | Serial number 7-8 | R/W |  | ASCII |  |  |
| 3005 | New Serial | NO | Serial number 9-10 | R/W |  | ASCII |  |  |
| 3006 | New Serial | NO | Serial number 11-12 | R/W |  | ASCII |  |  |
| 3007 | New Serial | NO | Serial number 13-14 | R/W |  | ASCII |  |  |
| 3008 | New Serial | NO | Serial number 15-16 | R/W |  | ASCII |  |  |

| 3009 | New Serial NO | Serial number 17-18 | R/W |  | ASCII |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3010 | New Serial NO | Serial number 19-20 | R/W |  | ASCII |  |  |
| 3011 | New Serial NO | Serial number 21-22 | R/W |  | ASCII |  |  |
| 3012 | New Serial NO | Serial number 23-24 | R/W |  | ASCII |  |  |
| 3013 | New Serial NO | Serial number 25-26 | R/W |  | ASCII |  |  |
| 3014 | New Serial NO | Serial number 27-28 | R/W |  | ASCII |  |  |
| 3015 | New Serial NO | Serial number 29-30 | R/W |  | ASCII |  |  |
| 3016 | DryContactFu ncEn | DryContact function enable | R/W | 0:Disable 1: Enable |  |  | DryContact function enable |
| 3017 | DryContactOn Rate | The power rate of drycontact turn on | R/W | 0~1000 | 0.1% |  | The power rate of drycontact turn on |
| 3018 | bWorkMode | WorkMode----0:default,1: System Retrofit 2: Multi-Parallel | R/W | 0、1、2 |  |  | MIN2.5~6KTL-XH/ XA Double CT special |
| 3019 | DryContactOf fRate | DryContactOffRate | Dry contact closure power | R/W | 0~100 0 | 0.1% | Dry contact closure power pe rcentage |
| 3020 | BoxCtrlInvOrd er | BoxCtrlInvOrder | Off-net box control instruct ion | R/W |  |  |  |
| 3021 | ExterCommOf fGridEn | External communication setting manual off-network enable | R/W |  |  |  | 0x00: Disable; （default） 0x01: Enable; |
| 3022 | uwBdcStopW orkOfBusVolt | BdcStopWorkOfBusVolt | R |  |  |  |  |
| 3023 | bGridType | GridType---0:SinglePhase 1:ThreePhase 2:SplitPhase | R/W | 0、1、2 |  |  | MIN2.5~6KTL-XH/ XA Double CT special |
| 3024 | Float charge current limit | When charge current battery need is lower than | R/W |  | 0.1A | 600 | CC current |

|  |  | this value, enter into float charge |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3025 | VbatWarning | "Battery-low" warning setup voltage | R/W |  | 0.1V | 4800 | Lead acid battery LV voltage |
| 3026 | VbatlowWarn Clr | "Battery-low" warning clear voltage | R/W |  | 0.1V |  | Clear battery low voltage error voltage point LoadPercent(only lead-Acid): 45.5V(Load < 20%); 48.0V(20%<=Load <=50%); 49.0V(Load > 50%); |
| 3027 | Vbatstopfordi scharge | Battery cut off voltage | R/W |  | 0.1V |  | Should stop discharge when lower than this voltage(only lead-Acid): 46.0V(Load < 20%); 44.8V(20%<=Load <=50%); 44.2V(Load > 50%); |
| 3028 | Vbat stop for charge | Battery over charge voltage | R/W |  | 0.01V | 5800 | Should stop charge when higher than this voltage |
| 3029 | Vbat start for discharge | Battery start discharge voltage | R/W |  | 0.01V | 4800 | Should not discharge when lower than this voltage |
| 3030 | Vbat constant charge | Battery constant charge voltage | R/W |  | 0.01V | 5800 | CV voltage（acid） can charge when lower than this voltage |

| 3031 | Battemp lower limit d | Battery temperature lower limit for discharge | R/W |  | 0.1℃ | 1170 | 0-200:0-20℃ 1000-1400： -40-0℃ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3032 | Bat temp upper limit d | Battery temperature upper limit for discharge | R/W |  | 0.1℃ | 420 |  |
| 3033 | Bat temp lower limit c | Battery temperature lower limit for charge | R/W |  | 0.1℃ | 30 | Battery temperature lower limit 0-200:0-20℃ 1000-1400： -40-0℃ |
| 3034 | Bat temp upper limit c | Battery temperature upper limit for charge | R/W |  | 0.1℃ | 370 | Battery temperature upper limit |
| 3035 | uwUnderFreD ischargeDelyT ime | Under Fre Delay Time | R/W |  | 50ms |  | Under Fre Delay Time |
| 3036 | GridFirstDisch argePowerRat e | Discharge Power Rate when Grid First |  |  |  | 1-255 |  |
| 3037 | GridFirstStopS OC | Stop Discharge soc when Grid First |  |  |  | 1-100 |  |
| 3038 | Time 1(xh) | Period 1: [Start Time ~ End Time], [Charge/Discharge], [Disable/Enable] 3038 enable, charge and discharge, start time, end time 3039 | R/W |  |  |  | Bit0~7: minutes; Bit8~12: hour; Bit13~14, 0: load priority; 1: battery priority; 2: Grid priority; Bit15, 0: prohibited; 1: enabled; |
| 3039 |  |  | R/W |  |  |  | Bit0~7: minutes; Bit8~12: hour; Bit13~15: reserved |
| 3040 | Time 2(xh) | Time period 2: [start time ~ end time], [charge / discharge], [disable / enable] 3040 enable, charge and discharge, start time, 3041 end time | R/W |  |  |  | Bit0~7: minutes; Bit8~12: hour; Bit13~14, 0: load priority; 1: battery priority; 2: Grid priority; Bit15, 0: prohibited; 1: |

|  |  |  |  |  |  |  | enabled; |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3041 |  |  | R/W |  |  |  | Bit0~7: minutes; Bit8~12: hour; Bit13~15: reserved |
| 3042 | Time 3(xh) | With Time1 | R/W |  |  |  | With Time1 |
| 3043 |  |  | R/W |  |  |  | With Time1 |
| 3044 | Time 4(xh) | With Time1 | R/W |  |  |  | With Time1 |
| 3045 |  |  | R/W |  |  |  | With Time1 |
| 3046 | 预留 |  |  |  |  |  |  |
| 3047 | BatFirstPower Rate | Charge Power Rate when Bat First |  |  |  | 1-100 |  |
| 3048 | wBatFirst stop SOC | Stop Charge soc when Bat First |  |  |  | 1-100 |  |
| 3049 | AcChargeEna ble | AcChargeEnable |  |  |  |  | Enable :1 Disable:0 |
| 3050 | Time 5(xh) | With Time1 | R/W |  |  |  | With Time1 |
| 3051 |  |  | R/W |  |  |  | With Time1 |
| 3052 | Time 6(xh) | With Time1 | R/W |  |  |  | With Time1 |
| 3053 |  |  | R/W |  |  |  | With Time1 |
| 3054 | Time 7(xh) | With Time1 | R/W |  |  |  | With Time1 |
| 3055 |  |  | R/W |  |  |  | With Time1 |
| 3056 | Time 8(xh) | With Time1 | R/W |  |  |  | With Time1 |
| 3057 |  |  | R/W |  |  |  | With Time1 |
| 3058 | Time 9(xh) | With Time1 | R/W |  |  |  | With Time1 |
| 3059 |  |  | R/W |  |  |  | With Time1 |
| 3060~ 3069 | Reserved |  |  |  |  |  |  |

| 3070 | BatteryType | Battery type choose of buck-boost input | R/W |  |  |  | Battery type 0:Lithium 1:Lead-acid 2:other |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3071 | BatMdlSeria/ ParalNum | BatMdlSeria/ParalNum | R/W |  |  |  | BatMdlSeria/Paral Num; SPH4-11K used The upper 8 bits indicate the number of series segments； The lower 8 bits indicate the number of parallel sections; |
| 3072 | Reserved |  |  |  |  |  |  |
| 3073 | Reserved |  |  |  |  |  |  |
| 3074 | Reserved |  |  |  |  |  |  |
| 3075 | Reserved |  |  |  |  |  |  |
| 3076 | Reserved |  |  |  |  |  |  |
| 3077 | Reserved |  |  |  |  |  |  |
| 3078 | Reserved |  |  |  |  |  |  |
| 3079 | UpsFunEn | Ups function enable or disable | R/W |  |  | 0 | 0:disable 1:enable |
| 3080 | UPSVoltSet | UPS output voltage | R/W |  |  | 0 | 0:230V 1:208V 2:240V |
| 3081 | UPSFreqSet | UPS output frequency | R/W |  |  | 0 | 0:50Hz 1:60Hz |
| 3082 | bLoadFirstSto pSocSet | StopSoc When LoadFirst | R/W |  |  | 13-100 | ratio |
| 3083 | Reserved |  |  |  |  |  |  |
| 3084 | Reserved |  |  |  |  |  |  |
| 3085 | Com Address | Communication addr | R/W |  |  | 1 | 1 : Communication addr=1 1 ~ 254 : Communication addr=1~254 |
| 3086 | BaudRate | Communication BaudRate | R/W |  |  | 0 | 0: 9600 bps 1: 38400 bps |
| 3087 | Serial NO. 1 | Serial Number 1-2 | R/W |  | ASCII |  | For battery |

| 3088 | Serial NO. 2 | Serial Number 3-4 |  | R/W |  | ASCII |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3089 | Serial NO. 3 | Serial Number 5-6 |  | R/W |  | ASCII |  |  |
| 3090 | Serial NO. 4 | Serial Number 7-8 |  | R/W |  | ASCII |  |  |
| 3091 | Serial No. 5 | Serial Number 9-10 |  | R/W |  | ASCII |  |  |
| 3092 | Serial No.6 | Serial Number 11-12 |  | R/W |  | ASCII |  |  |
| 3093 | Serial No. 7 | Serial Number 13-14 |  | R/W |  | ASCII |  |  |
| 3094 | Serial No. 8 | Serial Number 15-16 |  | R/W |  | ASCII |  |  |
| 3095 | BdcResetCmd | BDC Reset command |  | R/W |  |  |  | 0：Invalid data 1：Reset setting parameters 2：Reset correction parameter 3：Clear historical power |
| 3096 | ARKM3 Code | BDCMonitoring software code |  | R |  | ASCII |  | ZEBA |
| 3097 |  |  |  |  |  |  |  |  |
| 3098 | DTC | DTC |  | R |  |  |  |  |
| 3099 | FW Code | DSP software code |  | R |  | ASCII |  |  |
| 3100 |  |  |  |  |  |  |  |  |
| 3101 | Processor1 FW Vision | DSP Software Version |  | R |  | ASCII |  |  |
| 3102 | BusVoltRef | Minimum BUS voltage for charging and discharging batteries |  | R |  |  |  |  |
| 3103 | ARKM3Ver | BDC monitoring software version |  | R |  |  |  |  |
| 3104 | BMS_MCUVer sion | BMS hardware version information | R |  | 1 |  |  |  |
| 3105 | BMS_FW | BMS software version information | R |  | 1 |  |  |  |
| 3106 | BMS_Info | BMS ManufacturerName | R |  | 1 |  |  |  |
| 3107 | BMSCommTy pe | BMSCommType | R |  | 1 |  |  | BMSCommunicati on interface type： 0: RS485; 1: CAN; |
| 3108 | Module 4 | BDCmodel (4) |  | R/W | &*11 |  |  | SxxBxx |
| 3109 | Module 3 | BDCmodel (3) |  | R/W | &*11 |  |  | DxxTxx |

| 3110 | Module 2 | BDCmodel (2) | R/W | &*11 |  |  | PxxUxx |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3111 | Module 1 | BDCmodel (1) | R/W | &*11 |  |  | Mxxxx |
| 3112 | Reserved |  |  |  |  |  |  |
| 3113 | unProtocolVe r | BDCProtocolVer | R | 1 |  |  | Bit8-bit15 The major version number ranges from 0-256. In principle, it cannot be changed Bit0-bit7 Minor version number [0-256]. If the protocol is changed, you need to update this version No. |
| 3114 | uwCertificatio nVer | BDC CertificationVer | R | 1 |  |  |  |
| 3115 ~ 3124 | Reserved |  |  |  |  |  |  |
| US Machine type Time Set |  |  |  |  |  |  |  |
| 3125 | Time Month1 | Use with Time1-9（us） ，Add month time | R/W |  |  |  | bit0~3:month_L； bit4~7: month_H bit8, 0:disable 1：enable Bit9~15:reserve |
| 3126 | Time Month2 | Use with Time10-18（us） ，Add month time | R/W |  |  |  | With Time Month1 |
| 3127 | Time Month3 | Use with Time19-27（us） ，Add month time | R/W |  |  |  | With Time Month1 |
| 3128 | Time Month4 | Use with Time28-36（us） ，Add month time | R/W |  |  |  | With Time Month1 |
| 3129 | Time 1（us） | time1：[starttime~endtime] | R/W | [Charge/ discharg e/counte r |  |  | bit0~6:min； bit7~11:hour； bit12~14, 0:loadfirst; |

|  |  |  |  | current], [disable/ enable] |  |  | 1:batfirst； 2:gridfirst； 3: anti-reflux bit15, 0:disable; 1:enable; |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3130 |  |  | R/W |  |  |  | bit0~6:min； bit7~11:hour； bit12-13, 0:Weekday 1:Weekend 2:WeeK bit14~15：reserve |
| 3131-3 132 | Time 2（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3133-3 134 | Time 3（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3135-3 136 | Time 4（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3137-3 138 | Time 5（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3139-3 140 | Time 6（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3141-3 142 | Time 7（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3143-3 144 | Time 8（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3145-3 146 | Time9（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3147-3 148 | Time 10（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3149-3 150 | Time 11（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3151-3 152 | Time 12（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3153-3 154 | Time 13（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3155-3 156 | Time 14（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3157-3 158 | Time15（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |

| 3159-3 160 | Time 16（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3161-3 162 | Time 17（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3163-3 164 | Time 18（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3165-3 166 | Time 19（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3167-3 168 | Time 20（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3169-3 170 | Time 21（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3171-3 172 | Time 22（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3173-3 174 | Time 23（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3175-3 176 | Time 24（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3177-3 178 | Time 25（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3179-3 180 | Time 26（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3181-3 182 | Time 27（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3183-3 184 | Time 28（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3185-3 186 | Time 29（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3187-3 188 | Time 30（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3189-3 190 | Time 31（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3191-3 192 | Time 32（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3193-3 194 | Time 33（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3195-3 196 | Time 34（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3197-3 198 | Time 35（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |
| 3199-3 200 | Time 36（us） | Same as above | R/W |  |  |  | Same as Time 1 （us） |

| 3201 | SpecialDay1 | SpecialDay1（month，Day） | R/W |  |  |  | bit0~7:day； bit8~14:month bit15， 0：disable 1： enable |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3202 | SpecialDay1_ Time1 | Start time | R/W |  |  |  | bit0~6:min； bit7~11:hour； bit12~14, 0:loadfirst; 1:batfirst； 2:gridfirst； 3: anti-reflux bit15, 0: disable; 1: enable; |
| 3203 |  | endtime | R/W |  |  |  | bit0~6:min； bit7~11:hour； bit12~15：reserve |
| 3204-3 205 | SpecialDay1_ Time2 | Same as above | R/W |  |  |  | Same as SpecialDay1_Time 1 |
| 3206-3 207 | SpecialDay1_ Time3 | Same as above | R/W |  |  |  | Same as SpecialDay1_Time 1 |
| 3208-3 209 | SpecialDay1_ Time4 | Same as above | R/W |  |  |  | Same as SpecialDay1_Time 1 |
| 3210-3 211 | SpecialDay1_ Time5 | Same as above | R/W |  |  |  | Same as SpecialDay1_Time 1 |
| 3212-3 213 | SpecialDay1_ Time6 | Same as above | R/W |  |  |  | Same as SpecialDay1_Time 1 |
| 3214-3 215 | SpecialDay1_ Time7 | Same as above | R/W |  |  |  | Same as SpecialDay1_Time 1 |
| 3216-3 217 | SpecialDay1_ Time8 | Same as above | R/W |  |  |  | Same as SpecialDay1_Time 1 |
| 3218-3 219 | SpecialDay1_ Time9 | Same as above | R/W |  |  |  | Same as SpecialDay1_Time 1 |

| 3220 | SpecialDay2 | SpecialDay2（month，Day） | R/W |  |  |  | bit0~7:day； bit8~14:month bit15， 0：disable 1：enable |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3221 | SpecialDay2_ Time1 | Start time | R/W |  |  |  | bit0~6: min； bit7~11: hour； bit12~14, 0: loadfirst; 1: batfirst； 2: gridfirst； 3: anti-reflux bit15, 0: disable; 1: enable; |
| 3222 |  | endtime | R/W |  |  |  | bit0~6: min； bit7~11: hour； bit12~15：reserve |
| 3223-3 224 | SpecialDay2_ Time2 | Same as above | R/W |  |  |  | Same as SpecialDay2_Time 1 |
| 3225-3 226 | SpecialDay2_ Time3 | Same as above | R/W |  |  |  | Same as SpecialDay2_Time 1 |
| 3227-3 228 | SpecialDay2_ Time4 | Same as above | R/W |  |  |  | Same as SpecialDay2_Time 1 |
| 3229-3 230 | SpecialDay2_ Time5 | Same as above | R/W |  |  |  | Same as SpecialDay2_Time 1 |
| 3231-3 232 | SpecialDay2_ Time6 | Same as above | R/W |  |  |  | Same as SpecialDay2_Time 1 |
| 3233-3 234 | SpecialDay2_ Time7 | Same as above | R/W |  |  |  | Same as SpecialDay2_Time 1 |
| 3235-3 236 | SpecialDay2_ Time8 | Same as above | R/W |  |  |  | Same as SpecialDay2_Time 1 |
| 3237-3 238 | SpecialDay2_ Time9 | Same as above | R/W |  |  |  | Same as SpecialDay2_Time 1 |
| 3239-3 249 | Reserve | Reserve | R/W |  |  |  |  |
| BDC information (support up to 10 parallel BDC) |  |  |  |  |  |  |  |
| 5000-5039 |  | 1 |  |  | Reference 3085 to 3124 for a total of 40 registers Description |  |  |
| 5040-5079 |  | 2 |  |  |  |  |  |
| 5000+(N-1)*40--- 5039+(N-1)*40 |  | N |  |  |  |  |  |

## Input Reg

| NO. | Variable Name |  | Description | Value | Unit | Note |
| --- | --- | --- | --- | --- | --- | --- |
| First group |  |  |  |  |  |  |
| 0. |  | Inverter Status | Inverter run state | 0:waiting, 1:normal, 3:fault |  |  |
| 1. |  | Ppv H | Input power (high) |  | 0.1W |  |
| 2. |  | Ppv L | Input power (low) |  | 0.1W |  |
| 3. |  | Vpv1 | PV1 voltage |  | 0.1V |  |
| 4. |  | PV1Curr | PV1 input current |  | 0.1A |  |
| 5. |  | Ppv1 H | PV1 input power(high) |  | 0.1W |  |
| 6. |  | Ppv1 L | PV1 input power(low) |  | 0.1W |  |
| 7. |  | Vpv2 | PV2 voltage |  | 0.1V |  |
| 8. |  | PV2Curr | PV2 input current |  | 0.1A |  |
| 9. |  | Ppv2 H | PV2 input power (high) |  | 0.1W |  |
| 10. |  | Ppv2 L | PV2 input power (low) |  | 0.1W |  |
| 11. |  | Vpv3 | PV3 voltage |  | 0.1V |  |
| 12. |  | PV3Curr | PV3 input current |  | 0.1A |  |
| 13. |  | Ppv3 H | PV3 input power (high) |  | 0.1W |  |
| 14. |  | Ppv3 L | PV3 input power (low) |  | 0.1W |  |
| 15. |  | Vpv4 | PV4 voltage |  | 0.1V |  |
| 16. |  | PV4Curr | PV4 input current |  | 0.1A |  |
| 17. |  | Ppv4 H | PV4 input power (high) |  | 0.1W |  |
| 18. |  | Ppv4 L | PV4 input power (low) |  | 0.1W |  |
| 19. |  | Vpv5 | PV5 voltage |  | 0.1V |  |
| 20. |  | PV5Curr | PV5 input current |  | 0.1A |  |
| 21. |  | Ppv5H | PV5 input power(high) |  | 0.1W |  |
| 22. |  | Ppv5 L | PV5 input power(low) |  | 0.1W |  |
| 23. |  | Vpv6 | PV6 voltage |  | 0.1V |  |
| 24. |  | PV6Curr | PV6 input current |  | 0.1A |  |

| 25. | Ppv6 H | PV6 input power (high) |  | 0.1W |  |
| --- | --- | --- | --- | --- | --- |
| 26. | Ppv6 L | PV6 input power (low) |  | 0.1W |  |
| 27. | Vpv7 | PV7 voltage |  | 0.1V |  |
| 28. | PV7Curr | PV7 input current |  | 0.1A |  |
| 29. | Ppv7 H | PV7 input power (high) |  | 0.1W |  |
| 30. | Ppv7 L | PV7 input power (low) |  | 0.1W |  |
| 31. | Vpv8 | PV8 voltage |  | 0.1V |  |
| 32. | PV8Curr | PV8 input current |  | 0.1A |  |
| 33. | Ppv8 H | PV8 input power (high) |  | 0.1W |  |
| 34. | Ppv8 L | PV8 input power (low) |  | 0.1W |  |
| 35. | Pac H | Output power (high) |  | 0.1W |  |
| 36. | Pac L | Output power (low) |  | 0.1W |  |
| 37. | Fac | Grid frequency |  | 0.01Hz |  |
| 38. | Vac1 | Three/single phase grid voltage |  | 0.1V |  |
| 39. | Iac1 | Three/single phase grid output current |  | 0.1A |  |
| 40. | Pac1 H | Three/single phase grid output watt VA (high) |  | 0.1VA |  |
| 41. | Pac1 L | Three/single phase grid output watt VA(low) |  | 0.1VA |  |
| 42. | Vac2 | Three phase grid voltage |  | 0.1V |  |
| 43. | Iac2 | Three phase grid output current |  | 0.1A |  |
| 44. | Pac2 H | Three phase grid output power (high) |  | 0.1VA |  |
| 45. | Pac2 L | Three phase grid output power (low) |  | 0.1VA |  |
| 46. | Vac3 | Three phase grid voltage |  | 0.1V |  |
| 47. | Iac3 | Three phase grid output current |  | 0.1A |  |
| 48. | Pac3 H | Three phase grid output power (high) |  | 0.1VA |  |
| 49. | Pac3 L | Three phase grid output power (low) |  | 0.1VA |  |
| 50. | Vac_RS | Three phase grid voltage |  | 0.1V | Line voltage |
| 51. | Vac_ST | Three phase grid voltage |  | 0.1V | Line voltage |
| 52. | Vac_TR | Three phase grid voltage |  | 0.1V | Line voltage |
| 53. | Eactoday H | Today generate energy (high) |  | 0.1kWH |  |
| 54. | Eac today L | Today generate energy (low) |  | 0.1kWH |  |
| 55. | Eac total H | Total generate energy (high) |  | 0.1kWH |  |
| 56. | Eac total L | Total generate energy (low) |  | 0.1kWH |  |
| 57. | Time total H | Work time total (high) |  | 0.5s |  |
| 58. | Time total L | Work time total (low) |  | 0.5s |  |
| 59. | Epv1_today H | PV1Energy today(high) |  | 0.1kWh |  |
| 60. | Epv1_today L | PV1Energy today (low) |  | 0.1kWh |  |
| 61. | Epv1_total H | PV1Energy total(high) |  | 0.1kWh |  |
| 62. | Epv1_total L | PV1Energy total (low) |  | 0.1kWh |  |
| 63. | Epv2_today H | PV2Energy today(high) |  | 0.1kWh |  |

| 64. | Epv2_today L | PV2Energy today (low) |  | 0.1kWh |  |
| --- | --- | --- | --- | --- | --- |
| 65. | Epv2_total H | PV2Energy total(high) |  | 0.1kWh |  |
| 66. | Epv2_total L | PV2Energy total (low) |  | 0.1kWh |  |
| 67. | Epv3_today H | PV3 Energy today(high) |  | 0.1kWh |  |
| 68. | Epv3_today L | PV3 Energy today (low) |  | 0.1kWh |  |
| 69. | Epv3_total H | PV3 Energy total(high) |  | 0.1kWh |  |
| 70. | Epv3_total L | PV3 Energy total (low) |  | 0.1kWh |  |
| 71. | Epv4_today H | PV4Energy today(high) |  | 0.1kWh |  |
| 72. | Epv4_today L | PV4Energy today (low) |  | 0.1kWh |  |
| 73. | Epv4_total H | PV4Energy total(high) |  | 0.1kWh |  |
| 74. | Epv4_total L | PV4Energy total (low) |  | 0.1kWh |  |
| 75. | Epv5_today H | PV5Energy today(high) |  | 0.1kWh |  |
| 76. | Epv5_today L | PV5Energy today (low) |  | 0.1kWh |  |
| 77. | Epv5_total H | PV5Energy total(high) |  | 0.1kWh |  |
| 78. | Epv5_total L | PV5Energy total (low) |  | 0.1kWh |  |
| 79. | Epv6_today H | PV6Energy today(high) |  | 0.1kWh |  |
| 80. | Epv6_today L | PV6Energy today (low) |  | 0.1kWh |  |
| 81. | Epv6_total H | PV6Energy total(high) |  | 0.1kWh |  |
| 82. | Epv6_total L | PV6Energy total (low) |  | 0.1kWh |  |
| 83. | Epv7_today H | PV7Energy today(high) |  | 0.1kWh |  |
| 84. | Epv7_today L | PV7Energy today (low) |  | 0.1kWh |  |
| 85. | Epv7_total H | PV7 Energy total(high) |  | 0.1kWh |  |
| 86. | Epv7_total L | PV7Energy total (low) |  | 0.1kWh |  |
| 87. | Epv8_today H | PV8Energy today(high) |  | 0.1kWh |  |
| 88. | Epv8_today L | PV8Energy today (low) |  | 0.1kWh |  |
| 89. | Epv8_total H | PV8Energy total(high) |  | 0.1kWh |  |
| 90. | Epv8_total L | PV8Energy total (low) |  | 0.1kWh |  |
| 91. | Epv_total H | PV Energy total(high) |  | 0.1kWh |  |
| 92. | Epv_total L | PV Energy total (low) |  | 0.1kWh |  |
| 93. | Temp1 | Inverter temperature |  | 0.1C |  |
| 94. | Temp2 | The inside IPM in inverter Temperature |  | 0.1C |  |
| 95. | Temp3 | Boost temperature |  | 0.1C |  |
| 96. | Temp4 |  |  |  | reserved |
| 97. | uwBatVolt_DSP | BatVolt_DSP |  | 0.1V | BatVolt(DSP) |
| 98. | P Bus Voltage | P Bus inside Voltage |  | 0.1V |  |
| 99. | N Bus Voltage | N Bus inside Voltage |  | 0.1V |  |
| 100. | IPF | Inverter output PF now | 0-20000 |  |  |
| 101. | RealOPPercent | Real Output power Percent |  | 1% |  |
| 102. | OPFullwatt H | Output Maxpower Limited high |  |  |  |

| 103. | OPFullwatt L | Output Maxpower Limited low |  | 0.1W |  |
| --- | --- | --- | --- | --- | --- |
| 104. | DeratingMode | DeratingMode | 0:no derate; 1:PV; 2:*; 3:Vac; 4:Fac; 5:Tboost; 6:Tinv; 7:Control; 8:*; 9:*OverBack ByTime; |  |  |
| 105. | Fault Maincode | Inverter fault maincode |  |  |  |
| 106. |  |  |  |  |  |
| 107. | Fault Subcode | Inverter fault subcode |  |  |  |
| 108. | RemoteCtrlEn | / | 0.Load First 1.BatFirst 2.Grid | / | StoragePow er (SPA) |
| 109. | RemoteCtrlPow er | / |  | / | StoragePow er (SPA) |
| 110. | Warning bit H | Warning bit H |  |  |  |
| 111. | Warn Subcode | Inverter warn subcode |  |  |  |
| 112. | Warn Maincode | Inverter warn maincode |  |  |  |
|  | EACharge_Today _H | ACCharge energy today |  | 0.1kwh | Storage Power |
| 113. | real Power Percent | real Power Percent | 0-100 | % | MAX |
|  | EACharge_Today _L | ACCharge energy today |  | 0.1kwh | Storage Power |
| 114. | inv start delay time | inv start delay time |  |  | MAX |
|  | EACharge_Total _H | ACCharge energy total |  | 0.1kwh | Storage Power |
| 115. | bINVAllFaultCod e | bINVAllFaultCode |  |  | MAX |
|  | EACharge_Total _L | ACCharge energy total |  | 0.1kwh | Storage Power |
| 116. | AC charge Power_H | Grid power to local load |  | 0.1kwh | Storage Power |
| 117. | AC charge Power_L | Grid power to local load |  | 0.1kwh | Storage Power |
| 118. | Priority | 0:Load First |  |  | Storage |

|  |  | 1:Battery First 2:Grid First |  |  |  |  |  | Power |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 119. | Battery Type | 0：Lead-acid 1：Lithium battery |  |  |  |  |  | Storage Power |
| 120. | AutoProofreadC MD | Aging mode Auto-calibration command |  |  |  |  |  | Storage Power |
| … | reserved |  |  |  |  |  |  | reserved |
| 124. | reserved |  |  |  |  |  |  | reserved |
| Second group |  |  |  |  |  |  |  |  |
| 125. | PID PV1+ Voltage |  | PID PV1PE Volt/ Flyspan voltage (MAX HV) |  |  | 0~1000V | 0.1V |  |
| 126. | PID PV1+ Current |  | PID PV1PE Curr |  |  | -10~10mA | 0.1mA |  |
| 127. | PID PV2+ Voltage |  | PID PV2PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 128. | PID PV2+ Current |  | PID PV2PE Curr |  |  | -10~10mA | 0.1mA |  |
| 129. | PID PV3+ Voltage |  | PID PV3PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 130. | PID PV3+ Current |  | PID PV3PE Curr |  |  | -10~10mA | 0.1mA |  |
| 131. | PID PV4+ Voltage |  | PID PV4PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 132. | PID PV4+ Current |  | PID PV4PE Curr |  |  | -10~10mA | 0.1mA |  |
| 133. | PID PV5+ Voltage |  | PID PV5PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 134. | PID PV5+ Current |  | PID PV5PE Curr |  |  | -10~10mA | 0.1mA |  |
| 135. | PID PV6+ Voltage |  | PID PV6PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 136. | PID PV6+ Current |  | PID PV6PE Curr |  |  | -10~10mA | 0.1mA |  |
| 137. | PID PV7+ Voltage |  | PID PV7PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 138. | PID PV7+ Current |  | PID PV7PE Curr |  |  | -10~10mA | 0.1mA |  |
| 139. | PID PV8+ Voltage |  | PID PV8PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 140. | PID PV8+ Current |  | PID PV8PE Curr |  |  | -10~10mA | 0.1mA |  |
| 141. | PID Status |  | Bit0~7:PID Working Status 1:Wait Status 2:Normal Status 3:Fault Status Bit8~15:Reversed |  |  | 0~3 |  |  |
| 142. | V _String1 |  | PV String1 voltage |  |  |  | 0.1V |  |
| 143. | Curr _String1 |  | PV String1 current |  |  | -15~15A | 0.1A |  |
| 144. | V _String2 |  | PV String2 voltage |  |  |  | 0.1V |  |

| 145. | Curr _String2 | PV String2 current | -15~15A | 0.1A |  |
| --- | --- | --- | --- | --- | --- |
| 146. | V _String3 | PV String3 voltage |  | 0.1V |  |
| 147. | Curr _String3 | PV String3 current | -15~15A | 0.1A |  |
| 148. | V _String4 | PV String4 voltage |  | 0.1V |  |
| 149. | Curr _String4 | PV String4 current | -15~15A | 0.1A |  |
| 150. | V _String5 | PV String5 voltage |  | 0.1V |  |
| 151. | Curr _String5 | PV String5 current | -15~15A | 0.1A |  |
| 152. | V _String6 | PV String6 voltage |  | 0.1V |  |
| 153. | Curr _String6 | PV String6 current | -15~15A | 0.1A |  |
| 154. | V _String7 | PV String7 voltage |  | 0.1V |  |
| 155. | Curr _String7 | PV String7 current | -15~15A | 0.1A |  |
| 156. | V _String8 | PV String8 voltage |  | 0.1V |  |
| 157. | Curr _String8 | PV String8 current | -15A~15A | 0.1A |  |
| 158. | V _String9 | PV String9 voltage |  | 0.1V |  |
| 159. | Curr _String9 | PV String9 current | -15A~15A | 0.1A |  |
| 160. | V _String10 | PV String10 voltage |  | 0.1V |  |
| 161. | Curr _String10 | PV String10 current | -15~15A | 0.1A |  |
| 162. | V _String11 | PV String11 voltage |  | 0.1V |  |
| 163. | Curr _String11 | PV String11 current | -15~15A | 0.1A |  |
| 164. | V _String12 | PV String12 voltage |  | 0.1V |  |
| 165. | Curr _String12 | PV String12 current | -15~15A | 0.1A |  |
| 166. | V _String13 | PV String13 voltage |  | 0.1V |  |
| 167. | Curr _String13 | PV String13 current | -15A~15A | 0.1A |  |
| 168. | V _String14 | PV String14 voltage |  | 0.1V |  |
| 169. | Curr _String14 | PV String14 current | -15~15A | 0.1A |  |
| 170. | V _String15 | PV String15 voltage |  | 0.1V |  |
| 171. | Curr _String15 | PV String15 current | -15~15A | 0.1A |  |
| 172. | V _String16 | PV String16 voltage |  | 0.1V |  |
| 173. | Curr _String16 | PV String16 current | -15~15A | 0.1A |  |
| 174. | StrUnmatch | Bit0~15: String1~16 unmatch |  |  | suggestive |
| 175. | StrCurrentUnblan ce | Bit0~15: String1~16 current unblance |  |  | suggestive |
| 176. | StrDisconnect | Bit0~15: String1~16 disconnect |  |  | suggestive |
| 177. | PIDFaultCode | Bit0:Output over voltage Bit1: ISO fault Bit2: BUS voltage abnormal Bit3~15:reserved |  |  |  |
| 178. | String Prompt | String Prompt Bit0:String Unmatch Bit1:StrDisconnect Bit2:StrCurrentUnblance |  |  |  |

|  |  |  | Bit3~15:reserved |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 179 | PV Warning Value |  | PV Warning Value |  |  |  |
| 180 | DSP075 Value | Warning | DSP075 Warning Value |  |  |  |
| 181 | DSP075 Value | Fault | DSP075 Fault Value |  |  |  |
| 182 | DSP067 Data1 | Debug | DSP067 Debug Data1 |  |  |  |
| 183 | DSP067 Data2 | Debug | DSP067 Debug Data2 |  |  |  |
| 184 | DSP067 Data3 | Debug | DSP067 Debug Data3 |  |  |  |
| 185 | DSP067 Data4 | Debug | DSP067 Debug Data4 |  |  |  |
| 186 | DSP067 Data5 | Debug | DSP067 Debug Data5 |  |  |  |
| 187 | DSP067 Data6 | Debug | DSP067 Debug Data6 |  |  |  |
| 188 | DSP067 Data7 | Debug | DSP067 Debug Data7 |  |  |  |
| 189 | DSP067 Data8 | Debug | DSP067 Debug Data8 |  |  |  |
| 190 | DSP075 Data1 | Debug | DSP075 Debug Data1 |  |  |  |
| 191 | DSP075 Data2 | Debug | DSP075 Debug Data2 |  |  |  |
| 192 | DSP075 Data3 | Debug | DSP075 Debug Data3 |  |  |  |
| 193 | DSP075 Data4 | Debug | DSP075 Debug Data4 |  |  |  |
| 194 | DSP075 Data55 | Debug | DSP075 Debug Data5 |  |  |  |
| 195 | DSP075 Data6 | Debug | DSP075 Debug Data6 |  |  |  |
| 196 | DSP075 Data7 | Debug | DSP075 Debug Data7 |  |  |  |
| 197 | DSP075 Data8 | Debug | DSP075 Debug Data8 |  |  |  |
| 198 | bUSBAgingTestOk Flag |  | USBAgingTestOkFlag | 0-1 |  |  |
| 199 | bFlashEraseAging OkFlag |  | FlashEraseAgingOkFlag | 0-1 |  |  |

| 200 | PVISO | PVISOValue |  |  | KΩ |  |
| --- | --- | --- | --- | --- | --- | --- |
| 201 | R_DCI | R DCI Curr |  |  | 0.1mA |  |
| 202 | S_DCI | S DCI Curr |  |  | 0.1mA |  |
| 203 | T_DCI | T DCI Curr |  |  | 0.1mA |  |
| 204 | PID_Bus | PIDBusVolt |  |  | 0.1V |  |
| 205 | GFCI | GFCI Curr |  |  | mA |  |
| 206 | SVG/APF Status+SVGAPFEq ualRatio | SVG/APF Status+SVGAPFEqualRatio |  | High 8 bit： SVGAPFEqua lRatio Low 8 bit： SVG/APF Status 0:None 1:SVG Run 2:APF Run 3:SVG/APF Run |  |  |
| 207 | CT_I _R | R phase load side current for SVG |  |  | 0.1A |  |
| 208 | CT_I _S | S phase load side current for SVG |  |  | 0.1A |  |
| 209 | CT_I _T | T phase load side current for SVG |  |  | 0.1A |  |
| 210 | CT_Q _R H | R phase load side output power for SVG(High) | reactive |  | 0.1Var |  |
| 211 | CT_Q _R L | R phase load side output power for SVG(low) | reactive |  | 0.1Var |  |
| 212 | CT_Q _S H | S phase load side output power for SVG(High) | reactive |  | 0.1Var |  |
| 213 | CT_Q _S L | S phase load side output power for SVG(low) | reactive |  | 0.1Var |  |
| 214 | CT_Q _T H | T phase load side output power for SVG(High) | reactive |  | 0.1Var |  |
| 215 | CT_Q _T L | T phase load side output power for SVG(low) | reactive |  | 0.1Var |  |
| 216 | CT HAR_I_R | R phase load side harmonic |  |  | 0.1A |  |
| 217 | CT HAR_I_S | S phase load side harmonic |  |  | 0.1A |  |
| 218 | CT HAR_I_T | T phase load side harmonic |  |  | 0.1A |  |
| 219 | COMP_Q _R H | R phase compensate reactive power for SVG(High) |  |  | 0.1Var |  |
| 220 | COMP_Q _R L | R phase compensate reactive power for SVG(low) |  |  | 0.1Var |  |
| 221 | COMP_Q _S H | S phase compensate reactive power for SVG(High) |  |  | 0.1Var |  |
| 222 | COMP_Q _S L | S phase compensate reactive power |  |  | 0.1Var |  |

|  |  |  | for SVG(low) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 223 | COMP_Q _T H |  | T phase compensate reactive power for SVG(High) |  | 0.1Var |  |
| 224 | COMP_Q _T L |  | T phase compensate reactive power for SVG(low) |  | 0.1Var |  |
| 225 | COMP HAR_I_R |  | R phase compensate harmonic for SVG |  | 0.1A |  |
| 226 | COMP HAR_I_S |  | S phase compensate harmonic for SVG |  | 0.1A |  |
| 227 | COMP HAR_I_T |  | T phase compensate harmonic for SVG |  | 0.1A |  |
| 228 | bRS232AgingTest OkFlag |  | RS232AgingTestOkFlag | 0-1 |  |  |
| 229 | bFanFaultBit |  | Bit0: Fan 1 fault bit Bit1: Fan 2 fault bit Bit2: Fan 3 fault bit Bit3: Fan 4 fault bit Bit4-7: Reserved |  |  |  |
| 230 | Sac H |  | Output apparent power H |  | 0.1W |  |
| 231 | Sac L |  | Output apparent power L |  | 0.1W |  |
| 232 | ReActPowerH |  | Real Output Reactive Power H | Int32 | 0.1W |  |
| 233 | ReActPowerL |  | Real Output Reactive Power L |  |  |  |
| 234 | ReActPowerMaxH |  | Nominal Output Reactive Power H |  | 0.1var |  |
| 235 | ReActPowerMaxL |  | Nominal Output Reactive Power L |  |  |  |
| 236 | ReActPower_Total H |  | Reactive power generation |  | 0.1kwh |  |
| 237 | ReActPower_Total L |  | Reactive power generation |  |  |  |
| 238 | bAfciStatus |  | 0：Waiting 1：Self-check state 2：Detect pull arc state 3：Fault 4：Update |  |  |  |
| 239 | uwPresentFFTValu e [CHANNEL_A] |  | PresentFFTValue [CHANNEL_A] |  |  |  |
| 240 | uwPresentFFTValu e [CHANNEL_B] |  | PresentFFTValue [CHANNEL_B] |  |  |  |
| 241 | DSP067 Data1 | Debug | DSP067 Debug Data1 |  |  |  |
| 242 | DSP067 Data2 | Debug | DSP067 Debug Data2 |  |  |  |
| 243 | DSP067 | Debug | DSP067 Debug Data3 |  |  |  |

|  | Data3 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 244 | DSP067 Data4 | Debug | DSP067 Debug Data4 |  |  |  |
| 245 | DSP067 Data5 | Debug | DSP067 Debug Data5 |  |  |  |
| 246 | DSP067 Data6 | Debug | DSP067 Debug Data6 |  |  |  |
| 247 | DSP067 Data7 | Debug | DSP067 Debug Data7 |  |  |  |
| 248 | DSP067 Data8 | Debug | DSP067 Debug Data8 |  |  |  |
| 249 |  |  |  |  |  | reserved |
| The eighth group for |  | PV9-PV16 information |  |  |  |  |
| 875 | Vpv9 |  | PV9 voltage |  | 0.1V |  |
| 876 | PV9Curr |  | PV9 Input current |  | 0.1A |  |
| 877 | Ppv9 H |  | PV9 input power (High) |  | 0.1W |  |
| 878 | Ppv9 L |  | PV9 input power (Low) |  | 0.1W |  |
| 879 | Vpv10 |  | PV10 voltage |  | 0.1V |  |
| 880 | PV10Curr |  | PV10 Input current |  | 0.1A |  |
| 881 | Ppv10 H |  | PV10 input power (High) |  | 0.1W |  |
| 882 | Ppv10 L |  | PV10 input power (Low) |  | 0.1W |  |
| 883 | Vpv11 |  | PV11 voltage |  | 0.1V |  |
| 884 | PV11Curr |  | PV11 Input current |  | 0.1A |  |
| 885 | Ppv11 H |  | PV11 input power (High) |  | 0.1W |  |
| 886 | Ppv11 L |  | PV11 input power (Low) |  | 0.1W |  |
| 887 | Vpv12 |  | PV12 voltage |  | 0.1V |  |
| 888 | PV12Curr |  | PV12 Input current |  | 0.1A |  |
| 889 | Ppv12 H |  | PV12 input power (High) |  | 0.1W |  |
| 890 | Ppv12 L |  | PV12 input power (Low) |  | 0.1W |  |
| 891 | Vpv13 |  | PV13 voltage |  | 0.1V |  |
| 892 | PV13Curr |  | PV13 Input current |  | 0.1A |  |
| 893 | Ppv13H |  | PV13 input power (High) |  | 0.1W |  |
| 894 | Ppv13 L |  | PV13 input power (Low) |  | 0.1W |  |
| 895 | Vpv14 |  | PV14 voltage |  | 0.1V |  |
| 896 | PV14Curr |  | PV14 Input current |  | 0.1A |  |
| 897 | Ppv14 H |  | PV14 input power (High) |  | 0.1W |  |
| 898 | Ppv14 L |  | PV14 input power (Low) |  | 0.1W |  |
| 899 | Vpv15 |  | PV15 voltage |  | 0.1V |  |
| 900 | PV15Curr |  | PV15 Input current |  | 0.1A |  |
| 901 | Ppv15 H |  | PV15 input power (High) |  | 0.1W |  |
| 902 | Ppv15 L |  | PV15 input power (Low) |  | 0.1W |  |

| 903 | Vpv16 | PV16 voltage |  |  | 0.1V |  |
| --- | --- | --- | --- | --- | --- | --- |
| 904 | PV16Curr | PV16 Input current |  |  | 0.1A |  |
| 905 | Ppv16 H | PV16 input power (High) |  |  | 0.1W |  |
| 906 | Ppv16 L | PV16 input power (Low) |  |  | 0.1W |  |
| 907 | Epv9_today H | PV9 energy today (High) |  |  | 0.1kWh |  |
| 908 | Epv9_today L | PV9 energy today (Low) |  |  | 0.1kWh |  |
| 909 | Epv9_total H | PV9 energy total (High) |  |  | 0.1kWh |  |
| 910 | Epv9_total L | PV9 energy total (Low) |  |  | 0.1kWh |  |
| 911 | Epv10_today H | PV10 energy today (High) |  |  | 0.1kWh |  |
| 912 | Epv10_today L | PV10 energy today (Low) |  |  | 0.1kWh |  |
| 913 | Epv10_total H | PV10 energy total (High) |  |  | 0.1kWh |  |
| 914 | Epv10_total L | PV10 energy total (Low) |  |  | 0.1kWh |  |
| 915 | Epv11_today H | PV11 energy today (High) |  |  | 0.1kWh |  |
| 916 | Epv11_today L | PV11 energy today (Low) |  |  | 0.1kWh |  |
| 917 | Epv11_total H | PV11 energy total (High) |  |  | 0.1kWh |  |
| 918 | Epv11_total L | PV11 energy total (Low) |  |  | 0.1kWh |  |
| 919 | Epv12_today H | PV12 energy today (High) |  |  | 0.1kWh |  |
| 920 | Epv12_today L | PV12 energy today (Low) |  |  | 0.1kWh |  |
| 921 | Epv12_total H | PV12 energy total (High) |  |  | 0.1kWh |  |
| 922 | Epv12_total L | PV12 energy total (Low) |  |  | 0.1kWh |  |
| 923 | Epv13_today H | PV13 energy today (High) |  |  | 0.1kWh |  |
| 924 | Epv13_today L | PV13 energy today (Low) |  |  | 0.1kWh |  |
| 925 | Epv13_total H | PV13 energy total (High) |  |  | 0.1kWh |  |
| 926 | Epv13_total L | PV13 energy total (Low) |  |  | 0.1kWh |  |
| 927 | Epv14_today H | PV14 energy today (High) |  |  | 0.1kWh |  |
| 928 | Epv14_today L | PV14 energy today (Low) |  |  | 0.1kWh |  |
| 929 | Epv14_total H | PV14 energy total (High) |  |  | 0.1kWh |  |
| 930 | Epv14_total L | PV14 energy total (Low) |  |  | 0.1kWh |  |
| 931 | Epv15_today H | PV15 energy today (High) |  |  | 0.1kWh |  |
| 932 | Epv15_today L | PV15 energy today (Low) |  |  | 0.1kWh |  |
| 933 | Epv15_total H | PV15 energy total (High) |  |  | 0.1kWh |  |
| 934 | Epv15_total L | PV15 energy total (Low) |  |  | 0.1kWh |  |
| 935 | Epv16_today H | PV16 energy today (High) |  |  | 0.1kWh |  |
| 936 | Epv16_today L | PV16 energy today (Low) |  |  | 0.1kWh |  |
| 937 | Epv16_total H | PV16 energy total (High) |  |  | 0.1kWh |  |
| 938 | Epv16_total L | PV16 energy total (Low) |  |  | 0.1kWh |  |
| 939 | PID PV9+ Voltage | PID PV9PE Volt/ Flyspan (MAX HV) | voltage | 0~1000V | 0.1V |  |
| 940 | PID PV9+ Current | PID PV9PE Current |  | -10~10mA | 0.1mA |  |
| 941 | PID PV10+ Voltage | PID PV10PE/ Flyspan voltage (MAX HV) |  | 0~1000V | 0.1V |  |

| 942 | PID Current | PV10+ | PID PV10PE Current |  |  | -10~10mA | 0.1mA |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 943 | PID Voltage | PV11+ | PID PV11PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 944 | PID Current | PV11+ | PID PV11PE Current |  |  | -10~10mA | 0.1mA |  |
| 945 | PID Voltage | PV12+ | PID PV12PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 946 | PID Current | PV12+ | PID PV12PE Current |  |  | -10~10mA | 0.1mA |  |
| 947 | PID Voltage | PV13+ | PID PV13PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 948 | PID Current | PV13+ | PID PV13PE Current |  |  | -10~10mA | 0.1mA |  |
| 949 | PID Voltage | PV14+ | PID PV14PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 950 | PID Current | PV14+ | PID PV14PE Current |  |  | -10~10mA | 0.1mA |  |
| 951 | PID Voltage | PV15+ | PID PV15PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 952 | PID Current | PV15+ | PID PV15PE Current |  |  | -10~10mA | 0.1mA |  |
| 953 | PID Voltage | PV16+ | PID PV16PE Volt/ (MAX HV) | Flyspan | voltage | 0~1000V | 0.1V |  |
| 954 | PID Current | PV16+ | PID PV16PE Current |  |  | -10~10mA | 0.1mA |  |
| 955 | V _String17 |  | PV String 17 voltage |  |  |  | 0.1V |  |
| 956 | Curr _String17 |  | PV String 17 Current |  |  | -15~15A | 0.1A |  |
| 957 | V _String18 |  | PV String 18 voltage |  |  |  | 0.1V |  |
| 958 | Curr _String18 |  | PV String 18 Current |  |  | -15~15A | 0.1A |  |
| 959 | V _String19 |  | PV String 19 voltage |  |  |  | 0.1V |  |
| 960 | Curr _String19 |  | PV String 19 Current |  |  | -15~15A | 0.1A |  |
| 961 | V _String20 |  | PV String 20 voltage |  |  |  | 0.1V |  |
| 962 | Curr _String20 |  | PV String 20 Current |  |  | -15~15A | 0.1A |  |
| 963 | V _String21 |  | PV String 21 voltage |  |  |  | 0.1V |  |
| 964 | Curr _String21 |  | PV String 21 Current |  |  | -15~15A | 0.1A |  |
| 965 | V _String22 |  | PV String22 voltage |  |  |  | 0.1V |  |
| 966 | Curr _String22 |  | PV String 22 Current |  |  | -15~15A | 0.1A |  |
| 967 | V _String23 |  | PV String 23 voltage |  |  |  | 0.1V |  |
| 968 | Curr _String23 |  | PV String 23 Current |  |  | -15~15A | 0.1A |  |
| 969 | V _String24 |  | PV String 24 voltage |  |  |  | 0.1V |  |

| 970 | Curr _String24 | PV String 24 Current |  |  | -15A~15A |  | 0.1A |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 971 | V _String25 | PV String 25 voltage |  |  |  |  | 0.1V |  |  |
| 972 | Curr _String25 | PV String 25 Current |  |  | -15A~15A |  | 0.1A |  |  |
| 973 | V _String26 | PV String 26 voltage |  |  |  |  | 0.1V |  |  |
| 974 | Curr _String26 | PV String 26 Current |  |  | -15~15A |  | 0.1A |  |  |
| 975 | V _String27 | PV String 27 voltage |  |  |  |  | 0.1V |  |  |
| 976 | Curr _String27 | PV String 27 Current |  |  | -15~15A |  | 0.1A |  |  |
| 977 | V _String28 | PV String 28 voltage |  |  |  |  | 0.1V |  |  |
| 978 | Curr _String28 | PV String 28 Current |  |  | -15~15A |  | 0.1A |  |  |
| 979 | V _String29 | PV String 29 voltage |  |  |  |  | 0.1V |  |  |
| 980 | Curr _String29 | PV String 29 Current |  |  | -15A~15A |  | 0.1A |  |  |
| 981 | V _String30 | PV String 30 voltage |  |  |  |  | 0.1V |  |  |
| 982 | Curr _String30 | PV String 30 Current |  |  | -15~15A |  | 0.1A |  |  |
| 983 | V _String31 | PV String 31 voltage |  |  |  |  | 0.1V |  |  |
| 984 | Curr _String31 | PV String 31 Current |  |  | -15~15A |  | 0.1A |  |  |
| 985 | V _String32 | PV String 32 voltage |  |  |  |  | 0.1V |  |  |
| 986 | Curr _String32 | PV String 32 Current |  |  | -15~15A |  | 0.1A |  |  |
| 987 | StrUnmatch2 | Bit0~15: String 17~32 unmatch |  |  |  |  |  |  |  |
| 988 | StrCurrentUnblan ce2 | Bit0~15:String 17~32 current unblance |  |  |  |  |  |  |  |
| 989 | StrDisconnect2 | Bit0~15: String 17~32 disconnect |  |  |  |  |  |  |  |
| 990 | PV Warning Value | PV Warning Value (PV9-PV16) Contains PV9~16 abnormal ， 和 Boost9~16 Drive anomalies |  |  |  |  |  |  |  |
| 991 | StrWaringvalue1 | string1~string16 abnormal |  |  |  |  |  |  |  |
| 992 | StrWaringvalue2 | string17~string32 abnormal |  |  |  |  |  |  |  |
| …… |  |  |  |  |  |  |  |  |  |
| 999 | SystemCmd | M3 to DSP system command |  |  |  |  |  |  | system command |
| Ninth group for Storage power |  |  |  |  |  |  |  |  |  |
| 1000. | uwSysWorkMode |  | System work mode | 0x00:waiting module 0x01: Self-test mode, optional 0x02 : Reserved 0x03：SysFault module 0x04: Flash module |  |  |  | Theworkingmode displayed by the monitoring to the customer is： 0x00: waiting module 0x01: Self-test mode, 0x03:fault module 0x04:flash |  |

|  |  |  |  | 0x05 ： PVBATOnline module, 0x06 ： BatOnline module, 0x07 ： PVOfflineMod e module, 0x08 ： BatOfflineMo de module, |  | module 0x05¦0x06¦0x07¦ x08:normal module | 0 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1001. | Systemfault word0 |  | System fault word0 |  |  | Please refer | to |
|  |  |  |  |  |  | thefault description Hybrid | of |
| 1002. | Systemfault word1 |  | System fault word1 |  |  |  |  |
| 1003. | Systemfault word2 |  | System fault word2 |  |  |  |  |
| 1004. | Systemfault word3 |  | System fault word3 |  |  |  |  |
| 1005. | Systemfault word4 |  | System fault word4 |  |  |  |  |
| 1006. | Systemfault word5 |  | System fault word5 |  |  |  |  |
| 1007. | Systemfault word6 |  | System fault word6 |  |  |  |  |
| 1008. | Systemfault word7 |  | System fault word7 |  |  |  |  |
| 1009. | Pdischarge1 H |  | Discharge power(high) |  | 0.1W |  |  |
| 1010. | Pdischarge1 L |  | Discharge power (low) |  | 0.1W |  |  |
| 1011. | Pcharge1 H |  | Charge power(high) |  | 0.1W |  |  |
| 1012. | Pcharge1 L |  | Charge power (low) |  | 0.1W |  |  |
| 1013. | Vbat |  | Battery voltage |  | 0.1V |  |  |
| 1014. | SOC |  | State of charge Capacity | 0-100 | 1% | lith/leadacid |  |
| 1015. | Pactouser R | H | AC power to user H |  | 0.1w |  |  |
| 1016. | Pactouser R | L | AC power to user L |  | 0.1w |  |  |
| 1017. | Pactouser S | H | Pactouser S H |  | 0.1w |  |  |
| 1018. | Pactouser S | L | Pactouser S L |  | 0.1w |  |  |
| 1019. | Pactouser T | H | Pactouser T H |  | 0.1w |  |  |
| 1020. | Pactouser T | L | Pactouser T H |  | 0.1w |  |  |
| 1021. | PactouserTotal H |  | AC power to user total H |  | 0.1w |  |  |
| 1022. | PactouserTotal L |  | AC power to user total L |  | 0.1w |  |  |
| 1023. | Pac to grid R H |  | AC power to grid H |  | 0.1w | Ac output |  |
| 1024. | Pac to grid R L |  | AC power to grid L |  | 0.1w |  |  |
| 1025. | Pactogrid S H |  |  |  | 0.1w |  |  |
| 1026. | Pactogrid S L |  |  |  | 0.1w |  |  |

| 1027. |  | Pactogrid T H |  |  |  |  | 0.1w |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1028. |  | Pactogrid T L |  |  |  |  | 0.1w |  |
| 1029. |  | Pactogrid total H |  | AC power to grid total H |  |  | 0.1w |  |
| 1030. |  | Pactogrid total L |  | AC power to grid total L |  |  | 0.1w |  |
| 1031. |  | PLocalLoad R H |  | INV power to local load H |  |  | 0.1w |  |
| 1032. |  | PLocalLoad R L |  | INV power to local load L |  |  | 0.1w |  |
| 1033. |  | PLocalLoad S H |  |  |  |  | 0.1w |  |
| 1034. |  | PLocalLoad S L |  |  |  |  | 0.1w |  |
| 1035. |  | PLocalLoadT H |  |  |  |  | 0.1w |  |
| 1036. |  | PLocalLoadT L |  |  |  |  | 0.1w |  |
| 1037. |  | PLocalLoad total H |  | INV power to local load total H |  |  | 0.1w |  |
| 1038. |  | PLocalLoad total L |  | INV power to local load total L |  |  | 0.1w |  |
| 1039. |  | IPM Temperature |  | REC Temperature |  |  | 0.1℃ | No use |
| 1040. |  | Battery Temperature |  | Battery Temperature |  |  | 0.1℃ | Lead acid/lithium battery temp |
| 1041. |  | SP DSP Status |  | SP state |  |  |  | CHG/DisCHG |
| 1042. |  | SP Bus Volt |  | SP BUS2 Volt |  |  | 0.1V |  |
| 1043 |  |  |  |  |  |  |  |  |
| Power generation data |  |  |  |  |  |  |  |  |
| 1044. | Etouser_today H |  | Energy to user today high |  |  | 0.1kWh |  |  |
| 1045. | Etouser_today L |  | Energy to user today low |  |  | 0.1kWh |  |  |
| 1046. | Etouser_total H |  | Energy to user total high |  |  | 0.1kWh |  |  |
| 1047. | Etouser_ total L |  | Energy to user total high |  |  | 0.1kWh |  |  |
| 1048. | Etogrid_today H |  | Energy to grid today high |  |  | 0.1kWh |  |  |
| 1049. | Etogrid _today L |  | Energy to grid today low |  |  | 0.1kWh |  |  |
| 1050. | Etogrid _total H |  | Energy to grid total high |  |  | 0.1kWh |  |  |
| 1051. | Etogrid _ total L |  | Energy to grid total high |  |  | 0.1kWh |  |  |
| 1052. | Edischarge1_toda y H |  | Discharge energy1 today |  |  | 0.1kWh |  |  |
| 1053. | Edischarge1_toda y L |  | Discharge energy1 today |  |  | 0.1kWh |  |  |
| 1054. | Edischarge1_total H |  | Total discharge energy1 (high) |  |  | 0.1kWh |  |  |
| 1055. | Edischarge1_total L |  | Total discharge energy1 (low) |  |  | 0.1kWh |  |  |
| 1056. | Echarge1_today H |  | Charge1 energy today |  |  | 0.1kWh |  |  |
| 1057. | Echarge1_today L |  | Charge1 energy today |  |  | 0.1kWh |  |  |
| 1058. | Echarge1_total H |  | Charge1 energy total |  |  | 0.1kWh |  |  |
| 1059. | Echarge1_total L |  | Charge1 energy total |  |  | 0.1kWh |  |  |

| 1060. |  | ELocalLoad_Today H |  |  |  | Local load energy today |  | 0.1kWh |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1061. |  | ELocalLoad_Today L |  |  |  | Local load energy today |  | 0.1kWh |  |
| 1062. |  | ELocalLoad_Total H |  |  |  | Local load energy total |  | 0.1kWh |  |
| 1063. |  | ELocalLoad_Total L |  |  |  | Local load energy total |  | 0.1kWh |  |
| 1064. |  | dwExportLimitAp parentPower |  |  |  | ExportLimitApparentPower H |  | 0.1kWh | ApparentPower |
| 1065. |  | dwExportLimitAp parentPower |  |  |  | ExportLimitApparentPower L |  | 0.1kWh | ApparentPower |
| 1066. |  | / |  |  |  | / | / | / | reserved |
|  | Ups information (offline) |  |  |  |  |  |  |  |  |
| 1067. |  | EPS Fac |  |  |  | UPSfrequency | 5000/6000 | 0.01Hz |  |
| 1068. |  | EPS Vac1 |  |  |  | UPS phase R output voltage | 2300 | 0.1V |  |
| 1069. |  | EPS Iac1 |  |  |  | UPS phase R output current |  | 0.1A |  |
| 1070. |  | EPS Pac1 H |  |  |  | UPS phase R output power (H) |  | 0.1VA |  |
| 1071. |  | EPS Pac1 L |  |  |  | UPS phase R output power (L) |  | 0.1VA |  |
| 1072. |  | EPS Vac2 |  |  |  | UPS phase S output voltage |  | 0.1V |  |
| 1073. |  | EPS Iac2 |  |  |  | UPS phase S output current |  | 0.1A | No use |
| 1074. |  | EPS Pac2 H |  |  |  | UPS phase S output power (H) |  | 0.1VA |  |
| 1075. |  | EPS Pac2 L |  |  |  | UPS phase S output power (L) |  | 0.1VA |  |
| 1076. |  | EPS Vac3 |  |  |  | UPS phase T output voltage |  | 0.1V |  |
| 1077. |  | EPS Iac3 |  |  |  | UPS phase T output current |  | 0.1A | No use |
| 1078. |  | EPS Pac3 H |  |  |  | UPS phase T output power (H) |  | 0.1VA |  |
| 1079. |  | EPS Pac3 L |  |  |  | UPS phase T output power (L) |  | 0.1VA |  |
| 1080. |  | Loadpercent |  |  |  | Load percent of UPS ouput | 0-100 | 1% |  |
| 1081. |  | PF |  |  |  | Power factor | 0-2 | 0.1 | Primary Value+1 |
|  | BMS Infomation |  |  |  |  |  |  |  |  |
| 1082. |  |  | BMS_StatusOld |  |  | StatusOld from BMS | Detail information, refer to document:GrowattxxSxx P ESS Protocol; |  |  |
| 1083. |  |  | BMS_Status |  |  | Status from BMS |  |  | W/R |
| 1084. |  |  | BMS_ErrorOld |  |  | Error info Old from BMS |  |  |  |
| 1085. |  |  | BMS_Error |  |  | Errorinfomation from BMS |  |  |  |
| 1086. |  |  | BMS_SOC |  |  | SOC from BMS |  |  | R SPH6K |
| 1087. |  |  | BMS_BatteryVol t |  |  | Battery voltage from BMS |  |  | R SPH6K |
| 1088. |  |  | BMS_BatteryCu r |  | r | Battery current from BMS |  |  |  |
| 1089. |  |  | BMS_BatteryTe mp |  |  | Battery temperature from BMS |  |  |  |

| 1090. | BMS_MaxCurr | Max. charge/discharge current from BMS (pylon) |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1091. | BMS_GaugeRM | Gauge RM from BMS |  |  |  |
| 1092. | BMS_GaugeFCC | Gauge FCC from BMS |  |  |  |
| 1093. | BMS_FW |  |  |  |  |
| 1094. | BMS_DeltaVolt | Delta V from BMS |  |  |  |
| 1095. | BMS_CycleCnt | Cycle Count from BMS |  |  |  |
| 1096. | BMS_SOH | SOH from BMS |  |  |  |
| 1097. | BMS_ConstantV olt | CV voltage from BMS |  |  |  |
| 1098. | BMS_WarnInfoO ld | Warning info old from BMS |  |  |  |
| 1099. | BMS_WarnInfo | Warning info from BMS |  |  |  |
| 1100. | BMS_GaugeICCu rr | Gauge IC current from BMS |  |  |  |
| 1101. | BMS_MCUVersi on | MCU Software version from BMS |  |  |  |
| 1102. | BMS_GaugeVers ion | Gauge Version from BMS |  |  |  |
| 1103. | BMS_wGaugeFR Version_ L | Gauge FR Version L16 from BMS |  |  |  |
| 1104. | BMS_wGaugeFR Version_H | Gauge FR Version H16 from BMS |  |  |  |
| 1105. | BMS_BMSInfo | BMSInformation from BMS |  |  |  |
| 1106. | BMS_PackInfo | Pack Information from BMS |  |  |  |
| 1107. | BMS_UsingCap | Using Cap from BMS |  |  |  |
| 1108. | uwMaxCellVolt | Maximum single battery voltage |  | 0.001V |  |
| 1109. | uwMinCellVolt | Lowest single battery voltage |  | 0.001V |  |
| 1110. | bModuleNum | Battery parallel number |  | 1 |  |
| 1111. |  | Number of batteries |  | 1 |  |
| 1112. | uwMaxVoltCellN o | MaxVoltCellNo |  | 1 |  |
| 1113. | uwMinVoltCellN o | MinVoltCellNo |  | 1 |  |
| 1114. | uwMaxTemprCe ll_10T | MaxTemprCell_10T |  | 0.1℃ |  |
| 1115. | uwMinTemprCel l_10T | MinTemprCell_10T |  | 0.1℃ |  |
| 1116. | uwMaxTemprCe llNo | MaxVoltTemprCellNo |  | 1 |  |
| 1117. | uwMinTemprCel | MinVoltTemprCellNo |  | 1 |  |

|  | lNo |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1118. | Protect pack ID | Faulty Battery Address |  | 1 |  |  |
| 1119. | MaxSOC | Parallel maximum SOC |  | 1% |  |  |
| 1120. | MinSOC | Parallel minimum SOC |  | 1% |  |  |
| 1121. | BMS_Error2 | Battery Protection 2 |  | - |  | CAN ID ： 0x323 Byte4~5 |
| 1122. | BMS_Error3 | Battery Protection3 |  | - |  | CAN ID ： 0x323 Byte6 |
| 1123. | BMS_WarnInfo2 | Battery Warn2 |  | - |  | CAN ID ： 0x323 Byte7 |
| 1124 | AC Charge Energy Today H | AC Charge Energy today | kwh |  |  | Energy today |
| Ninth group reserved for storage power |  |  |  |  |  |  |
| 1125. | ACCharge Energy TodayL | AC Charge Energy today | kwh |  |  |  |
| 1126. | AC Charge Energy Total H |  |  |  |  | Energy total |
| 1127. | ACCharge Energy Total L |  |  |  |  |  |
| 1128. | AC Charge Power H | AC Charge Power | W |  |  |  |
| 1129. | AC Charge Power L | AC Charge Power | w |  |  |  |
| 1130. | 70% INV Power adjust | uwGridPower_70_AdjEE_SP | W |  |  |  |
| 1131. | Extra AC Power to grid_H | Extra inverte AC Power to grid High | For SPA connect inverter |  |  | SPA used |
| 1132. | Extra AC Power to grid_L | Extrainverte AC Power to grid Low |  |  |  | SPA used |
| 1133. | Eextra_today H | Extra inverter PowerTOUser_Extra today (high) | R |  | 0.1kWh | SPA used |
| 1134. | Eextra_today L | Extra inverter PowerTOUser_Extra today (low) | R |  | 0.1kWh | SPA used |
| 1135. | Eextra_total H | Extra inverter PowerTOUser_Extra total(high) |  |  | 0.1kWh | SPA used |
| 1136. | Eextra_total L | Extra inverter PowerTOUser_Extra total(low) |  |  | 0.1kWh | SPA used |
| 1137. | Esystem_today H | System electric energy today H |  |  | 0.1kWh | SPA used System electric energy today H |

| 1138. | Esystem_ today L |  |  | System electric energy today L |  |  |  | 0.1kWh |  |  | SPA used System electric energy today L |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1139. | Esystem_total H |  |  | System electric energy total H |  |  |  | 0.1kWh |  |  | SPA used System electric energy total H |
| 1140. | Esystem_ total L |  |  | System electric energy total L |  |  |  | 0.1kWh |  |  | SPA used System electric energy total L |
| 1141. | Eself_today H |  |  | self electric energy today H |  |  |  | 0.1kWh |  |  | self electric energy today H |
| 1142. | Eself_ today L |  |  | self electric energy today L |  |  |  | 0.1kWh |  |  | self electric energy today L |
| 1143. | Eself_total H |  |  | self electric energy total H |  |  |  | 0.1kWh |  |  | self electric energy total H |
| 1144. | Eself_ total L |  |  | self electric energy total L |  |  |  | 0.1kWh |  |  | self electric energy total L |
| 1145. | PSystem H |  |  | System power H |  |  |  | 0.1w |  |  | System power H |
| 1146. | PSystem L |  |  | System power L |  |  |  | 0.1w |  |  | System power L |
| 1147. | PSelf H |  |  | self power H |  |  |  | 0.1w |  |  | self power H |
| 1148. | PSelf L |  |  | self power L |  |  |  | 0.1w |  |  | self power L |
| 1149. | EPVAll_Today H |  |  | PV electric energy today H |  |  |  |  |  |  |  |
| 1150. | EPVAll_Today L |  |  | PV electric | energy today L |  |  |  |  |  |  |
| 1151. | AcDischarge PackSn |  |  | Discharge number | power pack | serial | R | / |  |  |  |
| 1152. |  | Accdischarge power_H |  | Cumulative 16-bit byte | discharge power high |  | R |  | 0.1 | kWH |  |
| 1153. |  | Accdischarge power_L |  | Cumulative 16-bit byte | discharge power low |  | R |  | 0.1 | kWH |  |
| 1154. | AccCharge PackSn |  |  | charge power pack serial number |  |  | R | / |  |  |  |

| 1155. |  | AccCharge power_H |  | Cumulative charge power 16-bit byte |  | high |  | R |  | 0.1 | kWH |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1156. |  | AccCharge power_L |  | Cumulative charge power 16-bit byte |  | low |  | R |  | 0.1 | kWH |  |
| 1157. |  | FirstBattFaultSn |  |  | FirstBattFaultSn |  |  | R | / |  |  |  |
| 1158. |  | Second BattFaultSn |  |  | Second BattFaultSn |  |  | R | / |  |  |  |
| 1159. |  | Third BattFaultSn |  |  | Third BattFaultSn |  |  | R | / |  |  |  |
| 1160. |  | Fourth BattFaultSn |  |  | Fourth BattFaultSn |  |  | R | / |  |  |  |
| 1161. |  | Battery history fault code 1 |  |  | Battery history fault code 1 |  |  | R | / |  |  |  |
| 1162. |  | Battery history fault code 2 |  |  | Battery history fault code 2 |  |  | R | / |  |  |  |
| 1163. |  | Battery history fault code 3 |  |  | Battery history fault code 3 |  |  | R | / |  |  |  |
| 1164. |  | Battery history fault code 4 |  |  | Battery history fault code 4 |  |  | R | / |  |  |  |

| 1165. |  | Battery history fault code 5 |  |  | Battery history fault code 5 |  | R | / |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1166. |  | Battery history fault code 6 |  |  | Battery history fault code 6 |  | R | / |  |
| 1167. |  | Battery history fault code 7 |  |  | Battery history fault code 7 |  | R | / |  |
| 1168. |  | Battery history fault code 8 |  |  | Battery history fault code 8 |  | R | / |  |
| 1169. |  | Number of battery codes |  | Number of battery codes PACK number + BIC forward and reverse codes |  |  | R | / |  |
| 1170. |  |  |  |  |  |  |  |  |  |
| …… | / |  |  | / |  |  | / | / | reversed |
| 1199 | NewEPowerCalc Flag |  |  | Intelligent reading is used to identify software compatibility features |  |  |  |  | - ： Old energy calculation； - ： new energy calculation |
| 1200 | MaxCellVolt |  |  | Maximum cell voltage |  |  | R | 0.001V |  |
| 1201 | MinCellVolt |  |  | Minimum cell voltage |  |  | R | 0.001V |  |
| 1202 | ModuleNum |  |  | Number of Battery modules |  |  | R | / |  |
| 1203 | TotalCellNum |  |  | Total number of cells |  |  | R | / |  |
| 1204 | MaxVoltCellNo |  |  | MaxVoltCellNo |  |  | R | / |  |
| 1205 | MinVoltCellNo |  |  | MinVoltCellNo |  |  | R | / |  |
| 1206 | MaxTemprCell_ 10T |  |  | MaxTemprCell_10T |  |  | R | 0.1℃ |  |
| 1207 | MinTemprCell_1 0T |  |  | MinTemprCell_10T |  |  | R | 0.1℃ |  |

| 1208 |  | MaxTemprCellN o | MaxTemprCellNo |  | R |  | / |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1209 |  | MinTemprCellN o | MinTemprCellNo |  | R |  | / |  |  |  |
| 1210 |  | ProtectPackID | Fault Pack ID |  | R |  | / |  |  |  |
| 1211 |  | MaxSOC | Parallel maximum SOC |  | R |  | 1% |  |  |  |
| 1212 |  | MinSOC | Parallel minimum SOC |  | R |  | 1% |  |  |  |
| 1213 |  | BatProtect1Add | BatProtect1Add |  | R |  | / |  |  |  |
| 1214 |  | BatProtect2Add | BatProtect2Add |  | R |  | / |  |  |  |
| 1215 |  | BatWarn1Add | BatWarn1Add |  | R |  | / |  |  |  |
| 1216 |  | BMS_HighestSof tVersion | BMS_HighestSoftVersion |  | R |  | / |  |  |  |
| 1217 |  | BMS_Hardware Version | BMS_HardwareVersion |  | R |  | / |  |  |  |
| 1218 |  | BMS_RequestTy pe | BMS_RequestType |  | R |  | / |  |  |  |
| …… |  | / | / |  | / |  | / |  | reversed |  |
| 1248 |  | bKeyAgingTestO kFlag | Success sign of key detection before aging |  |  |  |  |  | 1：Finished test 0 ： test not completed |  |
| 1249. |  | / | / |  | / |  | / |  | reversed |  |
|  | thirteen group for Storage power’s SPA |  |  |  |  |  |  |  |  |  |
| 2000 |  | Inverter Status | Inverter run state |  |  | 0:waiting, 1:normal, 3:fault |  |  |  | SPA |
| …… |  | reversed |  |  |  |  |  |  |  |  |
| 2035 |  | Pac H | Output power (high) |  |  |  |  | 0.1W |  | SPA |
| 2036 |  | Pac L | Output power (low) |  |  |  |  | 0.1W |  | SPA |
| 2037 |  | Fac | Grid frequency |  |  |  |  | 0.01Hz |  | SPA |
| 2038 |  | Vac1 | Three/single phase grid voltage |  |  |  |  | 0.1V |  | SPA |
| 2039 |  | Iac1 | Three/single phase grid output current |  |  |  |  | 0.1A |  | SPA |
| 2040 |  | Pac1 H | Three/single phase grid output watt VA (high) |  |  |  |  | 0.1VA |  | SPA |
| 2041 |  | Pac1 L | Three/single phase grid output watt VA(low) |  |  |  |  | 0.1VA |  | SPA |
| …… |  | reversed |  |  |  |  |  |  |  |  |
| 2053 |  | Eac today H | Today generate energy (high) |  |  |  |  | 0.1kWH |  | SPA |
| 2054 |  | Eac today L | Today generate energy (low) |  |  |  |  | 0.1kWH |  | SPA |

| 2055 | Eac total H | Total generate energy (high) |  | 0.1kWH | SPA |
| --- | --- | --- | --- | --- | --- |
| 2056 | Eac total L | Total generate energy (low) |  | 0.1kWH | SPA |
| 2057 | Time total H | Work time total (high) |  | 0.5s | SPA |
| 2058 | Time total L | Work time total (low) |  | 0.5s | SPA |
| …… | reversed |  |  |  |  |
| 2093 | Temp1 | Inverter temperature |  | 0.1C | SPA |
| 2094 | Temp2 | The inside IPM in inverter Temperature |  | 0.1C | SPA |
| 2095 | Temp3 | Boost temperature |  | 0.1C | SPA |
| 2096 | Temp4 |  |  |  | reserved |
| 2097 | uwBatVolt_DSP | BatVolt_DSP |  | 0.1V | BatVolt(DSP) |
| 2098 | P Bus Voltage | P Bus inside Voltage |  | 0.1V | SPA |
| 2099 | N Bus Voltage | N Bus inside Voltage |  | 0.1V | SPA |
| 2100 | RemoteCtrlEn | / | 0.Load First 1.BatFirst 2.Grid | / | Remote setup enable |
| 2101 | RemoteCtrlPow er | / |  | / | Remotely set power |
| 2102 | Extra AC Power to grid_H | Extra inverte AC Power to grid High | For SPA connect inverter |  | SPA used |
| 2103 | Extra AC Power to grid_L | Extrainverte AC Power to grid Low |  |  | SPA used |
| 2104 | Eextra_today H | Extra inverter PowerTOUser_Extra today (high) | R | 0.1kWh | SPA used |
| 2105 | Eextra_today L | Extra inverter PowerTOUser_Extra today (low) | R | 0.1kWh | SPA used |
| 2106 | Eextra_total H | Extra inverter PowerTOUser_Extratotal(high) |  | 0.1kWh | SPA used |
| 2107 | Eextra_total L | Extra inverter PowerTOUser_Extra total(low) |  | 0.1kWh | SPA used |
| 2108 | Esystem_today H | System electric energy today H |  | 0.1kWh | SPA used System electric energy today H |
| 2109 | Esystem_ today L | System electric energy today L |  | 0.1kWh | SPA used System electric energy today L |
| 2110 | Esystem_total H | System electric energy total H |  | 0.1kWh | SPA used System |

|  |  |  |  |  |  | electric energy total H |
| --- | --- | --- | --- | --- | --- | --- |
| 2111 | Esystem_ total L | System electric energy total L |  | 0.1kWh |  | SPA used System electric energy total L |
| 2112 | EACharge_Today _H | ACCharge energy today |  | 0.1kwh |  | Storage Power |
| 2113 | EACharge_Today _L | ACCharge energy today |  | 0.1kwh |  | Storage Power |
| 2114 | EACharge_Total _H | ACCharge energy total |  | 0.1kwh |  | Storage Power |
| 2115 | EACharge_Total _L | ACCharge energy total |  | 0.1kwh |  | Storage Power |
| 2116 | AC charge Power_H | Grid power to local load |  | 0.1kwh |  | Storage Power |
| 2117 | AC charge Power_L | Grid power to local load |  | 0.1kwh |  | Storage Power |
| 2118 | Priority | 0:Load First 1:Battery First 2:Grid First |  |  |  | Storage Power |
| 2119 | Battery Type | 0：Lead-acid 1：Lithium battery |  |  |  | Storage Power |
| 2120 | AutoProofreadC MD | Aging mode |  |  |  | Storage Power |
| … | reserved |  |  |  |  | reserved |
| 2124. | reserved |  |  |  |  | reserved |
| Use for TL-X and TL-XH |  |  |  |  |  |  |
| 3000 | Inverter Status | Inverter run state High 8 bits mode (specific mode) 0: Waiting module 1: Self-test mode, optional 2: Reserved 3：SysFault module 4: Flash module 5：PVBATOnline module: 6：BatOnline module |  |  |  |  |

|  |  | 7：PVOfflineMode 8：BatOfflineMode The lower 8 bits indicate the machine status (web page display) 0: StandbyStatus; 1: NormalStatus; 3: FaultStatus 4：FlashStatus; |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 3001 | Ppv H | PV total power |  | 0.1W |  |
| 3002 | Ppv L |  |  |  |  |
| 3003 | Vpv1 | PV1 voltage |  | 0.1V |  |
| 3004 | Ipv1 | PV1 input current |  | 0.1A |  |
| 3005 | Ppv1 H | PV1 power |  | 0.1W |  |
| 3006 | Ppv1 L |  |  |  |  |
| 3007 | Vpv2 | PV2 voltage |  | 0.1V |  |
| 3008 | Ipv2 | PV2 input current |  | 0.1A |  |
| 3009 | Ppv2 H | PV2 power |  | 0.1W |  |
| 3010 | Ppv2 L |  |  |  |  |
| 3011 | Vpv3 | PV3 voltage |  | 0.1V |  |
| 3012 | Ipv3 | PV3 input current |  | 0.1A |  |
| 3013 | Ppv3 H | PV3 power |  | 0.1W |  |
| 3014 | Ppv3 L |  |  |  |  |
| 3015 | Vpv4 | PV4 voltage |  |  |  |
| 3016 | Ipv4 | PV4 input current |  |  |  |
| 3017 | Ppv4H | PV4 power |  |  |  |
| 3018 | Ppv4L |  |  |  |  |
| 3019 | Psys H | System output power |  | 0.1W |  |
| 3020 | Psys L |  |  |  |  |
| 3021 | Qac H | reactive power |  | 0.1Var |  |
| 3022 | Qac L |  |  |  |  |
| 3023 | Pac H | Output power |  | 0.1W | Output power |
| 3024 | Pac L |  |  |  |  |
| 3025 | Fac | Grid frequency |  | 0.01Hz | Grid frequency |
| 3026 | Vac1 | Three/single phase grid voltage |  | 0.1V | Three/single phase grid voltage |
| 3027 | Iac1 | Three/single phase grid output current |  | 0.1A | Three/single |

|  |  |  |  |  | phase grid output current |
| --- | --- | --- | --- | --- | --- |
| 3028 | Pac1 H | Three/single phase grid output watt VA |  | 0.1VA | Three/single phase grid output watt VA |
| 3029 | Pac1 L |  |  |  |  |
| 3030 | Vac2 | Three phase grid voltage |  | 0.1V | Three phase grid voltage |
| 3031 | Iac2 | Three phase grid output current |  | 0.1A | Three phase grid output current |
| 3032 | Pac2 H | Three phase grid output power |  | 0.1VA | Three phase grid output power |
| 3033 | Pac2 L |  |  |  |  |
| 3034 | Vac3 | Three phase grid voltage |  | 0.1V | Three phase grid voltage |
| 3035 | Iac3 | Three phase grid output current |  | 0.1A | Three phase grid output current |
| 3036 | Pac3 H | Three phase grid output power |  | 0.1VA | Three phase grid output power |
| 3037 | Pac3 L |  |  |  |  |
| 3038 | Vac_RS | Three phase grid voltage |  | 0.1V |  |
| 3039 | Vac_ST | Three phase grid voltage |  | 0.1V |  |
| 3040 | Vac_TR | Three phase grid voltage |  | 0.1V |  |
| 3041 | Ptouser total H | Total forward power |  | 0.1W | Total forward power |
| 3042 | Ptouser total L |  |  |  |  |
| 3043 | Ptogrid total H | Total reverse power |  | 0.1W | Total reverse power |
| 3044 | Ptogrid total L |  |  |  |  |
| 3045 | Ptoload total H | Total load power |  | 0.1W | Total load power |
| 3046 | Ptoload total L |  |  |  |  |
| 3047 | Time total H | Work time total |  | 0.5s |  |
| 3048 | Time total L |  |  |  |  |
| 3049 | Eac today H | Today generate energy |  | 0.1kWh | Today generate energy |
| 3050 | Eac today L |  |  |  |  |
| 3051 | Eac total H | Total generate energy |  | 0.1kWh | Total generate |
| 3052 | Eac total L |  |  |  |  |

|  |  |  |  |  | energy |
| --- | --- | --- | --- | --- | --- |
| 3053 | Epv_total H | PV energy total |  | 0.1kWh | PV energy total |
| 3054 | Epv_total L |  |  |  |  |
| 3055 | Epv1_today H | PV1 energy today |  | 0.1kWh |  |
| 3056 | Epv1_today L |  |  |  |  |
| 3057 | Epv1_total H | PV1 energy total |  | 0.1kWh |  |
| 3058 | Epv1_total L |  |  |  |  |
| 3059 | Epv2_today H | PV2 energy today |  | 0.1kWh |  |
| 3060 | Epv2_today L |  |  |  |  |
| 3061 | Epv2_total H | PV2 energy total |  | 0.1kWh |  |
| 3062 | Epv2_total L |  |  |  |  |
| 3063 | Epv3_today H | PV3 energy today |  | 0.1kWh |  |
| 3064 | Epv3_today L |  |  |  |  |
| 3065 | Epv3_total H | PV3 energy total |  | 0.1kWh |  |
| 3066 | Epv3_total L |  |  |  |  |
| 3067 | Etouser_today H | Today energy to user |  | 0.1kWh | Today energy to user |
| 3068 | Etouser_today L |  |  |  |  |
| 3069 | Etouser_total H | Total energy to user |  | 0.1kWh | Total energy to user |
| 3070 | Etouser_total L |  |  |  |  |
| 3071 | Etogrid_today H | Today energy to grid |  | 0.1kWh | Today energy to grid |
| 3072 | Etogrid_today L |  |  |  |  |
| 3073 | Etogrid_total H | Total energy to grid |  | 0.1kWh | Total energy to grid |
| 3074 | Etogrid_total L |  |  |  |  |
| 3075 | Eload_today H | Today energy of user load |  | 0.1kWh | Today energy of user load |
| 3076 | Eload_today L |  |  |  |  |
| 3077 | Eload_total H | Total energy of user load |  | 0.1kWh | Total energy of user load |
| 3078 | Eload_total L |  |  |  |  |
| 3079 | Epv4_today H | PV4 energy today |  | 0.1kWh |  |
| 3080 | Epv4_today L |  |  |  |  |
| 3081 | Epv4_total H | PV4 energy total |  | 0.1kWh |  |
| 3082 | Epv4_total L |  |  |  |  |
| 3083 | Epv_today H | PV energy today |  | 0.1kWh |  |
| 3084 | Epv_today L |  |  |  |  |

| 3085 | Reserved |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 3086 | DeratingMode | DeratingMode |  |  | 0:cNOTDerate 1:cPVHighDer ate 2: cPowerCon stantDerate 3: cGridVHigh Derate 4:cFreqHighD erate 5:cDcSoureM odeDerate 6:cInvTemprD erate 7:cActivePow erOrder 8:cLoadSpeed Process 9:cOverBack byTime 10:cInternalT emprDerate 11:cOutTemp rDerate 12:cLineImpe CalcDerate 13: cParallelA ntiBackflowD erate 14:cLocalAnti BackflowDera te 15:cBdcLoadP riDerate 16:cChkCTErr Derate |
| 3087 | ISO | PV ISO value |  | 1KΩ |  |
| 3088 | DCI_R | R DCI Curr |  | 0.1mA |  |
| 3089 | DCI_S | S DCI Curr |  | 0.1mA |  |
| 3090 | DCI_T | T DCI Curr |  | 0.1mA |  |
| 3091 | GFCI | GFCI Curr |  | 1mA |  |
| 3092 | Bus Voltage | total bus voltage |  | 0.1V |  |

| 3093 | Temp1 | Inverter temperature |  | 0.1℃ |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3094 | Temp2 | The inside IPM in inverter temperature |  | 0.1℃ |  |  |
| 3095 | Temp3 | Boost temperature |  | 0.1℃ |  |  |
| 3096 | Temp4 | Reserved |  | 0.1℃ |  |  |
| 3097 | Temp5 | Commmunication broad temperature |  | 0.1℃ |  |  |
| 3098 | P Bus Voltage | P Bus inside Voltage |  | 0.1V |  |  |
| 3099 | N Bus Voltage | N Bus inside Voltage |  | 0.1V |  |  |
| 3100 | IPF | Inverter output PF now |  |  | 0-20000 |  |
| 3101 | RealOPPercent | Real Output power Percent |  | 1% | 1~100 |  |
| 3102 | OPFullwatt H | Output Maxpower Limited |  | 0.1W | Output Maxpower Limited |  |
| 3103 | OPFullwatt L |  |  |  |  |  |
| 3104 | StandbyFlag | Inverter standby flag |  | bitfield | bit0:turn Order； bit1:PV Low bit2:AC Volt/Freq out of scope bit3~bit7 Reserved | off ； ； ： |
| 3105 | Fault Maincode | Inverter fault maincode |  |  |  |  |
| 3106 | Warn Maincode | Inverter Warning maincode |  |  |  |  |
| 3107 | Fault Subcode | Inverter fault subcode |  | bitfield |  |  |
| 3108 | Warn Subcode | Inverter Warning subcode |  | bitfield |  |  |
| 3109 |  |  |  | bitfield |  |  |
| 3110 |  |  |  | bitfield |  |  |
| 3111 | uwPresentFFTVa lue [CHANNEL_A ] | PresentFFTValue [CHANNEL_A] |  | bitfield |  |  |
| 3112 | bAfciStatus | AFCI Status |  |  | 0 ： waiting state 1：self-check 2：Detection of arcing state 3：fault state 4 ： update state |  |
| 3113 | uwStrength[CHA NNEL_A] | AFCI Strength[CHANNEL_A] |  |  |  |  |

| 3114 | uwSelfCheckVal ue[CHANNEL_A] | AFCI SelfCheck[CHANNEL_A] |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 3115 | inv start delay time | inv start delay time |  | 1S | inv start delay time |
| 3116 | Reserved |  |  |  |  |
| 3117 | Reserved |  |  |  |  |
| 3118 | BDC_OnOffState | BDC connect state |  |  | 0:No BDC Connect 1:BDC1 Connect 2:BDC2 Connect 3:BDC1+BDC2 Connect |
| 3119 | DryContactState | Current status of DryContact |  |  | Current status of DryContact 0: turn off; 1: turn on; |
| 3120 | Reserved |  |  |  |  |
| 3121 | Pself H | self-use power |  | 0.1W |  |
| 3122 | Pself L |  |  |  |  |
| 3123 | Esys_today H | System energy today |  | 0.1kwh |  |
| 3124 | Esys_today L |  |  |  |  |
| 3125 | Edischr_today H | Today discharge energy |  | 0.1kWh | Today discharge energy |
| 3126 | Edischr_today L |  |  |  |  |
| 3127 | Edischr_total H | Total discharge energy |  | 0.1kWh | Total discharge energy |
| 3128 | Edischr_total L |  |  |  |  |
| 3129 | Echr_today H | Charge energy today |  | 0.1kWh | Charge energy today |
| 3130 | Echr_today L |  |  |  |  |
| 3131 | Echr_total H | Charge energy total |  | 0.1kWh | Charge energy total |
| 3132 | Echr_total L |  |  |  |  |
| 3133 | Eacchr_today H | Today energy of AC charge |  | 0.1kWh | Today energy of AC charge |
| 3134 | Eacchr_today L |  |  |  |  |
| 3135 | Eacchr_total H | Total energy of AC charge |  | 0.1kWh | Total energy of AC charge |
| 3136 | Eacchr_total L |  |  |  |  |
| 3137 | Esys_total H |  |  |  |  |

| 3138 | Esys_total L | Total energy of system output \ |  | 0.1kWh |  |
| --- | --- | --- | --- | --- | --- |
| 3139 | Eself_today H | Today energy of Self output |  | 0.1kWh |  |
| 3140 | Eself_today L |  |  |  |  |
| 3141 | Eself_total H | Total energy of Self output |  | 0.1kwh |  |
| 3142 | Eself_ total L |  |  |  |  |
| 3143 | Reserved |  |  |  |  |
| 3144 | Priority | Word Mode |  |  | 0 LoadFirst 1 BatteryFirs t 2 GridFirst |
| 3145 | EPS Fac | UPS frequency |  | 0.01Hz |  |
| 3146 | EPS Vac1 | UPS phase R output voltage |  | 0.1V |  |
| 3147 | EPS Iac1 | UPS phase R output current |  | 0.1A |  |
| 3148 | EPS Pac1 H | UPS phase R output power |  | 0.1VA |  |
| 3149 | EPS Pac1 L |  |  |  |  |
| 3150 | EPS Vac2 | UPS phase S output voltage |  | 0.1V |  |
| 3151 | EPS Iac2 | UPS phase S output current |  | 0.1A |  |
| 3152 | EPS Pac2 H | UPS phase S output power |  | 0.1VA |  |
| 3153 | EPS Pac2 L |  |  |  |  |
| 3154 | EPS Vac3 | UPS phase T output voltage |  | 0.1V |  |
| 3155 | EPS Iac3 | UPS phase T output current |  | 0.1A |  |
| 3156 | EPS Pac3 H | UPS phase T output power |  | 0.1VA |  |
| 3157 | EPS Pac3 L |  |  |  |  |
| 3158 | EPS Pac H | UPS output power |  | 0.1VA |  |
| 3159 | EPS Pac L |  |  |  |  |
| 3160 | Loadpercent | Load percent of UPS ouput |  | 0.10% |  |
| 3161 | PF | Power factor |  | 0.1 |  |
| 3162 | DCV | DC voltage |  | 1mV |  |
| 3163 | Reserved |  |  |  |  |
| 3164 | NewBdcFlag | Whether to parse BDC data separately |  |  | 0: Don't need 1：need |
| 3165 | BDCDeratingMo de | BDCDeratingMode： 0: Normal, unrestricted 1：Standby or fault 2：Maximum battery current limit (discharge) 3：Battery discharge Enable (Discharge) 4：High bus discharge derating |  |  |  |

|  |  | (discharge) 5：High temperature discharge derating (discharge) 6：System warning No discharge (discharge) 7-15 Reserved (Discharge) 16：Maximum charging current of battery (charging) 17：High Temperature (LLC and Buckboost) (Charging) 18：Final soft charge 19：SOC setting limits (charging) 20：Battery low temperature (charging) 21：High bus voltage (charging) 22：Battery SOC (charging) 23: Need to charge (charge） 24: System warning not charging (charging) 25-29：Reserve (charge) |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 3166 | SysState_Mode | System work State and mode The upper 8 bits indicate the mode; 0：No charge and discharge； 1：charge； 2：Discharge； The lower 8 bits represent the status; 0: StandbyStatus; 1: NormalStatus; 2: FaultStatus 3：FlashStatus; |  |  | BDC1 |
| 3167 | FaultCode | Storge device fault code |  |  |  |
| 3168 | WarnCode | Storge device warning code |  |  |  |
| 3169 | Vbat | Battery voltage |  | 0.01V |  |
| 3170 | Ibat | Battery current |  | 0.1A |  |
| 3171 | SOC | State of charge Capacity |  | 1% |  |
| 3172 | Vbus1 | Total BUS voltage |  | 0.1V |  |
| 3173 | Vbus2 | On the BUS voltage |  | 0.1V |  |
| 3174 | Ibb | BUCK-BOOST Current |  | 0.1A |  |
| 3175 | Illc | LLC Current |  | 0.1A |  |
| 3176 | TempA | Temperture A |  | 0.1℃ |  |
| 3177 | TempB | Temperture B |  | 0.1℃ |  |
| 3178 | Pdischr H | Discharge power |  | 0.1W |  |
| 3179 | Pdischr L |  |  |  |  |

| 3180 | Pchr H | Charge power |  | 0.1W |  |
| --- | --- | --- | --- | --- | --- |
| 3181 | Pchr L |  |  |  |  |
| 3182 | Edischr_total H | Discharge total energy of storge device |  | 0.1kWh |  |
| 3183 | Edischr_total L |  |  |  |  |
| 3184 | Echr_total H | Charge total energy of storge device |  | 0.1kWh |  |
| 3185 | Echr_total L |  |  |  |  |
| 3186 | Reserved | Reserved |  |  |  |
| 3187 | BDC1_Flag | BDC mark (charge and discharge, fault alarm code) Bit0: ChargeEn; BDC allows charging Bit1: DischargeEn; BDC allows discharge Bit2~7: Resvd; reserved Bit8~11: WarnSubCode; BDC sub-warning code Bit12~15: FaultSubCode; BDC sub-error code |  |  |  |
| 3188 | Vbus2 | Lower BUS voltage |  | 0.1V |  |
| 3189 | BmsMaxVoltCell No | BmsMaxVoltCellNo |  |  |  |
| 3190 | BmsMinVoltCell No | BmsMinVoltCellNo |  |  |  |
| 3191 | BmsBatteryAvgT emp | BmsBatteryAvgTemp |  |  |  |
| 3192 | BmsMaxCellTem p | BmsMaxCellTemp |  | 0.1°C |  |
| 3193 | BmsBatteryAvgT emp | BmsBatteryAvgTemp |  | 0.1°C |  |
| 3194 | BmsMaxCellTem p | BmsMaxCellTemp |  |  |  |
| 3195 | BmsBatteryAvgT emp | BmsBatteryAvgTemp |  |  |  |
| 3196 | BmsMaxSOC | BmsMaxSOC |  | 1% |  |
| 3197 | BmsMinSOC | BmsMinSOC |  | 1% |  |
| 3198 | ParallelBatteryN um | ParallelBatteryNum |  |  |  |
| 3199 | BmsDerateReas on | BmsDerateReason |  |  |  |
| 3200 | BmsGaugeFCC （Ah） | BmsGaugeFCC（Ah） |  |  |  |

| 3201 | BmsGaugeRM （Ah） | BmsGaugeRM（Ah） |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 3202 | BmsError | BMS Protect1 |  |  |  |
| 3203 | BmsWarn | BMSWarn1 |  |  |  |
| 3204 | BmsFault | BMS Fault1 |  |  |  |
| 3205 | BmsFault2 | BMS Fault2 |  |  |  |
| 3206 | Reserved |  |  |  |  |
| 3207 | Reserved |  |  |  |  |
| 3208 | Reserved |  |  |  |  |
| 3209 | Reserved |  |  |  |  |
| 3210 | BatIsoStatus | Battery ISO detection status |  |  | 0：Not detected 1：Detection completed |
| 3211 | BattNeedCharge RequestFlag | battery work request |  | bit0:1： Prohibit chargin g，0： Allow the chargin g bit1:1： Enable strong charge， 0： disable strong charge bit2:1： Enable strong charge2 0： disable strong charge |  |

|  |  |  |  | 2 bit8:1: Dischar ge is prohibit ed， 0： allow discharg e bit9:1： Turn on power reductio n 0： turn off power reductio n； |  |
| --- | --- | --- | --- | --- | --- |
| 3212 | BMS_Status | battery working status | R |  | 0: dormancy 1:Charge 2:Discharge 3:free 4:standby 5:Soft start 6:fault 7:update |
| 3213 | BmsError2 | BMS Protect2 | R | 1 |  |
| 3214 | BmsWarn2 | BMS Warn2 | R | 1 |  |
| 3215 | BMS_SOC | BMS SOC | R | 1% |  |
| 3216 | BMS_BatteryVol t | BMS BatteryVolt | R | 0.01V |  |
| 3217 | BMS_BatteryCur r | BMS BatteryCurr | R | 0.01A |  |
| 3218 | BMS_BatteryTe mp | battery cell maximum temperature | R | 0.1℃ |  |
| 3219 | BMS_MaxCurr | Maximum charging current | R | 0.01A |  |
| 3220 | BMS_MaxDischr Curr | Maximum discharge current | R | 0.01A |  |
| 3221 | BMS_CycleCnt | BMSCycleCnt | R | 1 |  |

| 3222 | BMS_SOH | BMS SOH | R | 1 |  |
| --- | --- | --- | --- | --- | --- |
| 3223 | BMS_ChargeVol tLimit | Battery charging voltage limit value | R | 0.01V |  |
| 3224 | BMS_Discharge VoltLimit | Battery discharge voltage limit value |  |  |  |
| 3225 | Bms Warn3 | BMS Warn 3 | R | 1 |  |
| 3226 | Bms Error3 | BMS Protect3 | R | 1 |  |
| 3227 | Reserved |  |  |  |  |
| 3228 | Reserved |  |  |  |  |
| 3229 | Reserved |  |  |  |  |
| 3230 | BMSSingleVoltM ax | BMS Battery SingleVoltMax | R | 0.001V |  |
| 3231 | BMSSingleVoltM in | BMS Battery SingleVoltMin | R | 0.001V |  |
| 3232 | BatLoadVolt | Battery LoadVolt | R | 0.01V | [0，650.00] |
| 3233 |  |  |  |  |  |
| 3234 | Debug data1 | Debug data1 | R |  |  |
| 3235 | Debug data2 | Debug data2 | R |  |  |
| 3236 | Debug data3 | Debug data3 | R |  |  |
| 3237 | Debug data4 | Debug data4 | R |  |  |
| 3238 | Debug data5 | Debug data5 | R |  |  |
| 3239 | Debug data6 | Debug data6 | R |  |  |
| 3240 | Debug data7 | Debug data7 | R |  |  |
| 3241 | Debug data8 | Debug data8 | R |  |  |
| 3242 | Debug data9 | Debug data9 | R |  |  |
| 3243 | Debug data10 | Debug data10 | R |  |  |
| 3244 | Debug data10 | Debug data10 | R |  |  |
| 3245 | Debug data12 | Debug data12 | R |  |  |
| 3246 | Debug data13 | Debug data13 | R |  |  |
| 3247 | Debug data14 | Debug data14 | R |  |  |
| 3248 | Debug data15 | Debug data15 | R |  |  |

| 3249 | Debug data16 | Debug data16 | R |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 3250 | Pex1H | PV inverter 1 output power H | R | 0.1W |  |  |
| 3251 | Pex1L | PV inverter 1 output power L | R | 0.1W |  |  |
| 3252 | Pex2H | PV inverter 2 output power H | R | 0.1W |  |  |
| 3253 | Pex2L | PV inverter 2 output power L | R | 0.1W |  |  |
| 3254 | Eex1TodayH | PV inverter 1 energy Today H | R | 0.1kWh |  |  |
| 3255 | Eex1TodayL | PV inverter 1 energy Today L | R | 0.1kWh |  |  |
| 3256 | Eex2TodayH | PV inverter 2 energy Today H | R | 0.1kWh |  |  |
| 3257 | Eex2TodayL | PV inverter 2 energy Today L | R | 0.1kWh |  |  |
| 3258 | Eex1TotalH | PV inverter 1 energy Total H | R | 0.1kWh |  |  |
| 3259 | Eex1TotalL | PV inverter 1 energy Total L | R | 0.1kWh |  |  |
| 3260 | Eex2TotalH | PV inverter 2 energy Total H | R | 0.1kWh |  |  |
| 3261 | Eex2TotalL | PV inverter 2 energy Total L | R | 0.1kWh |  |  |
| 3262 | uwBatNo | battery pack number | R |  | BDC reports are updated every 15 minutes |  |
| 3263 | BatSerialNum1 | Battery pack serial numberSN[0]SN[1] | R |  | BDC reports are updated every minutes | 15 |
| 3264 | BatSerialNum2 | Battery pack serial numberSN[2]SN[3] | R |  |  |  |
| 3265 | BatSerialNum3 | Battery pack serial numberSN[4]SN[5] | R |  |  |  |
| 3266 | BatSerialNum4 | Battery pack serial numberSN[6]SN[7] | R |  |  |  |
| 3267 | BatSerialNum5 | Battery pack serial numberSN[8]SN[9] | R |  |  |  |
| 3268 | BatSerialNum6 | Battery pack serial numberSN[10]SN[11] | R |  |  |  |
| 3269 | BatSerialNum7 | Battery pack serial numberSN[12]SN[13] | R |  |  |  |
| 3270 | BatSerialNum8 | Battery pack serial numberSN[14]SN[15] | R |  |  |  |
| 3271- 3279 | Reserve | Reserve |  |  |  |  |
| 3280 | bClrTodayDataFl ag | Clear day data flag | R |  | Data of current | the day |
|  |  |  |  |  | that server | the |
|  |  |  |  |  | determines whether to clear. 0:not cleared. 1: Clear. |  |
| BDC and BMS information (support up to 10 PARALLEL BDCS) |  |  |  |  |  |  |
| 4000- 4107 | 1 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number). |  |  |  |  |
| 4108- 4215 | 2 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number). |  |  |  |  |
| …… |  | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number). |  |  |  |  |
| 4864- 4971 | 9 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number). |  |  |  |  |
| 4972- 5079 | 10 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number). |  |  |  |  |

# Set address

Refer to the Inverter user manual.	Always is :

Knock the pv inverter to let the lcd display to the “COM Addr: xxx”, then double knock, if displays “Move”, you should another double knock, until it displays a address number, then you can give a single knock to change the address, this address will be remembered when the lcd backlight off.

# Notice

- It can drive mostly 32 pv inverters for one rs485 comport.

- There are only read input and hold registers commands even the newest version.

- App user could only care the input register.

- App user could not care the holding registers.

- Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing the other registers;