## Parameter
Wert | Parameter
JSON Susciption | cmnd/WSABINV
JSON Publish | tele/WSABINV
Modbus Adress | 5
Thing | mqtt:topic:growatt
Alias | Growatt_
Category | energy
Group | Photovoltaik, Boden
Tag | PV-Anlage

## SPH-UP registers 1.24
Shortlist | Function | Register | Variablename | Description | Write or not | Value | Unit | Initial value | Note | Device | Format | Unit | Decimal | Channel | Item | NO.,Variable,Data Source,String,Modbus Slave Addr.,Modbus Function,Modbus RegAddr,645 ID,645 Type, Data Len,4 Bytes Order,Data Format,Position of Bool,Decimal Position,Unit,With Qutation,Query Period,645 version, Func sel, JSON array, substract, divide, FE number, | No.,mode (set coil1 set; register2; transparent3), JSON name, slave address, register address, coil on1 or off0, number of register bytes, big-endin and little-endin (0 is big)
X | 4 | 0 | InverterStatus | Inverter run state |  | 0:waiting, |  |  |  | ALL |  |  | 0 | Type number : InverterStatus "Growatt_InverterStatus" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.InverterStatus"] | Number Growatt_InverterStatus "InverterStatus" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:InverterStatus"} | 1.,InverterStatus,Modbus RTU,,5,4,0,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1 | PpvH | Input power (high) |  |  | 0.1W |  | ASCII | TL_X-TL_XH | 0.1 | W | 1 | Type number : PpvH "Growatt_PpvH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PpvH"] | Number:Power Growatt_PpvH "PpvH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PpvH"} | 2.,PpvH,Modbus RTU,,5,4,1,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 2 | PpvL | Input power (low) |  |  | 0.1W |  | ASCII | TL_X-TL_XH | 0.1 | W | 1 | Type number : PpvL "Growatt_PpvL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PpvL"] | Number:Power Growatt_PpvL "PpvL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PpvL"} | 2.,PpvL,Modbus RTU,,5,4,2,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 3 | Vpv1 | PV1 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv1 "Growatt_Vpv1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv1"] | Number:ElectricPotential Growatt_Vpv1 "Vpv1 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv1"} | 3.,Vpv1,Modbus RTU,,5,4,3,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
X | 4 | 4 | PV1Curr | PV1 input current |  |  | 0.1A |  | With Time1 | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV1Curr "Growatt_PV1Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV1Curr"] | Number:ElectricCurrent Growatt_PV1Curr "PV1Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV1Curr"} | 4.,PV1Curr,Modbus RTU,,5,4,4,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
X | 4 | 5 | Ppv1H | PV1 input power(high) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv1H "Growatt_Ppv1H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv1H"] | Number:Power Growatt_Ppv1H "Ppv1H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv1H"} | 5.,Ppv1H,Modbus RTU,,5,4,5,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 6 | Ppv1L | PV1 input power(low) |  |  | 0.1W |  |  | USTimeSet | 0.1 | W | 1 | Type number : Ppv1L "Growatt_Ppv1L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv1L"] | Number:Power Growatt_Ppv1L "Ppv1L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv1L"} | 5.,Ppv1L,Modbus RTU,,5,4,6,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 7 | Vpv2 | PV2 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv2 "Growatt_Vpv2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv2"] | Number:ElectricPotential Growatt_Vpv2 "Vpv2 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv2"} | 6.,Vpv2,Modbus RTU,,5,4,7,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
X | 4 | 8 | PV2Curr | PV2 input current |  |  | 0.1A |  | With Time1 | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV2Curr "Growatt_PV2Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV2Curr"] | Number:ElectricCurrent Growatt_PV2Curr "PV2Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV2Curr"} | 7.,PV2Curr,Modbus RTU,,5,4,8,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
X | 4 | 9 | Ppv2H | PV2 input power (high) |  |  | 0.1W |  | bit0~7:day; bit8~14:month bit15, 0:disable | USTimeSet | 0.1 | W | 1 | Type number : Ppv2H "Growatt_Ppv2H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv2H"] | Number:Power Growatt_Ppv2H "Ppv2H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv2H"} | 8.,Ppv2H,Modbus RTU,,5,4,9,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 10 | Ppv2L | PV2 input power (low) |  |  | 0.1W |  | bit0~7:day; bit8~14:month bit15, 0:disable 1: enable | USTimeSet | 0.1 | W | 1 | Type number : Ppv2L "Growatt_Ppv2L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv2L"] | Number:Power Growatt_Ppv2L "Ppv2L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv2L"} | 8.,Ppv2L,Modbus RTU,,5,4,10,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 11 | Vpv3 | PV3 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv3 "Growatt_Vpv3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv3"] | Number:ElectricPotential Growatt_Vpv3 "Vpv3 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv3"} | 8.,Vpv3,Modbus RTU,,5,4,11,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 12 | PV3Curr | PV3 input current |  |  | 0.1A |  | With Time1 | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV3Curr "Growatt_PV3Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV3Curr"] | Number:ElectricCurrent Growatt_PV3Curr "PV3Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV3Curr"} | 8.,PV3Curr,Modbus RTU,,5,4,12,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 13 | Ppv3H | PV3 input power (high) |  |  | 0.1W |  | With Time Month1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv3H "Growatt_Ppv3H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv3H"] | Number:Power Growatt_Ppv3H "Ppv3H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv3H"} | 8.,Ppv3H,Modbus RTU,,5,4,13,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 14 | Ppv3L | PV3 input power (low) |  |  | 0.1W |  | With Time Month1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv3L "Growatt_Ppv3L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv3L"] | Number:Power Growatt_Ppv3L "Ppv3L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv3L"} | 8.,Ppv3L,Modbus RTU,,5,4,14,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 15 | Vpv4 | PV4 voltage |  |  | 0.1V |  | ASCII | ALL | 0.1 | V | 1 | Type number : Vpv4 "Growatt_Vpv4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv4"] | Number:ElectricPotential Growatt_Vpv4 "Vpv4 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv4"} | 8.,Vpv4,Modbus RTU,,5,4,15,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 16 | PV4Curr | PV4 input current |  |  | 0.1A |  | Enable :1 | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV4Curr "Growatt_PV4Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV4Curr"] | Number:ElectricCurrent Growatt_PV4Curr "PV4Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV4Curr"} | 8.,PV4Curr,Modbus RTU,,5,4,16,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 17 | Ppv4H | PV4 input power (high) |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv4H "Growatt_Ppv4H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv4H"] | Number:Power Growatt_Ppv4H "Ppv4H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv4H"} | 8.,Ppv4H,Modbus RTU,,5,4,17,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 18 | Ppv4L | PV4 input power (low) |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv4L "Growatt_Ppv4L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv4L"] | Number:Power Growatt_Ppv4L "Ppv4L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv4L"} | 8.,Ppv4L,Modbus RTU,,5,4,18,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 19 | Vpv5 | PV5 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv5 "Growatt_Vpv5" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv5"] | Number:ElectricPotential Growatt_Vpv5 "Vpv5 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv5"} | 8.,Vpv5,Modbus RTU,,5,4,19,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 20 | PV5Curr | PV5 input current |  |  | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV5Curr "Growatt_PV5Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV5Curr"] | Number:ElectricCurrent Growatt_PV5Curr "PV5Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV5Curr"} | 8.,PV5Curr,Modbus RTU,,5,4,20,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 21 | Ppv5H | PV5 input power(high) |  |  | 0.1W |  | Mxxxx | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv5H "Growatt_Ppv5H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv5H"] | Number:Power Growatt_Ppv5H "Ppv5H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv5H"} | 8.,Ppv5H,Modbus RTU,,5,4,21,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 22 | Ppv5L | PV5 input power(low) |  |  | 0.1W |  | PxxUxx | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv5L "Growatt_Ppv5L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv5L"] | Number:Power Growatt_Ppv5L "Ppv5L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv5L"} | 8.,Ppv5L,Modbus RTU,,5,4,22,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 23 | Vpv6 | PV6 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv6 "Growatt_Vpv6" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv6"] | Number:ElectricPotential Growatt_Vpv6 "Vpv6 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv6"} | 8.,Vpv6,Modbus RTU,,5,4,23,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 24 | PV6Curr | PV6 input current |  |  | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV6Curr "Growatt_PV6Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV6Curr"] | Number:ElectricCurrent Growatt_PV6Curr "PV6Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV6Curr"} | 8.,PV6Curr,Modbus RTU,,5,4,24,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 25 | Ppv6H | PV6 input power (high) |  |  | 0.1W |  | DxxTxx | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv6H "Growatt_Ppv6H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv6H"] | Number:Power Growatt_Ppv6H "Ppv6H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv6H"} | 8.,Ppv6H,Modbus RTU,,5,4,25,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 26 | Ppv6L | PV6 input power (low) |  |  | 0.1W |  | SxxBxx | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv6L "Growatt_Ppv6L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv6L"] | Number:Power Growatt_Ppv6L "Ppv6L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv6L"} | 8.,Ppv6L,Modbus RTU,,5,4,26,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 27 | Vpv7 | PV7 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv7 "Growatt_Vpv7" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv7"] | Number:ElectricPotential Growatt_Vpv7 "Vpv7 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv7"} | 8.,Vpv7,Modbus RTU,,5,4,27,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 28 | PV7Curr | PV7 input current |  |  | 0.1A |  | With Time1 | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV7Curr "Growatt_PV7Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV7Curr"] | Number:ElectricCurrent Growatt_PV7Curr "PV7Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV7Curr"} | 8.,PV7Curr,Modbus RTU,,5,4,28,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 29 | Ppv7H | PV7 input power (high) |  |  | 0.1W |  | BMSCommunicati on interface type: | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv7H "Growatt_Ppv7H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv7H"] | Number:Power Growatt_Ppv7H "Ppv7H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv7H"} | 8.,Ppv7H,Modbus RTU,,5,4,29,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 30 | Ppv7L | PV7 input power (low) |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv7L "Growatt_Ppv7L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv7L"] | Number:Power Growatt_Ppv7L "Ppv7L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv7L"} | 8.,Ppv7L,Modbus RTU,,5,4,30,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 31 | Vpv8 | PV8 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv8 "Growatt_Vpv8" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv8"] | Number:ElectricPotential Growatt_Vpv8 "Vpv8 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv8"} | 8.,Vpv8,Modbus RTU,,5,4,31,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 32 | PV8Curr | PV8 input current |  |  | 0.1A |  | With Time1 | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV8Curr "Growatt_PV8Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV8Curr"] | Number:ElectricCurrent Growatt_PV8Curr "PV8Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV8Curr"} | 8.,PV8Curr,Modbus RTU,,5,4,32,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 33 | Ppv8H | PV8 input power (high) |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv8H "Growatt_Ppv8H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv8H"] | Number:Power Growatt_Ppv8H "Ppv8H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv8H"} | 8.,Ppv8H,Modbus RTU,,5,4,33,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 34 | Ppv8L | PV8 input power (low) |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv8L "Growatt_Ppv8L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv8L"] | Number:Power Growatt_Ppv8L "Ppv8L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv8L"} | 8.,Ppv8L,Modbus RTU,,5,4,34,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 35 | Pac | Output power (high) |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac "Growatt_Pac" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac"] | Number:Power Growatt_Pac "Pac [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac"} | 9.,Pac,Modbus RTU,,5,4,35,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 37 | Fac | Grid frequency |  |  | 0.01Hz |  |  | PV9_32 | 0.01 | Hz | 2 | Type number : Fac "Growatt_Fac" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Fac"] | Number:Frequency Growatt_Fac "Fac [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Fac"} | 10.,Fac,Modbus RTU,,5,4,37,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255
X | 4 | 38 | Vac1 | Three/single phase grid voltage |  |  | 0.1V |  | ASCII | ALL | 0.1 | V | 1 | Type number : Vac1 "Growatt_Vac1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac1"] | Number:ElectricPotential Growatt_Vac1 "Vac1 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac1"} | 11.,Vac1,Modbus RTU,,5,4,38,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
X | 4 | 39 | Iac1 | Three/single phase grid output current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Iac1 "Growatt_Iac1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Iac1"] | Number:ElectricCurrent Growatt_Iac1 "Iac1 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Iac1"} | 12.,Iac1,Modbus RTU,,5,4,39,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
X | 4 | 40 | Pac1H | Three/single phase grid output watt |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac1H "Growatt_Pac1H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac1H"] | Number:Power Growatt_Pac1H "Pac1H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac1H"} | 13.,Pac1H,Modbus RTU,,5,4,40,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 41 | Pac1L | Three/single phase grid output watt |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac1L "Growatt_Pac1L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac1L"] | Number:Power Growatt_Pac1L "Pac1L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac1L"} | 14.,Pac1L,Modbus RTU,,5,4,41,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 42 | Vac2 | Three phase grid voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vac2 "Growatt_Vac2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac2"] | Number:ElectricPotential Growatt_Vac2 "Vac2 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac2"} | 15.,Vac2,Modbus RTU,,5,4,42,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
X | 4 | 43 | Iac2 | Three phase grid output current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Iac2 "Growatt_Iac2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Iac2"] | Number:ElectricCurrent Growatt_Iac2 "Iac2 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Iac2"} | 16.,Iac2,Modbus RTU,,5,4,43,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
X | 4 | 44 | Pac2H | Three phase grid output power (high) |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac2H "Growatt_Pac2H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac2H"] | Number:Power Growatt_Pac2H "Pac2H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac2H"} | 17.,Pac2H,Modbus RTU,,5,4,44,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 45 | Pac2L | Three phase grid output power (low) |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac2L "Growatt_Pac2L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac2L"] | Number:Power Growatt_Pac2L "Pac2L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac2L"} | 18.,Pac2L,Modbus RTU,,5,4,45,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 46 | Vac3 | Three phase grid voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vac3 "Growatt_Vac3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac3"] | Number:ElectricPotential Growatt_Vac3 "Vac3 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac3"} | 19.,Vac3,Modbus RTU,,5,4,46,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
X | 4 | 47 | Iac3 | Three phase grid output current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Iac3 "Growatt_Iac3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Iac3"] | Number:ElectricCurrent Growatt_Iac3 "Iac3 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Iac3"} | 20.,Iac3,Modbus RTU,,5,4,47,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
X | 4 | 48 | Pac3H | Three phase grid output power (high) |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac3H "Growatt_Pac3H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac3H"] | Number:Power Growatt_Pac3H "Pac3H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac3H"} | 21.,Pac3H,Modbus RTU,,5,4,48,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 49 | Pac3L | Three phase grid output power (low) |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac3L "Growatt_Pac3L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac3L"] | Number:Power Growatt_Pac3L "Pac3L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac3L"} | 22.,Pac3L,Modbus RTU,,5,4,49,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 50 | Vac_RS | Three phase grid voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vac_RS "Growatt_Vac_RS" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac_RS"] | Number:ElectricPotential Growatt_Vac_RS "Vac_RS [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac_RS"} | 22.,Vac_RS,Modbus RTU,,5,4,50,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 51 | Vac_ST | Three phase grid voltage |  |  | 0.1V |  | ASCII | ALL | 0.1 | V | 1 | Type number : Vac_ST "Growatt_Vac_ST" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac_ST"] | Number:ElectricPotential Growatt_Vac_ST "Vac_ST [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac_ST"} | 22.,Vac_ST,Modbus RTU,,5,4,51,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 52 | Vac_TR | Three phase grid voltage |  |  | 0.1V |  | ASCII | ALL | 0.1 | V | 1 | Type number : Vac_TR "Growatt_Vac_TR" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac_TR"] | Number:ElectricPotential Growatt_Vac_TR "Vac_TR [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac_TR"} | 22.,Vac_TR,Modbus RTU,,5,4,52,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 53 | EactodayH | Today generate energy (high) |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : EactodayH "Growatt_EactodayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactodayH"] | Number:Energy Growatt_EactodayH "EactodayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactodayH"} | 22.,EactodayH,Modbus RTU,,5,4,53,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 54 | EactodayL | Today generate energy (low) |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : EactodayL "Growatt_EactodayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactodayL"] | Number:Energy Growatt_EactodayL "EactodayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactodayL"} | 22.,EactodayL,Modbus RTU,,5,4,54,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 55 | EactotalH | Total generate energy (high) |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : EactotalH "Growatt_EactotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactotalH"] | Number:Energy Growatt_EactotalH "EactotalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactotalH"} | 23.,EactotalH,Modbus RTU,,5,4,55,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 56 | EactotalL | Total generate energy (low) |  |  | 0.1kWh |  | System power H | BMS | 0.1 | kWh | 1 | Type number : EactotalL "Growatt_EactotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactotalL"] | Number:Energy Growatt_EactotalL "EactotalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactotalL"} | 23.,EactotalL,Modbus RTU,,5,4,56,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 57 | TimetotalH | Work time total (high) |  |  | 0.5s |  |  | ALL | 0.5 | s | 1 | Type number : TimetotalH "Growatt_TimetotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.TimetotalH"] | Number:Time Growatt_TimetotalH "TimetotalH [%0.5f s]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TimetotalH"} | 23.,TimetotalH,Modbus RTU,,5,4,57,1,9410,2,0,Unsigned int,0,1,s,1,100,97,0,0,0,1.000000,0,255
| 4 | 58 | TimetotalL | Work time total (low) |  |  | 0.5s |  | 0:Disable; | ALL | 0.5 | s | 1 | Type number : TimetotalL "Growatt_TimetotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.TimetotalL"] | Number:Time Growatt_TimetotalL "TimetotalL [%0.5f s]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TimetotalL"} | 23.,TimetotalL,Modbus RTU,,5,4,58,1,9410,2,0,Unsigned int,0,1,s,1,100,97,0,0,0,1.000000,0,255
X | 4 | 59 | Epv1_todayH | PV1Energy today(high) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv1_todayH "Growatt_Epv1_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv1_todayH"] | Number:Energy Growatt_Epv1_todayH "Epv1_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv1_todayH"} | 24.,Epv1_todayH,Modbus RTU,,5,4,59,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 60 | Epv1_todayL | PV1Energy today (low) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv1_todayL "Growatt_Epv1_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv1_todayL"] | Number:Energy Growatt_Epv1_todayL "Epv1_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv1_todayL"} | 24.,Epv1_todayL,Modbus RTU,,5,4,60,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 61 | Epv1_totalH | PV1Energy total(high) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv1_totalH "Growatt_Epv1_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv1_totalH"] | Number:Energy Growatt_Epv1_totalH "Epv1_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv1_totalH"} | 24.,Epv1_totalH,Modbus RTU,,5,4,61,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 62 | Epv1_totalL | PV1Energy total (low) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv1_totalL "Growatt_Epv1_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv1_totalL"] | Number:Energy Growatt_Epv1_totalL "Epv1_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv1_totalL"} | 24.,Epv1_totalL,Modbus RTU,,5,4,62,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 63 | Epv2_todayH | PV2Energy today(high) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv2_todayH "Growatt_Epv2_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv2_todayH"] | Number:Energy Growatt_Epv2_todayH "Epv2_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv2_todayH"} | 25.,Epv2_todayH,Modbus RTU,,5,4,63,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 64 | Epv2_todayL | PV2Energy today (low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv2_todayL "Growatt_Epv2_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv2_todayL"] | Number:Energy Growatt_Epv2_todayL "Epv2_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv2_todayL"} | 25.,Epv2_todayL,Modbus RTU,,5,4,64,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 65 | Epv2_totalH | PV2Energy total(high) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv2_totalH "Growatt_Epv2_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv2_totalH"] | Number:Energy Growatt_Epv2_totalH "Epv2_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv2_totalH"} | 25.,Epv2_totalH,Modbus RTU,,5,4,65,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 66 | Epv2_totalL | PV2Energy total (low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv2_totalL "Growatt_Epv2_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv2_totalL"] | Number:Energy Growatt_Epv2_totalL "Epv2_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv2_totalL"} | 25.,Epv2_totalL,Modbus RTU,,5,4,66,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 67 | Epv3_todayH | PV3 Energy today(high) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv3_todayH "Growatt_Epv3_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv3_todayH"] | Number:Energy Growatt_Epv3_todayH "Epv3_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv3_todayH"} | 25.,Epv3_todayH,Modbus RTU,,5,4,67,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 68 | Epv3_todayL | PV3 Energy today (low) |  |  | 0.1kWh |  | lith/leadacid | Storage | 0.1 | kWh | 1 | Type number : Epv3_todayL "Growatt_Epv3_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv3_todayL"] | Number:Energy Growatt_Epv3_todayL "Epv3_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv3_todayL"} | 25.,Epv3_todayL,Modbus RTU,,5,4,68,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 69 | Epv3_totalH | PV3 Energy total(high) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv3_totalH "Growatt_Epv3_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv3_totalH"] | Number:Energy Growatt_Epv3_totalH "Epv3_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv3_totalH"} | 25.,Epv3_totalH,Modbus RTU,,5,4,69,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 70 | Epv3_totalL | PV3 Energy total (low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv3_totalL "Growatt_Epv3_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv3_totalL"] | Number:Energy Growatt_Epv3_totalL "Epv3_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv3_totalL"} | 25.,Epv3_totalL,Modbus RTU,,5,4,70,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 71 | Epv4_todayH | PV4Energy today(high) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv4_todayH "Growatt_Epv4_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv4_todayH"] | Number:Energy Growatt_Epv4_todayH "Epv4_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv4_todayH"} | 25.,Epv4_todayH,Modbus RTU,,5,4,71,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 72 | Epv4_todayL | PV4Energy today (low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv4_todayL "Growatt_Epv4_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv4_todayL"] | Number:Energy Growatt_Epv4_todayL "Epv4_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv4_todayL"} | 25.,Epv4_todayL,Modbus RTU,,5,4,72,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 73 | Epv4_totalH | PV4Energy total(high) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv4_totalH "Growatt_Epv4_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv4_totalH"] | Number:Energy Growatt_Epv4_totalH "Epv4_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv4_totalH"} | 25.,Epv4_totalH,Modbus RTU,,5,4,73,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 74 | Epv4_totalL | PV4Energy total (low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv4_totalL "Growatt_Epv4_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv4_totalL"] | Number:Energy Growatt_Epv4_totalL "Epv4_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv4_totalL"} | 25.,Epv4_totalL,Modbus RTU,,5,4,74,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 75 | Epv5_todayH | PV5Energy today(high) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv5_todayH "Growatt_Epv5_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv5_todayH"] | Number:Energy Growatt_Epv5_todayH "Epv5_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv5_todayH"} | 25.,Epv5_todayH,Modbus RTU,,5,4,75,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 76 | Epv5_todayL | PV5Energy today (low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv5_todayL "Growatt_Epv5_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv5_todayL"] | Number:Energy Growatt_Epv5_todayL "Epv5_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv5_todayL"} | 25.,Epv5_todayL,Modbus RTU,,5,4,76,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 77 | Epv5_totalH | PV5Energy total(high) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv5_totalH "Growatt_Epv5_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv5_totalH"] | Number:Energy Growatt_Epv5_totalH "Epv5_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv5_totalH"} | 25.,Epv5_totalH,Modbus RTU,,5,4,77,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 78 | Epv5_totalL | PV5Energy total (low) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv5_totalL "Growatt_Epv5_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv5_totalL"] | Number:Energy Growatt_Epv5_totalL "Epv5_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv5_totalL"} | 25.,Epv5_totalL,Modbus RTU,,5,4,78,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 79 | Epv6_todayH | PV6Energy today(high) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv6_todayH "Growatt_Epv6_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv6_todayH"] | Number:Energy Growatt_Epv6_todayH "Epv6_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv6_todayH"} | 25.,Epv6_todayH,Modbus RTU,,5,4,79,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 80 | Epv6_todayL | PV6Energy today (low) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv6_todayL "Growatt_Epv6_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv6_todayL"] | Number:Energy Growatt_Epv6_todayL "Epv6_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv6_todayL"} | 25.,Epv6_todayL,Modbus RTU,,5,4,80,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 81 | Epv6_totalH | PV6Energy total(high) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv6_totalH "Growatt_Epv6_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv6_totalH"] | Number:Energy Growatt_Epv6_totalH "Epv6_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv6_totalH"} | 25.,Epv6_totalH,Modbus RTU,,5,4,81,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 82 | Epv6_totalL | PV6Energy total (low) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv6_totalL "Growatt_Epv6_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv6_totalL"] | Number:Energy Growatt_Epv6_totalL "Epv6_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv6_totalL"} | 25.,Epv6_totalL,Modbus RTU,,5,4,82,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 83 | Epv7_todayH | PV7Energy today(high) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv7_todayH "Growatt_Epv7_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv7_todayH"] | Number:Energy Growatt_Epv7_todayH "Epv7_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv7_todayH"} | 25.,Epv7_todayH,Modbus RTU,,5,4,83,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 84 | Epv7_todayL | PV7Energy today (low) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv7_todayL "Growatt_Epv7_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv7_todayL"] | Number:Energy Growatt_Epv7_todayL "Epv7_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv7_todayL"} | 25.,Epv7_todayL,Modbus RTU,,5,4,84,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 85 | Epv7_totalH | PV7 Energy total(high) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv7_totalH "Growatt_Epv7_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv7_totalH"] | Number:Energy Growatt_Epv7_totalH "Epv7_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv7_totalH"} | 25.,Epv7_totalH,Modbus RTU,,5,4,85,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 86 | Epv7_totalL | PV7Energy total (low) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv7_totalL "Growatt_Epv7_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv7_totalL"] | Number:Energy Growatt_Epv7_totalL "Epv7_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv7_totalL"} | 25.,Epv7_totalL,Modbus RTU,,5,4,86,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 87 | Epv8_todayH | PV8Energy today(high) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv8_todayH "Growatt_Epv8_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv8_todayH"] | Number:Energy Growatt_Epv8_todayH "Epv8_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv8_todayH"} | 25.,Epv8_todayH,Modbus RTU,,5,4,87,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 88 | Epv8_todayL | PV8Energy today (low) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv8_todayL "Growatt_Epv8_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv8_todayL"] | Number:Energy Growatt_Epv8_todayL "Epv8_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv8_todayL"} | 25.,Epv8_todayL,Modbus RTU,,5,4,88,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 89 | Epv8_totalH | PV8Energy total(high) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv8_totalH "Growatt_Epv8_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv8_totalH"] | Number:Energy Growatt_Epv8_totalH "Epv8_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv8_totalH"} | 25.,Epv8_totalH,Modbus RTU,,5,4,89,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 90 | Epv8_totalL | PV8Energy total (low) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv8_totalL "Growatt_Epv8_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv8_totalL"] | Number:Energy Growatt_Epv8_totalL "Epv8_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv8_totalL"} | 25.,Epv8_totalL,Modbus RTU,,5,4,90,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 91 | Epv_totalH | PV Energy total(high) |  |  | 0.1kWh |  | ApparentPower | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv_totalH "Growatt_Epv_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv_totalH"] | Number:Energy Growatt_Epv_totalH "Epv_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv_totalH"} | 25.,Epv_totalH,Modbus RTU,,5,4,91,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 92 | Epv_totalL | PV Energy total (low) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv_totalL "Growatt_Epv_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv_totalL"] | Number:Energy Growatt_Epv_totalL "Epv_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv_totalL"} | 25.,Epv_totalL,Modbus RTU,,5,4,92,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 93 | Temp1 | Inverter temperature |  |  | 0.1°C |  | 0%~100.0%,US regulations | ALL | 0.1 | °C | 1 | Type number : Temp1 "Growatt_Temp1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp1"] | Number:Temperature Growatt_Temp1 "Temp1 [%0.1f °C]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp1"} | 26.,Temp1,Modbus RTU,,5,4,93,1,9410,2,0,Unsigned int,0,1,°C,1,100,97,0,0,0,1.000000,0,255
| 4 | 94 | Temp2 | The inside IPM in inverter Temperature |  |  | 0.1°C |  | Q varies exponentially with time | ALL | 0.1 | °C | 1 | Type number : Temp2 "Growatt_Temp2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp2"] | Number:Temperature Growatt_Temp2 "Temp2 [%0.1f °C]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp2"} | 26.,Temp2,Modbus RTU,,5,4,94,1,9410,2,0,Unsigned int,0,1,°C,1,100,97,0,0,0,1.000000,0,255
| 4 | 95 | Temp3 | Boost temperature |  |  | 0.1°C |  | 0:disable | ALL | 0.1 | °C | 1 | Type number : Temp3 "Growatt_Temp3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp3"] | Number:Temperature Growatt_Temp3 "Temp3 [%0.1f °C]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp3"} | 26.,Temp3,Modbus RTU,,5,4,95,1,9410,2,0,Unsigned int,0,1,°C,1,100,97,0,0,0,1.000000,0,255
| 4 | 96 | Temp4 | [6 empty] | ALL |  |  | 0 | Type number : Temp4 "Growatt_Temp4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp4"] | Number Growatt_Temp4 "Temp4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp4"} | 26.,Temp4,Modbus RTU,,5,4,96,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 97 | uwBatVolt_DSP | BatVolt_DSP |  | 0.1V | BatVolt(DSP) |  | ASCII | ALL |  | BatVolt(DSP) | 0 | Type number : uwBatVolt_DSP "Growatt_uwBatVolt_DSP" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwBatVolt_DSP"] | #N/A | 26.,uwBatVolt_DSP,Modbus RTU,,5,4,97,1,9410,2,0,Unsigned int,0,0,BatVolt(DSP),1,100,97,0,0,0,1.000000,0,255
| 4 | 98 | PBusVoltage | P Bus inside Voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : PBusVoltage "Growatt_PBusVoltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PBusVoltage"] | Number:ElectricPotential Growatt_PBusVoltage "PBusVoltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PBusVoltage"} | 26.,PBusVoltage,Modbus RTU,,5,4,98,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 99 | NBusVoltage | N Bus inside Voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : NBusVoltage "Growatt_NBusVoltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.NBusVoltage"] | Number:ElectricPotential Growatt_NBusVoltage "NBusVoltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NBusVoltage"} | 26.,NBusVoltage,Modbus RTU,,5,4,99,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 100 | IPF | Inverter output PF now |  | 0-20000 |  |  |  | ALL |  |  | 0 | Type number : IPF "Growatt_IPF" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.IPF"] | Number Growatt_IPF "IPF" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:IPF"} | 26.,IPF,Modbus RTU,,5,4,100,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 101 | RealOPPercent | Real Output power Percent |  | 0,01 |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : RealOPPercent "Growatt_RealOPPercent" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.RealOPPercent"] | Number Growatt_RealOPPercent "RealOPPercent" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:RealOPPercent"} | 26.,RealOPPercent,Modbus RTU,,5,4,101,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 102 | OPFullwattH | Output Maxpower Limited high | [5 empty] | ALL |  |  | 0 | Type number : OPFullwattH "Growatt_OPFullwattH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.OPFullwattH"] | Number Growatt_OPFullwattH "OPFullwattH" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OPFullwattH"} | 26.,OPFullwattH,Modbus RTU,,5,4,102,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 103 | OPFullwattL | Output Maxpower Limited low |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : OPFullwattL "Growatt_OPFullwattL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.OPFullwattL"] | Number:Power Growatt_OPFullwattL "OPFullwattL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OPFullwattL"} | 26.,OPFullwattL,Modbus RTU,,5,4,103,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 104 | DeratingMode | DeratingMode |  | 0:no derate; |  |  | SPA | SPA |  |  | 0 | Type number : DeratingMode "Growatt_DeratingMode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DeratingMode"] | Number Growatt_DeratingMode "DeratingMode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DeratingMode"} | 26.,DeratingMode,Modbus RTU,,5,4,104,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 105 | FaultMaincode | Inverter fault maincode | [5 empty] | PV9_32 |  |  | 0 | Type number : FaultMaincode "Growatt_FaultMaincode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.FaultMaincode"] | Number Growatt_FaultMaincode "FaultMaincode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FaultMaincode"} | 26.,FaultMaincode,Modbus RTU,,5,4,105,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 107 | FaultSubcode | Inverter fault subcode | [5 empty] | PV9_32 |  |  | 0 | Type number : FaultSubcode "Growatt_FaultSubcode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.FaultSubcode"] | Number Growatt_FaultSubcode "FaultSubcode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FaultSubcode"} | 26.,FaultSubcode,Modbus RTU,,5,4,107,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 108 | RemoteCtrlEn |  |  | 0.Load First |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : RemoteCtrlEn "Growatt_RemoteCtrlEn" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.RemoteCtrlEn"] | Number Growatt_RemoteCtrlEn "RemoteCtrlEn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:RemoteCtrlEn"} | 26.,RemoteCtrlEn,Modbus RTU,,5,4,108,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 109 | RemoteCtrlPower |  |  | 2.Grid |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : RemoteCtrlPower "Growatt_RemoteCtrlPower" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.RemoteCtrlPower"] | Number Growatt_RemoteCtrlPower "RemoteCtrlPower" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:RemoteCtrlPower"} | 26.,RemoteCtrlPower,Modbus RTU,,5,4,109,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 110 | WarningbitH | Warning bit H |  |  |  |  | 0: Italian; | ALL |  |  | 0 | Type number : WarningbitH "Growatt_WarningbitH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.WarningbitH"] | Number Growatt_WarningbitH "WarningbitH" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:WarningbitH"} | 27.,WarningbitH,Modbus RTU,,5,4,110,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 111 | WarnSubcode | Inverter warn subcode | [5 empty] | ALL |  |  | 0 | Type number : WarnSubcode "Growatt_WarnSubcode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.WarnSubcode"] | Number Growatt_WarnSubcode "WarnSubcode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:WarnSubcode"} | 27.,WarnSubcode,Modbus RTU,,5,4,111,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 112 | WarnMaincode | Inverter warn maincode | [5 empty] | ALL |  |  | 0 | Type number : WarnMaincode "Growatt_WarnMaincode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.WarnMaincode"] | Number Growatt_WarnMaincode "WarnMaincode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:WarnMaincode"} | 27.,WarnMaincode,Modbus RTU,,5,4,112,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 113 | realPowerPercent | real Power Percent |  | 0-100 | % |  | ASCII | TL_X-TL_XH |  | % | 0 | Type number : realPowerPercent "Growatt_realPowerPercent" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.realPowerPercent"] | Number Growatt_realPowerPercent "realPowerPercent" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:realPowerPercent"} | 28.,realPowerPercent,Modbus RTU,,5,4,113,1,9410,2,0,Unsigned int,0,0,%,1,100,97,0,0,0,1.000000,0,255
| 4 | 114 | invstartdelaytime | inv start delay time | [5 empty] | ALL |  |  | 0 | Type number : invstartdelaytime "Growatt_invstartdelaytime" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.invstartdelaytime"] | Number Growatt_invstartdelaytime "invstartdelaytime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:invstartdelaytime"} | 28.,invstartdelaytime,Modbus RTU,,5,4,114,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 115 | bINVAllFaultCode | bINVAllFaultCode | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : bINVAllFaultCode "Growatt_bINVAllFaultCode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.bINVAllFaultCode"] | Number Growatt_bINVAllFaultCode "bINVAllFaultCode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bINVAllFaultCode"} | 28.,bINVAllFaultCode,Modbus RTU,,5,4,115,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 116 | ACchargePower_H | Grid power to local load |  |  | 0.1kWh |  |  | TL_X-TL_XH | 0.1 | kWh | 1 | Type number : ACchargePower_H "Growatt_ACchargePower_H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ACchargePower_H"] | Number:Energy Growatt_ACchargePower_H "ACchargePower_H [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ACchargePower_H"} | 29.,ACchargePower_H,Modbus RTU,,5,4,116,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 117 | ACchargePower_L | Grid power to local load |  |  | 0.1kwh |  |  | TL_X-TL_XH | 0.1 | kwh | 1 | Type number : ACchargePower_L "Growatt_ACchargePower_L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ACchargePower_L"] | Number:Energy Growatt_ACchargePower_L "ACchargePower_L [%0.1f kwh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ACchargePower_L"} | 29.,ACchargePower_L,Modbus RTU,,5,4,117,1,9410,4,0,Unsigned int,0,1,kwh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 118 | Priority |  |  | 0:Load First |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : Priority "Growatt_Priority" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Priority"] | Number Growatt_Priority "Priority" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Priority"} | 30.,Priority,Modbus RTU,,5,4,118,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 119 | BatteryType |  |  | 0:Lead-acid |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatteryType "Growatt_BatteryType" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatteryType"] | Number Growatt_BatteryType "BatteryType" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatteryType"} | 30.,BatteryType,Modbus RTU,,5,4,119,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 120 | AutoProofreadCMD | Aging mode Auto-calibration command | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : AutoProofreadCMD "Growatt_AutoProofreadCMD" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.AutoProofreadCMD"] | Number Growatt_AutoProofreadCMD "AutoProofreadCMD" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AutoProofreadCMD"} | 30.,AutoProofreadCMD,Modbus RTU,,5,4,120,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 124 | reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : reserved "Growatt_reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.reserved"] | Number Growatt_reserved "reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:reserved"} | 30.,reserved,Modbus RTU,,5,4,124,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 125 | PIDPV1_Voltage | PID PV1PE Volt/ Flyspan voltage |  | 0~1000V | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : PIDPV1_Voltage "Growatt_PIDPV1_Voltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV1_Voltage"] | Number:ElectricPotential Growatt_PIDPV1_Voltage "PIDPV1_Voltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDPV1_Voltage"} | 30.,PIDPV1_Voltage,Modbus RTU,,5,4,125,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 126 | PIDPV1_Current | PID PV1PE Curr |  | -10~10mA | 0.1mA |  |  | ALL | 0.1 | mA | 1 | Type number : PIDPV1_Current "Growatt_PIDPV1_Current" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV1_Current"] | #N/A | 30.,PIDPV1_Current,Modbus RTU,,5,4,126,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 127 | PIDPV2_Voltage | PID PV2PE Volt/ |  | 0~1000V | 0.1V |  |  | BDC | 0.1 | V | 1 | Type number : PIDPV2_Voltage "Growatt_PIDPV2_Voltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV2_Voltage"] | Number:ElectricPotential Growatt_PIDPV2_Voltage "PIDPV2_Voltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDPV2_Voltage"} | 30.,PIDPV2_Voltage,Modbus RTU,,5,4,127,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 128 | PIDPV2_Current | PID PV2PE Curr |  | -10~10mA | 0.1mA |  |  | BDC | 0.1 | mA | 1 | Type number : PIDPV2_Current "Growatt_PIDPV2_Current" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV2_Current"] | #N/A | 30.,PIDPV2_Current,Modbus RTU,,5,4,128,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 129 | PIDPV3_Voltage | PID PV3PE Volt/ |  | 0~1000V | 0.1V |  | Same as | USTimeSet | 0.1 | V | 1 | Type number : PIDPV3_Voltage "Growatt_PIDPV3_Voltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV3_Voltage"] | Number:ElectricPotential Growatt_PIDPV3_Voltage "PIDPV3_Voltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDPV3_Voltage"} | 30.,PIDPV3_Voltage,Modbus RTU,,5,4,129,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 130 | PIDPV3_Current | PID PV3PE Curr |  | -10~10mA | 0.1mA |  |  | USTimeSet | 0.1 | mA | 1 | Type number : PIDPV3_Current "Growatt_PIDPV3_Current" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV3_Current"] | #N/A | 30.,PIDPV3_Current,Modbus RTU,,5,4,130,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 131 | PIDPV4_Voltage | PID PV4PE Volt/ |  | 0~1000V | 0.1V |  | Same as | USTimeSet | 0.1 | V | 1 | Type number : PIDPV4_Voltage "Growatt_PIDPV4_Voltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV4_Voltage"] | Number:ElectricPotential Growatt_PIDPV4_Voltage "PIDPV4_Voltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDPV4_Voltage"} | 30.,PIDPV4_Voltage,Modbus RTU,,5,4,131,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 132 | PIDPV4_Current | PID PV4PE Curr |  | -10~10mA | 0.1mA |  | Same as | USTimeSet | 0.1 | mA | 1 | Type number : PIDPV4_Current "Growatt_PIDPV4_Current" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV4_Current"] | #N/A | 30.,PIDPV4_Current,Modbus RTU,,5,4,132,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 133 | PIDPV5_Voltage | PID PV5PE Volt/ |  | 0~1000V | 0.1V |  | Same as | USTimeSet | 0.1 | V | 1 | Type number : PIDPV5_Voltage "Growatt_PIDPV5_Voltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV5_Voltage"] | Number:ElectricPotential Growatt_PIDPV5_Voltage "PIDPV5_Voltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDPV5_Voltage"} | 30.,PIDPV5_Voltage,Modbus RTU,,5,4,133,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 134 | PIDPV5_Current | PID PV5PE Curr |  | -10~10mA | 0.1mA |  | Same as | USTimeSet | 0.1 | mA | 1 | Type number : PIDPV5_Current "Growatt_PIDPV5_Current" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV5_Current"] | #N/A | 30.,PIDPV5_Current,Modbus RTU,,5,4,134,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 135 | PIDPV6_Voltage | PID PV6PE Volt/ |  | 0~1000V | 0.1V |  | Same as | USTimeSet | 0.1 | V | 1 | Type number : PIDPV6_Voltage "Growatt_PIDPV6_Voltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV6_Voltage"] | Number:ElectricPotential Growatt_PIDPV6_Voltage "PIDPV6_Voltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDPV6_Voltage"} | 30.,PIDPV6_Voltage,Modbus RTU,,5,4,135,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 136 | PIDPV6_Current | PID PV6PE Curr |  | -10~10mA | 0.1mA |  | Same as | USTimeSet | 0.1 | mA | 1 | Type number : PIDPV6_Current "Growatt_PIDPV6_Current" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV6_Current"] | #N/A | 30.,PIDPV6_Current,Modbus RTU,,5,4,136,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 137 | PIDPV7_Voltage | PID PV7PE Volt/ |  | 0~1000V | 0.1V |  | Same as | USTimeSet | 0.1 | V | 1 | Type number : PIDPV7_Voltage "Growatt_PIDPV7_Voltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV7_Voltage"] | Number:ElectricPotential Growatt_PIDPV7_Voltage "PIDPV7_Voltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDPV7_Voltage"} | 30.,PIDPV7_Voltage,Modbus RTU,,5,4,137,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 138 | PIDPV7_Current | PID PV7PE Curr |  | -10~10mA | 0.1mA |  | Same as | USTimeSet | 0.1 | mA | 1 | Type number : PIDPV7_Current "Growatt_PIDPV7_Current" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV7_Current"] | #N/A | 30.,PIDPV7_Current,Modbus RTU,,5,4,138,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 139 | PIDPV8_Voltage | PID PV8PE Volt/ |  | 0~1000V | 0.1V |  | Same as | USTimeSet | 0.1 | V | 1 | Type number : PIDPV8_Voltage "Growatt_PIDPV8_Voltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV8_Voltage"] | Number:ElectricPotential Growatt_PIDPV8_Voltage "PIDPV8_Voltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDPV8_Voltage"} | 30.,PIDPV8_Voltage,Modbus RTU,,5,4,139,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 140 | PIDPV8_Current | PID PV8PE Curr |  | -10~10mA | 0.1mA |  | Same as | USTimeSet | 0.1 | mA | 1 | Type number : PIDPV8_Current "Growatt_PIDPV8_Current" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV8_Current"] | #N/A | 30.,PIDPV8_Current,Modbus RTU,,5,4,140,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 141 | PIDStatus | Bit0~7:PID Working Status |  | 0~3 |  |  | Same as | USTimeSet |  |  | 0 | Type number : PIDStatus "Growatt_PIDStatus" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDStatus"] | Number Growatt_PIDStatus "PIDStatus" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDStatus"} | 30.,PIDStatus,Modbus RTU,,5,4,141,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 142 | V_String1 | PV String1 voltage |  |  | 0.1V |  | ASCII | ALL | 0.1 | V | 1 | Type number : V_String1 "Growatt_V_String1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String1"] | Number:ElectricPotential Growatt_V_String1 "V_String1 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String1"} | 30.,V_String1,Modbus RTU,,5,4,142,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 143 | Curr_String1 | PV String1 current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String1 "Growatt_Curr_String1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String1"] | Number:ElectricCurrent Growatt_Curr_String1 "Curr_String1 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String1"} | 30.,Curr_String1,Modbus RTU,,5,4,143,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 144 | V_String2 | PV String2 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V_String2 "Growatt_V_String2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String2"] | Number:ElectricPotential Growatt_V_String2 "V_String2 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String2"} | 30.,V_String2,Modbus RTU,,5,4,144,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 145 | Curr_String2 | PV String2 current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String2 "Growatt_Curr_String2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String2"] | Number:ElectricCurrent Growatt_Curr_String2 "Curr_String2 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String2"} | 30.,Curr_String2,Modbus RTU,,5,4,145,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 146 | V_String3 | PV String3 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V_String3 "Growatt_V_String3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String3"] | Number:ElectricPotential Growatt_V_String3 "V_String3 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String3"} | 30.,V_String3,Modbus RTU,,5,4,146,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 147 | Curr_String3 | PV String3 current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String3 "Growatt_Curr_String3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String3"] | Number:ElectricCurrent Growatt_Curr_String3 "Curr_String3 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String3"} | 30.,Curr_String3,Modbus RTU,,5,4,147,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 148 | V_String4 | PV String4 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V_String4 "Growatt_V_String4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String4"] | Number:ElectricPotential Growatt_V_String4 "V_String4 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String4"} | 30.,V_String4,Modbus RTU,,5,4,148,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 149 | Curr_String4 | PV String4 current |  | -15~15A | 0.1A |  | Storage | SPA | 0.1 | A | 1 | Type number : Curr_String4 "Growatt_Curr_String4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String4"] | Number:ElectricCurrent Growatt_Curr_String4 "Curr_String4 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String4"} | 30.,Curr_String4,Modbus RTU,,5,4,149,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 150 | V_String5 | PV String5 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V_String5 "Growatt_V_String5" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String5"] | Number:ElectricPotential Growatt_V_String5 "V_String5 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String5"} | 30.,V_String5,Modbus RTU,,5,4,150,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 151 | Curr_String5 | PV String5 current |  | -15~15A | 0.1A |  | Storage | SPA | 0.1 | A | 1 | Type number : Curr_String5 "Growatt_Curr_String5" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String5"] | Number:ElectricCurrent Growatt_Curr_String5 "Curr_String5 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String5"} | 30.,Curr_String5,Modbus RTU,,5,4,151,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 152 | V_String6 | PV String6 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V_String6 "Growatt_V_String6" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String6"] | Number:ElectricPotential Growatt_V_String6 "V_String6 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String6"} | 30.,V_String6,Modbus RTU,,5,4,152,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 153 | Curr_String6 | PV String6 current |  | -15~15A | 0.1A |  | SPA used | SPA | 0.1 | A | 1 | Type number : Curr_String6 "Growatt_Curr_String6" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String6"] | Number:ElectricCurrent Growatt_Curr_String6 "Curr_String6 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String6"} | 30.,Curr_String6,Modbus RTU,,5,4,153,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 154 | V_String7 | PV String7 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V_String7 "Growatt_V_String7" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String7"] | Number:ElectricPotential Growatt_V_String7 "V_String7 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String7"} | 30.,V_String7,Modbus RTU,,5,4,154,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 155 | Curr_String7 | PV String7 current |  | -15~15A | 0.1A |  | Storage | SPA | 0.1 | A | 1 | Type number : Curr_String7 "Growatt_Curr_String7" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String7"] | Number:ElectricCurrent Growatt_Curr_String7 "Curr_String7 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String7"} | 30.,Curr_String7,Modbus RTU,,5,4,155,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 156 | V_String8 | PV String8 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V_String8 "Growatt_V_String8" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String8"] | Number:ElectricPotential Growatt_V_String8 "V_String8 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String8"} | 30.,V_String8,Modbus RTU,,5,4,156,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 157 | Curr_String8 | PV String8 current |  | -15A~15A | 0.1A |  | Storage | SPA | 0.1 | A | 1 | Type number : Curr_String8 "Growatt_Curr_String8" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String8"] | Number:ElectricCurrent Growatt_Curr_String8 "Curr_String8 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String8"} | 30.,Curr_String8,Modbus RTU,,5,4,157,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 158 | V_String9 | PV String9 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V_String9 "Growatt_V_String9" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String9"] | Number:ElectricPotential Growatt_V_String9 "V_String9 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String9"} | 30.,V_String9,Modbus RTU,,5,4,158,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 159 | Curr_String9 | PV String9 current |  | -15A~15A | 0.1A |  | Storage | SPA | 0.1 | A | 1 | Type number : Curr_String9 "Growatt_Curr_String9" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String9"] | Number:ElectricCurrent Growatt_Curr_String9 "Curr_String9 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String9"} | 30.,Curr_String9,Modbus RTU,,5,4,159,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 160 | V_String10 | PV String10 voltage |  |  | 0.1V |  | ASCII | ALL | 0.1 | V | 1 | Type number : V_String10 "Growatt_V_String10" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String10"] | Number:ElectricPotential Growatt_V_String10 "V_String10 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String10"} | 30.,V_String10,Modbus RTU,,5,4,160,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 161 | Curr_String10 | PV String10 current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String10 "Growatt_Curr_String10" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String10"] | Number:ElectricCurrent Growatt_Curr_String10 "Curr_String10 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String10"} | 30.,Curr_String10,Modbus RTU,,5,4,161,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 162 | V_String11 | PV String11 voltage |  |  | 0.1V |  | 0:Independent | ALL | 0.1 | V | 1 | Type number : V_String11 "Growatt_V_String11" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String11"] | Number:ElectricPotential Growatt_V_String11 "V_String11 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String11"} | 30.,V_String11,Modbus RTU,,5,4,162,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 163 | Curr_String11 | PV String11 current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String11 "Growatt_Curr_String11" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String11"] | Number:ElectricCurrent Growatt_Curr_String11 "Curr_String11 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String11"} | 30.,Curr_String11,Modbus RTU,,5,4,163,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 164 | V_String12 | PV String12 voltage |  |  | 0.1V |  | ExportLimit PowerRate | ALL | 0.1 | V | 1 | Type number : V_String12 "Growatt_V_String12" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String12"] | Number:ElectricPotential Growatt_V_String12 "V_String12 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String12"} | 30.,V_String12,Modbus RTU,,5,4,164,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 165 | Curr_String12 | PV String12 current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String12 "Growatt_Curr_String12" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String12"] | Number:ElectricCurrent Growatt_Curr_String12 "Curr_String12 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String12"} | 30.,Curr_String12,Modbus RTU,,5,4,165,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 166 | V_String13 | PV String13 voltage |  |  | 0.1V |  | ExportLimit enable, | ALL | 0.1 | V | 1 | Type number : V_String13 "Growatt_V_String13" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String13"] | Number:ElectricPotential Growatt_V_String13 "V_String13 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String13"} | 30.,V_String13,Modbus RTU,,5,4,166,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 167 | Curr_String13 | PV String13 current |  | -15A~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String13 "Growatt_Curr_String13" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String13"] | Number:ElectricCurrent Growatt_Curr_String13 "Curr_String13 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String13"} | 30.,Curr_String13,Modbus RTU,,5,4,167,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 168 | V_String14 | PV String14 voltage |  |  | 0.1V |  | Mxxxx Power | ALL | 0.1 | V | 1 | Type number : V_String14 "Growatt_V_String14" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String14"] | Number:ElectricPotential Growatt_V_String14 "V_String14 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String14"} | 30.,V_String14,Modbus RTU,,5,4,168,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 169 | Curr_String14 | PV String14 current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String14 "Growatt_Curr_String14" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String14"] | Number:ElectricCurrent Growatt_Curr_String14 "Curr_String14 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String14"} | 30.,Curr_String14,Modbus RTU,,5,4,169,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 170 | V_String15 | PV String15 voltage |  |  | 0.1V |  | PxxUxx | ALL | 0.1 | V | 1 | Type number : V_String15 "Growatt_V_String15" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String15"] | Number:ElectricPotential Growatt_V_String15 "V_String15 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String15"} | 30.,V_String15,Modbus RTU,,5,4,170,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 171 | Curr_String15 | PV String15 current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String15 "Growatt_Curr_String15" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String15"] | Number:ElectricCurrent Growatt_Curr_String15 "Curr_String15 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String15"} | 30.,Curr_String15,Modbus RTU,,5,4,171,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 172 | V_String16 | PV String16 voltage |  |  | 0.1V |  | DxxTxx | ALL | 0.1 | V | 1 | Type number : V_String16 "Growatt_V_String16" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String16"] | Number:ElectricPotential Growatt_V_String16 "V_String16 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String16"} | 30.,V_String16,Modbus RTU,,5,4,172,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 173 | Curr_String16 | PV String16 current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String16 "Growatt_Curr_String16" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String16"] | Number:ElectricCurrent Growatt_Curr_String16 "Curr_String16 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String16"} | 30.,Curr_String16,Modbus RTU,,5,4,173,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 174 | StrUnmatch | Bit0~15: String1~16 unmatch |  |  |  |  | SPH4-11K used | Storage |  |  | 0 | Type number : StrUnmatch "Growatt_StrUnmatch" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.StrUnmatch"] | Number Growatt_StrUnmatch "StrUnmatch" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:StrUnmatch"} | 30.,StrUnmatch,Modbus RTU,,5,4,174,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 175 | StrCurrentUnblance | Bit0~15: String1~16 current unblance | [5 empty] | Storage |  |  | 0 | Type number : StrCurrentUnblance "Growatt_StrCurrentUnblance" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.StrCurrentUnblance"] | Number Growatt_StrCurrentUnblance "StrCurrentUnblance" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:StrCurrentUnblance"} | 30.,StrCurrentUnblance,Modbus RTU,,5,4,175,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 176 | StrDisconnect | Bit0~15: String1~16 disconnect | [5 empty] | Storage |  |  | 0 | Type number : StrDisconnect "Growatt_StrDisconnect" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.StrDisconnect"] | Number Growatt_StrDisconnect "StrDisconnect" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:StrDisconnect"} | 30.,StrDisconnect,Modbus RTU,,5,4,176,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 177 | PIDFaultCode | Bit0:Output over voltage | [5 empty] | ALL |  |  | 0 | Type number : PIDFaultCode "Growatt_PIDFaultCode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDFaultCode"] | Number Growatt_PIDFaultCode "PIDFaultCode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDFaultCode"} | 30.,PIDFaultCode,Modbus RTU,,5,4,177,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 178 | StringPrompt | String Prompt |  |  |  |  | 0:disable 1:enable | Storage |  |  | 0 | Type number : StringPrompt "Growatt_StringPrompt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.StringPrompt"] | Number Growatt_StringPrompt "StringPrompt" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:StringPrompt"} | 30.,StringPrompt,Modbus RTU,,5,4,178,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 179 | PVWarningValue | PV Warning Value |  |  |  |  | Battery temperature upper limit | TL_X-TL_XH |  |  | 0 | Type number : PVWarningValue "Growatt_PVWarningValue" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PVWarningValue"] | Number Growatt_PVWarningValue "PVWarningValue" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PVWarningValue"} | 30.,PVWarningValue,Modbus RTU,,5,4,179,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 180 | DSP075Value | DSP075 Warning Value |  |  |  |  | 0 : Old energy | BMS |  |  | 0 | Type number : DSP075Value "Growatt_DSP075Value" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP075Value"] | Number Growatt_DSP075Value "DSP075Value" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP075Value"} | 30.,DSP075Value,Modbus RTU,,5,4,180,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 181 | DSP075Value | DSP075 Fault Value | [5 empty] | BMS |  |  | 0 | Type number : DSP075Value "Growatt_DSP075Value" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP075Value"] | Number Growatt_DSP075Value "DSP075Value" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP075Value"} | 30.,DSP075Value,Modbus RTU,,5,4,181,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 182 | DSP067Data1 | DSP067 Debug Data1 |  |  |  |  | SPA | SPA |  |  | 0 | Type number : DSP067Data1 "Growatt_DSP067Data1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data1"] | Number Growatt_DSP067Data1 "DSP067Data1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data1"} | 30.,DSP067Data1,Modbus RTU,,5,4,182,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 183 | DSP067Data2 | DSP067 Debug Data2 |  |  |  |  | SPA | SPA |  |  | 0 | Type number : DSP067Data2 "Growatt_DSP067Data2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data2"] | Number Growatt_DSP067Data2 "DSP067Data2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data2"} | 30.,DSP067Data2,Modbus RTU,,5,4,183,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 184 | DSP067Data3 | DSP067 Debug Data3 | [5 empty] | BMS |  |  | 0 | Type number : DSP067Data3 "Growatt_DSP067Data3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data3"] | Number Growatt_DSP067Data3 "DSP067Data3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data3"} | 30.,DSP067Data3,Modbus RTU,,5,4,184,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 185 | DSP067Data4 | DSP067 Debug Data4 | [5 empty] | BMS |  |  | 0 | Type number : DSP067Data4 "Growatt_DSP067Data4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data4"] | Number Growatt_DSP067Data4 "DSP067Data4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data4"} | 30.,DSP067Data4,Modbus RTU,,5,4,185,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 186 | DSP067Data5 | DSP067 Debug Data5 | [5 empty] | BMS |  |  | 0 | Type number : DSP067Data5 "Growatt_DSP067Data5" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data5"] | Number Growatt_DSP067Data5 "DSP067Data5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data5"} | 30.,DSP067Data5,Modbus RTU,,5,4,186,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 187 | DSP067Data6 | DSP067 Debug Data6 | [5 empty] | BMS |  |  | 0 | Type number : DSP067Data6 "Growatt_DSP067Data6" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data6"] | Number Growatt_DSP067Data6 "DSP067Data6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data6"} | 30.,DSP067Data6,Modbus RTU,,5,4,187,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 188 | DSP067Data7 | DSP067 Debug Data7 | [5 empty] | BMS |  |  | 0 | Type number : DSP067Data7 "Growatt_DSP067Data7" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data7"] | Number Growatt_DSP067Data7 "DSP067Data7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data7"} | 30.,DSP067Data7,Modbus RTU,,5,4,188,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 189 | DSP067Data8 | DSP067 Debug Data8 | [5 empty] | BMS |  |  | 0 | Type number : DSP067Data8 "Growatt_DSP067Data8" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data8"] | Number Growatt_DSP067Data8 "DSP067Data8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data8"} | 30.,DSP067Data8,Modbus RTU,,5,4,189,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 190 | DSP075Data1 | DSP075 Debug Data1 | [5 empty] | BMS |  |  | 0 | Type number : DSP075Data1 "Growatt_DSP075Data1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP075Data1"] | Number Growatt_DSP075Data1 "DSP075Data1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP075Data1"} | 30.,DSP075Data1,Modbus RTU,,5,4,190,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 191 | DSP075Data2 | DSP075 Debug Data2 | [5 empty] | BMS |  |  | 0 | Type number : DSP075Data2 "Growatt_DSP075Data2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP075Data2"] | Number Growatt_DSP075Data2 "DSP075Data2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP075Data2"} | 30.,DSP075Data2,Modbus RTU,,5,4,191,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 192 | DSP075Data3 | DSP075 Debug Data3 | [5 empty] | BMS |  |  | 0 | Type number : DSP075Data3 "Growatt_DSP075Data3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP075Data3"] | Number Growatt_DSP075Data3 "DSP075Data3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP075Data3"} | 30.,DSP075Data3,Modbus RTU,,5,4,192,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 193 | DSP075Data4 | DSP075 Debug Data4 | [5 empty] | BMS |  |  | 0 | Type number : DSP075Data4 "Growatt_DSP075Data4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP075Data4"] | Number Growatt_DSP075Data4 "DSP075Data4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP075Data4"} | 30.,DSP075Data4,Modbus RTU,,5,4,193,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 194 | DSP075Data55 | DSP075 Debug Data5 | [5 empty] | BMS |  |  | 0 | Type number : DSP075Data55 "Growatt_DSP075Data55" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP075Data55"] | Number Growatt_DSP075Data55 "DSP075Data55" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP075Data55"} | 30.,DSP075Data55,Modbus RTU,,5,4,194,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 195 | DSP075Data6 | DSP075 Debug Data6 | [5 empty] | BMS |  |  | 0 | Type number : DSP075Data6 "Growatt_DSP075Data6" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP075Data6"] | Number Growatt_DSP075Data6 "DSP075Data6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP075Data6"} | 30.,DSP075Data6,Modbus RTU,,5,4,195,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 196 | DSP075Data7 | DSP075 Debug Data7 | [5 empty] | BMS |  |  | 0 | Type number : DSP075Data7 "Growatt_DSP075Data7" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP075Data7"] | Number Growatt_DSP075Data7 "DSP075Data7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP075Data7"} | 30.,DSP075Data7,Modbus RTU,,5,4,196,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 197 | DSP075Data8 | DSP075 Debug Data8 | [5 empty] | BMS |  |  | 0 | Type number : DSP075Data8 "Growatt_DSP075Data8" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP075Data8"] | Number Growatt_DSP075Data8 "DSP075Data8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP075Data8"} | 30.,DSP075Data8,Modbus RTU,,5,4,197,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 198 | bUSBAgingTestOk | USBAgingTestOkFlag |  | 0-1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bUSBAgingTestOk "Growatt_bUSBAgingTestOk" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.bUSBAgingTestOk"] | Number Growatt_bUSBAgingTestOk "bUSBAgingTestOk" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bUSBAgingTestOk"} | 30.,bUSBAgingTestOk,Modbus RTU,,5,4,198,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 199 | bFlashEraseAging | FlashEraseAgingOkFlag |  | 0-1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bFlashEraseAging "Growatt_bFlashEraseAging" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.bFlashEraseAging"] | Number Growatt_bFlashEraseAging "bFlashEraseAging" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bFlashEraseAging"} | 30.,bFlashEraseAging,Modbus RTU,,5,4,199,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 200 | PVISO | PVISOValue |  |  | K? |  | Bit0~7: minutes; | TL_X-TL_XH |  | K? | 0 | Type number : PVISO "Growatt_PVISO" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PVISO"] | #N/A | 30.,PVISO,Modbus RTU,,5,4,200,1,9410,2,0,Unsigned int,0,0,K?,1,100,97,0,0,0,1.000000,0,255
| 4 | 201 | R_DCI | R DCI Curr |  |  | 0.1mA |  | Lead acid battery | TL_X-TL_XH | 0.1 | mA | 1 | Type number : R_DCI "Growatt_R_DCI" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.R_DCI"] | #N/A | 30.,R_DCI,Modbus RTU,,5,4,201,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 202 | S_DCI | S DCI Curr |  |  | 0.1mA |  |  | Storage | 0.1 | mA | 1 | Type number : S_DCI "Growatt_S_DCI" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.S_DCI"] | #N/A | 30.,S_DCI,Modbus RTU,,5,4,202,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 203 | T_DCI | T DCI Curr |  |  | 0.1mA |  | 0%~100.0%,US latest safety regulations | ALL | 0.1 | mA | 1 | Type number : T_DCI "Growatt_T_DCI" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.T_DCI"] | #N/A | 30.,T_DCI,Modbus RTU,,5,4,203,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 204 | PID_Bus | PIDBusVolt |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : PID_Bus "Growatt_PID_Bus" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PID_Bus"] | Number:ElectricPotential Growatt_PID_Bus "PID_Bus [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PID_Bus"} | 30.,PID_Bus,Modbus RTU,,5,4,204,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 205 | GFCI | GFCI Curr |  |  | mA |  |  | PV9_32 |  | mA | 0 | Type number : GFCI "Growatt_GFCI" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.GFCI"] | #N/A | 30.,GFCI,Modbus RTU,,5,4,205,1,9410,2,0,Unsigned int,0,0,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 206 | SVG_APF | SVG/APF Status+SVGAPFEqualRatio |  | High 8 bit: |  |  | Lower temperature limit | Storage |  |  | 0 | Type number : SVG_APF "Growatt_SVG_APF" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.SVG_APF"] | Number Growatt_SVG_APF "SVG_APF" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SVG_APF"} | 30.,SVG_APF,Modbus RTU,,5,4,206,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 207 | CT_I_R | R phase load side current for SVG |  |  | 0.1A |  | Three phase grid output current | TL_X-TL_XH | 0.1 | A | 1 | Type number : CT_I_R "Growatt_CT_I_R" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CT_I_R"] | Number:ElectricCurrent Growatt_CT_I_R "CT_I_R [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CT_I_R"} | 30.,CT_I_R,Modbus RTU,,5,4,207,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 208 | CT_I_S | S phase load side current for SVG |  |  | 0.1A |  | Three phase grid voltage | TL_X-TL_XH | 0.1 | A | 1 | Type number : CT_I_S "Growatt_CT_I_S" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CT_I_S"] | Number:ElectricCurrent Growatt_CT_I_S "CT_I_S [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CT_I_S"} | 30.,CT_I_S,Modbus RTU,,5,4,208,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 209 | CT_I_T | T phase load side current for SVG |  |  | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : CT_I_T "Growatt_CT_I_T" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CT_I_T"] | Number:ElectricCurrent Growatt_CT_I_T "CT_I_T [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CT_I_T"} | 30.,CT_I_T,Modbus RTU,,5,4,209,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 210 | CT_Q_RH | R phase load side output power for SVG(High) |  |  | 0.1W |  | Three phase grid output power | TL_X-TL_XH | 0.1 | W | 1 | Type number : CT_Q_RH "Growatt_CT_Q_RH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CT_Q_RH"] | Number:Power Growatt_CT_Q_RH "CT_Q_RH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CT_Q_RH"} | 30.,CT_Q_RH,Modbus RTU,,5,4,210,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 211 | CT_Q_RL | R phase load side output power for SVG(low) |  |  | 0.1W |  | Three phase grid output current | TL_X-TL_XH | 0.1 | W | 1 | Type number : CT_Q_RL "Growatt_CT_Q_RL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CT_Q_RL"] | Number:Power Growatt_CT_Q_RL "CT_Q_RL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CT_Q_RL"} | 30.,CT_Q_RL,Modbus RTU,,5,4,211,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 212 | CT_Q_SH | S phase load side output power for SVG(High) reactive |  |  | 0.1W |  | Three phase grid voltage | TL_X-TL_XH | 0.1 | W | 1 | Type number : CT_Q_SH "Growatt_CT_Q_SH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CT_Q_SH"] | Number:Power Growatt_CT_Q_SH "CT_Q_SH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CT_Q_SH"} | 30.,CT_Q_SH,Modbus RTU,,5,4,212,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 213 | CT_Q_SL | S phase load side output power for SVG(low) reactive |  |  | 0.1W |  | VA | TL_X-TL_XH | 0.1 | W | 1 | Type number : CT_Q_SL "Growatt_CT_Q_SL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CT_Q_SL"] | Number:Power Growatt_CT_Q_SL "CT_Q_SL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CT_Q_SL"} | 30.,CT_Q_SL,Modbus RTU,,5,4,213,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 214 | CT_Q_TH | T phase load side output power for SVG(High) |  |  | 0.1W |  | Three/single phase grid output watt | TL_X-TL_XH | 0.1 | W | 1 | Type number : CT_Q_TH "Growatt_CT_Q_TH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CT_Q_TH"] | Number:Power Growatt_CT_Q_TH "CT_Q_TH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CT_Q_TH"} | 30.,CT_Q_TH,Modbus RTU,,5,4,214,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 215 | CT_Q_TL | T phase load side output power for SVG(low) |  |  | 0.1W |  | Three/single | TL_X-TL_XH | 0.1 | W | 1 | Type number : CT_Q_TL "Growatt_CT_Q_TL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CT_Q_TL"] | Number:Power Growatt_CT_Q_TL "CT_Q_TL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CT_Q_TL"} | 30.,CT_Q_TL,Modbus RTU,,5,4,215,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 216 | CTHAR_I_R | R phase load side harmonic |  |  | 0.1A |  | Grid frequency | TL_X-TL_XH | 0.1 | A | 1 | Type number : CTHAR_I_R "Growatt_CTHAR_I_R" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CTHAR_I_R"] | Number:ElectricCurrent Growatt_CTHAR_I_R "CTHAR_I_R [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CTHAR_I_R"} | 30.,CTHAR_I_R,Modbus RTU,,5,4,216,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 217 | CTHAR_I_S | S phase load side harmonic |  |  | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : CTHAR_I_S "Growatt_CTHAR_I_S" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CTHAR_I_S"] | Number:ElectricCurrent Growatt_CTHAR_I_S "CTHAR_I_S [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CTHAR_I_S"} | 30.,CTHAR_I_S,Modbus RTU,,5,4,217,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 218 | CTHAR_I_T | T phase load side harmonic |  |  | 0.1A |  | Output power | TL_X-TL_XH | 0.1 | A | 1 | Type number : CTHAR_I_T "Growatt_CTHAR_I_T" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.CTHAR_I_T"] | Number:ElectricCurrent Growatt_CTHAR_I_T "CTHAR_I_T [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CTHAR_I_T"} | 30.,CTHAR_I_T,Modbus RTU,,5,4,218,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 219 | COMP_Q_RH | R phase compensate reactive power for SVG(High) |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : COMP_Q_RH "Growatt_COMP_Q_RH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.COMP_Q_RH"] | Number:Power Growatt_COMP_Q_RH "COMP_Q_RH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:COMP_Q_RH"} | 30.,COMP_Q_RH,Modbus RTU,,5,4,219,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 220 | COMP_Q_RL | R phase compensate reactive power for SVG(low) |  |  | 0.1W |  | Total generate | TL_X-TL_XH | 0.1 | W | 1 | Type number : COMP_Q_RL "Growatt_COMP_Q_RL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.COMP_Q_RL"] | Number:Power Growatt_COMP_Q_RL "COMP_Q_RL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:COMP_Q_RL"} | 30.,COMP_Q_RL,Modbus RTU,,5,4,220,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 221 | COMP_Q_SH | S phase compensate reactive power for SVG(High) |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : COMP_Q_SH "Growatt_COMP_Q_SH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.COMP_Q_SH"] | Number:Power Growatt_COMP_Q_SH "COMP_Q_SH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:COMP_Q_SH"} | 30.,COMP_Q_SH,Modbus RTU,,5,4,221,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 222 | COMP_Q_SL | S phase compensate reactive power |  |  | 0.1W |  | Today generate energy | TL_X-TL_XH | 0.1 | W | 1 | Type number : COMP_Q_SL "Growatt_COMP_Q_SL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.COMP_Q_SL"] | Number:Power Growatt_COMP_Q_SL "COMP_Q_SL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:COMP_Q_SL"} | 30.,COMP_Q_SL,Modbus RTU,,5,4,222,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 223 | COMP_Q_TH | T phase compensate reactive power for SVG(High) |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : COMP_Q_TH "Growatt_COMP_Q_TH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.COMP_Q_TH"] | Number:Power Growatt_COMP_Q_TH "COMP_Q_TH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:COMP_Q_TH"} | 30.,COMP_Q_TH,Modbus RTU,,5,4,223,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 224 | COMP_Q_TL | T phase compensate reactive power for SVG(low) |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : COMP_Q_TL "Growatt_COMP_Q_TL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.COMP_Q_TL"] | Number:Power Growatt_COMP_Q_TL "COMP_Q_TL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:COMP_Q_TL"} | 30.,COMP_Q_TL,Modbus RTU,,5,4,224,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 225 | COMPHAR_I_R | R phase compensate harmonic for |  |  | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : COMPHAR_I_R "Growatt_COMPHAR_I_R" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.COMPHAR_I_R"] | Number:ElectricCurrent Growatt_COMPHAR_I_R "COMPHAR_I_R [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:COMPHAR_I_R"} | 30.,COMPHAR_I_R,Modbus RTU,,5,4,225,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 226 | COMPHAR_I_S | S phase compensate harmonic for |  |  | 0.1A |  | Total load power | TL_X-TL_XH | 0.1 | A | 1 | Type number : COMPHAR_I_S "Growatt_COMPHAR_I_S" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.COMPHAR_I_S"] | Number:ElectricCurrent Growatt_COMPHAR_I_S "COMPHAR_I_S [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:COMPHAR_I_S"} | 30.,COMPHAR_I_S,Modbus RTU,,5,4,226,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 227 | COMPHAR_I_T | T phase compensate harmonic for |  |  | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : COMPHAR_I_T "Growatt_COMPHAR_I_T" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.COMPHAR_I_T"] | Number:ElectricCurrent Growatt_COMPHAR_I_T "COMPHAR_I_T [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:COMPHAR_I_T"} | 30.,COMPHAR_I_T,Modbus RTU,,5,4,227,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 228 | bRS232AgingTest | RS232AgingTestOkFlag |  | 0-1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bRS232AgingTest "Growatt_bRS232AgingTest" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.bRS232AgingTest"] | Number Growatt_bRS232AgingTest "bRS232AgingTest" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bRS232AgingTest"} | 30.,bRS232AgingTest,Modbus RTU,,5,4,228,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 229 | bFanFaultBit | Bit0: Fan 1 fault bit | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : bFanFaultBit "Growatt_bFanFaultBit" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.bFanFaultBit"] | Number Growatt_bFanFaultBit "bFanFaultBit" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bFanFaultBit"} | 30.,bFanFaultBit,Modbus RTU,,5,4,229,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 230 | SacH | Output apparent power H |  |  | 0.1W |  |  | Storage | 0.1 | W | 1 | Type number : SacH "Growatt_SacH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.SacH"] | Number:Power Growatt_SacH "SacH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SacH"} | 30.,SacH,Modbus RTU,,5,4,230,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 231 | SacL | Output apparent power L |  |  | 0.1W |  | Bat First | Storage | 0.1 | W | 1 | Type number : SacL "Growatt_SacL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.SacL"] | Number:Power Growatt_SacL "SacL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SacL"} | 30.,SacL,Modbus RTU,,5,4,231,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 232 | ReActPowerH | Real Output Reactive Power H |  | Int32 | 0.1W |  | The power rate of drycontact turn on | TL_X-TL_XH | 0.1 | W | 1 | Type number : ReActPowerH "Growatt_ReActPowerH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ReActPowerH"] | Number:Power Growatt_ReActPowerH "ReActPowerH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ReActPowerH"} | 30.,ReActPowerH,Modbus RTU,,5,4,232,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 233 | ReActPowerL | Real Output Reactive Power L |  |  |  |  | DryContact function enable | TL_X-TL_XH |  |  | 0 | Type number : ReActPowerL "Growatt_ReActPowerL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ReActPowerL"] | Number Growatt_ReActPowerL "ReActPowerL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ReActPowerL"} | 30.,ReActPowerL,Modbus RTU,,5,4,233,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 234 | ReActPowerMaxH | Nominal Output Reactive Power H |  |  | 0.1W |  | ASCII | TL_X-TL_XH | 0.1 | W | 1 | Type number : ReActPowerMaxH "Growatt_ReActPowerMaxH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ReActPowerMaxH"] | Number:Power Growatt_ReActPowerMaxH "ReActPowerMaxH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ReActPowerMaxH"} | 30.,ReActPowerMaxH,Modbus RTU,,5,4,234,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 235 | ReActPowerMaxL | Nominal Output Reactive Power L |  |  |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : ReActPowerMaxL "Growatt_ReActPowerMaxL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ReActPowerMaxL"] | Number Growatt_ReActPowerMaxL "ReActPowerMaxL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ReActPowerMaxL"} | 30.,ReActPowerMaxL,Modbus RTU,,5,4,235,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 236 | ReActPower_TotalH | Reactive power generation |  |  | 0.1kwh |  | Dry contact closure power pe rcentage | TL_X-TL_XH | 0.1 | kwh | 1 | Type number : ReActPower_TotalH "Growatt_ReActPower_TotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ReActPower_TotalH"] | Number:Energy Growatt_ReActPower_TotalH "ReActPower_TotalH [%0.1f kwh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ReActPower_TotalH"} | 30.,ReActPower_TotalH,Modbus RTU,,5,4,236,1,9410,4,0,Unsigned int,0,1,kwh,1,100,97,0,0,0,1.000000,0,255
| 4 | 237 | ReActPower_TotalL | Reactive power generation |  |  |  |  | MIN2.5~6KTL-XH/ XA Double CT | TL_X-TL_XH |  |  | 0 | Type number : ReActPower_TotalL "Growatt_ReActPower_TotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ReActPower_TotalL"] | Number Growatt_ReActPower_TotalL "ReActPower_TotalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ReActPower_TotalL"} | 30.,ReActPower_TotalL,Modbus RTU,,5,4,237,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 238 | bAfciStatus |  |  | 0:Waiting |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bAfciStatus "Growatt_bAfciStatus" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.bAfciStatus"] | Number Growatt_bAfciStatus "bAfciStatus" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bAfciStatus"} | 30.,bAfciStatus,Modbus RTU,,5,4,238,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 239 | uwPresentFFTValue_CHANNEL_A | PresentFFTValue [CHANNEL_A] |  |  |  |  | UL | ALL |  |  | 0 | Type number : uwPresentFFTValue_CHANNEL_A "Growatt_uwPresentFFTValue_CHANNEL_A" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwPresentFFTValue_CHANNEL_A"] | Number Growatt_uwPresentFFTValue_CHANNEL_A "uwPresentFFTValue_CHANNEL_A" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwPresentFFTValue_CHANNEL_A"} | 30.,uwPresentFFTValue_CHANNEL_A,Modbus RTU,,5,4,239,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 240 | uwPresentFFTValue_CHANNEL_B | PresentFFTValue [CHANNEL_B] |  |  |  |  | CEI | ALL |  |  | 0 | Type number : uwPresentFFTValue_CHANNEL_B "Growatt_uwPresentFFTValue_CHANNEL_B" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwPresentFFTValue_CHANNEL_B"] | Number Growatt_uwPresentFFTValue_CHANNEL_B "uwPresentFFTValue_CHANNEL_B" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwPresentFFTValue_CHANNEL_B"} | 30.,uwPresentFFTValue_CHANNEL_B,Modbus RTU,,5,4,240,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 241 | DSP067Data1 | DSP067 Debug Data1 |  |  |  |  | SPA | SPA |  |  | 0 | Type number : DSP067Data1 "Growatt_DSP067Data1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data1"] | Number Growatt_DSP067Data1 "DSP067Data1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data1"} | 30.,DSP067Data1,Modbus RTU,,5,4,241,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 242 | DSP067Data2 | DSP067 Debug Data2 |  |  |  |  | SPA | SPA |  |  | 0 | Type number : DSP067Data2 "Growatt_DSP067Data2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data2"] | Number Growatt_DSP067Data2 "DSP067Data2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data2"} | 30.,DSP067Data2,Modbus RTU,,5,4,242,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 243 | DSP067Data3 | DSP067 Debug Data3 |  |  |  |  | SPA | SPA |  |  | 0 | Type number : DSP067Data3 "Growatt_DSP067Data3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data3"] | Number Growatt_DSP067Data3 "DSP067Data3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data3"} | 30.,DSP067Data3,Modbus RTU,,5,4,243,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 244 | DSP067Data4 | DSP067 Debug Data4 | [5 empty] | BMS |  |  | 0 | Type number : DSP067Data4 "Growatt_DSP067Data4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data4"] | Number Growatt_DSP067Data4 "DSP067Data4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data4"} | 30.,DSP067Data4,Modbus RTU,,5,4,244,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 245 | DSP067Data5 | DSP067 Debug Data5 | [5 empty] | BMS |  |  | 0 | Type number : DSP067Data5 "Growatt_DSP067Data5" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data5"] | Number Growatt_DSP067Data5 "DSP067Data5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data5"} | 30.,DSP067Data5,Modbus RTU,,5,4,245,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 246 | DSP067Data6 | DSP067 Debug Data6 | [5 empty] | BMS |  |  | 0 | Type number : DSP067Data6 "Growatt_DSP067Data6" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data6"] | Number Growatt_DSP067Data6 "DSP067Data6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data6"} | 30.,DSP067Data6,Modbus RTU,,5,4,246,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 247 | DSP067Data7 | DSP067 Debug Data7 | [5 empty] | BMS |  |  | 0 | Type number : DSP067Data7 "Growatt_DSP067Data7" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data7"] | Number Growatt_DSP067Data7 "DSP067Data7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data7"} | 30.,DSP067Data7,Modbus RTU,,5,4,247,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 248 | DSP067Data8 | DSP067 Debug Data8 | [5 empty] | BMS |  |  | 0 | Type number : DSP067Data8 "Growatt_DSP067Data8" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DSP067Data8"] | Number Growatt_DSP067Data8 "DSP067Data8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DSP067Data8"} | 30.,DSP067Data8,Modbus RTU,,5,4,248,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 875 | Vpv9 | PV9 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv9 "Growatt_Vpv9" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv9"] | Number:ElectricPotential Growatt_Vpv9 "Vpv9 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv9"} | 30.,Vpv9,Modbus RTU,,5,4,875,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 876 | PV9Curr | PV9 Input current |  |  | 0.1A |  | Bit0~7: minutes; | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV9Curr "Growatt_PV9Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV9Curr"] | Number:ElectricCurrent Growatt_PV9Curr "PV9Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV9Curr"} | 30.,PV9Curr,Modbus RTU,,5,4,876,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 877 | Ppv9H | PV9 input power (High) |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv9H "Growatt_Ppv9H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv9H"] | Number:Power Growatt_Ppv9H "Ppv9H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv9H"} | 30.,Ppv9H,Modbus RTU,,5,4,877,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 878 | Ppv9L | PV9 input power (Low) |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : Ppv9L "Growatt_Ppv9L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv9L"] | Number:Power Growatt_Ppv9L "Ppv9L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv9L"} | 30.,Ppv9L,Modbus RTU,,5,4,878,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 879 | Vpv10 | PV10 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv10 "Growatt_Vpv10" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv10"] | Number:ElectricPotential Growatt_Vpv10 "Vpv10 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv10"} | 30.,Vpv10,Modbus RTU,,5,4,879,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 880 | PV10Curr | PV10 Input current |  |  | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV10Curr "Growatt_PV10Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV10Curr"] | Number:ElectricCurrent Growatt_PV10Curr "PV10Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV10Curr"} | 30.,PV10Curr,Modbus RTU,,5,4,880,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 881 | Ppv10H | PV10 input power (High) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv10H "Growatt_Ppv10H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv10H"] | Number:Power Growatt_Ppv10H "Ppv10H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv10H"} | 30.,Ppv10H,Modbus RTU,,5,4,881,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 882 | Ppv10L | PV10 input power (Low) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv10L "Growatt_Ppv10L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv10L"] | Number:Power Growatt_Ppv10L "Ppv10L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv10L"} | 30.,Ppv10L,Modbus RTU,,5,4,882,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 883 | Vpv11 | PV11 voltage |  |  | 0.1V |  | ASCII | ALL | 0.1 | V | 1 | Type number : Vpv11 "Growatt_Vpv11" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv11"] | Number:ElectricPotential Growatt_Vpv11 "Vpv11 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv11"} | 30.,Vpv11,Modbus RTU,,5,4,883,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 884 | PV11Curr | PV11 Input current |  |  | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV11Curr "Growatt_PV11Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV11Curr"] | Number:ElectricCurrent Growatt_PV11Curr "PV11Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV11Curr"} | 30.,PV11Curr,Modbus RTU,,5,4,884,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 885 | Ppv11H | PV11 input power (High) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv11H "Growatt_Ppv11H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv11H"] | Number:Power Growatt_Ppv11H "Ppv11H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv11H"} | 30.,Ppv11H,Modbus RTU,,5,4,885,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 886 | Ppv11L | PV11 input power (Low) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv11L "Growatt_Ppv11L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv11L"] | Number:Power Growatt_Ppv11L "Ppv11L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv11L"} | 30.,Ppv11L,Modbus RTU,,5,4,886,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 887 | Vpv12 | PV12 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv12 "Growatt_Vpv12" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv12"] | Number:ElectricPotential Growatt_Vpv12 "Vpv12 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv12"} | 30.,Vpv12,Modbus RTU,,5,4,887,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 888 | PV12Curr | PV12 Input current |  |  | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV12Curr "Growatt_PV12Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV12Curr"] | Number:ElectricCurrent Growatt_PV12Curr "PV12Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV12Curr"} | 30.,PV12Curr,Modbus RTU,,5,4,888,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 889 | Ppv12H | PV12 input power (High) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv12H "Growatt_Ppv12H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv12H"] | Number:Power Growatt_Ppv12H "Ppv12H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv12H"} | 30.,Ppv12H,Modbus RTU,,5,4,889,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 890 | Ppv12L | PV12 input power (Low) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv12L "Growatt_Ppv12L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv12L"] | Number:Power Growatt_Ppv12L "Ppv12L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv12L"} | 30.,Ppv12L,Modbus RTU,,5,4,890,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 891 | Vpv13 | PV13 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv13 "Growatt_Vpv13" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv13"] | Number:ElectricPotential Growatt_Vpv13 "Vpv13 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv13"} | 30.,Vpv13,Modbus RTU,,5,4,891,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 892 | PV13Curr | PV13 Input current |  |  | 0.1A |  | BatMdlSeria/Paral | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV13Curr "Growatt_PV13Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV13Curr"] | Number:ElectricCurrent Growatt_PV13Curr "PV13Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV13Curr"} | 30.,PV13Curr,Modbus RTU,,5,4,892,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 893 | Ppv13H | PV13 input power (High) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv13H "Growatt_Ppv13H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv13H"] | Number:Power Growatt_Ppv13H "Ppv13H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv13H"} | 30.,Ppv13H,Modbus RTU,,5,4,893,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 894 | Ppv13L | PV13 input power (Low) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv13L "Growatt_Ppv13L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv13L"] | Number:Power Growatt_Ppv13L "Ppv13L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv13L"} | 30.,Ppv13L,Modbus RTU,,5,4,894,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 895 | Vpv14 | PV14 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv14 "Growatt_Vpv14" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv14"] | Number:ElectricPotential Growatt_Vpv14 "Vpv14 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv14"} | 30.,Vpv14,Modbus RTU,,5,4,895,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 896 | PV14Curr | PV14 Input current |  |  | 0.1A |  | Battery type | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV14Curr "Growatt_PV14Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV14Curr"] | Number:ElectricCurrent Growatt_PV14Curr "PV14Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV14Curr"} | 30.,PV14Curr,Modbus RTU,,5,4,896,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 897 | Ppv14H | PV14 input power (High) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv14H "Growatt_Ppv14H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv14H"] | Number:Power Growatt_Ppv14H "Ppv14H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv14H"} | 30.,Ppv14H,Modbus RTU,,5,4,897,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 898 | Ppv14L | PV14 input power (Low) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv14L "Growatt_Ppv14L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv14L"] | Number:Power Growatt_Ppv14L "Ppv14L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv14L"} | 30.,Ppv14L,Modbus RTU,,5,4,898,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 899 | Vpv15 | PV15 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv15 "Growatt_Vpv15" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv15"] | Number:ElectricPotential Growatt_Vpv15 "Vpv15 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv15"} | 30.,Vpv15,Modbus RTU,,5,4,899,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 900 | PV15Curr | PV15 Input current |  |  | 0.1A |  | With Time1 | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV15Curr "Growatt_PV15Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV15Curr"] | Number:ElectricCurrent Growatt_PV15Curr "PV15Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV15Curr"} | 30.,PV15Curr,Modbus RTU,,5,4,900,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 901 | Ppv15H | PV15 input power (High) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv15H "Growatt_Ppv15H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv15H"] | Number:Power Growatt_Ppv15H "Ppv15H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv15H"} | 30.,Ppv15H,Modbus RTU,,5,4,901,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 902 | Ppv15L | PV15 input power (Low) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv15L "Growatt_Ppv15L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv15L"] | Number:Power Growatt_Ppv15L "Ppv15L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv15L"} | 30.,Ppv15L,Modbus RTU,,5,4,902,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 903 | Vpv16 | PV16 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv16 "Growatt_Vpv16" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv16"] | Number:ElectricPotential Growatt_Vpv16 "Vpv16 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv16"} | 30.,Vpv16,Modbus RTU,,5,4,903,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 904 | PV16Curr | PV16 Input current |  |  | 0.1A |  | With Time1 | TL_X-TL_XH | 0.1 | A | 1 | Type number : PV16Curr "Growatt_PV16Curr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PV16Curr"] | Number:ElectricCurrent Growatt_PV16Curr "PV16Curr [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PV16Curr"} | 30.,PV16Curr,Modbus RTU,,5,4,904,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 905 | Ppv16H | PV16 input power (High) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv16H "Growatt_Ppv16H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv16H"] | Number:Power Growatt_Ppv16H "Ppv16H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv16H"} | 30.,Ppv16H,Modbus RTU,,5,4,905,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 906 | Ppv16L | PV16 input power (Low) |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv16L "Growatt_Ppv16L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv16L"] | Number:Power Growatt_Ppv16L "Ppv16L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv16L"} | 30.,Ppv16L,Modbus RTU,,5,4,906,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 907 | Epv9_todayH | PV9 energy today (High) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv9_todayH "Growatt_Epv9_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv9_todayH"] | Number:Energy Growatt_Epv9_todayH "Epv9_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv9_todayH"} | 30.,Epv9_todayH,Modbus RTU,,5,4,907,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 908 | Epv9_todayL | PV9 energy today (Low) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv9_todayL "Growatt_Epv9_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv9_todayL"] | Number:Energy Growatt_Epv9_todayL "Epv9_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv9_todayL"} | 30.,Epv9_todayL,Modbus RTU,,5,4,908,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 909 | Epv9_totalH | PV9 energy total (High) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv9_totalH "Growatt_Epv9_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv9_totalH"] | Number:Energy Growatt_Epv9_totalH "Epv9_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv9_totalH"} | 30.,Epv9_totalH,Modbus RTU,,5,4,909,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 910 | Epv9_totalL | PV9 energy total (Low) |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Epv9_totalL "Growatt_Epv9_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv9_totalL"] | Number:Energy Growatt_Epv9_totalL "Epv9_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv9_totalL"} | 30.,Epv9_totalL,Modbus RTU,,5,4,910,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 911 | Epv10_todayH | PV10 energy today (High) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv10_todayH "Growatt_Epv10_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv10_todayH"] | Number:Energy Growatt_Epv10_todayH "Epv10_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv10_todayH"} | 30.,Epv10_todayH,Modbus RTU,,5,4,911,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 912 | Epv10_todayL | PV10 energy today (Low) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv10_todayL "Growatt_Epv10_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv10_todayL"] | Number:Energy Growatt_Epv10_todayL "Epv10_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv10_todayL"} | 30.,Epv10_todayL,Modbus RTU,,5,4,912,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 913 | Epv10_totalH | PV10 energy total (High) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv10_totalH "Growatt_Epv10_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv10_totalH"] | Number:Energy Growatt_Epv10_totalH "Epv10_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv10_totalH"} | 30.,Epv10_totalH,Modbus RTU,,5,4,913,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 914 | Epv10_totalL | PV10 energy total (Low) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv10_totalL "Growatt_Epv10_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv10_totalL"] | Number:Energy Growatt_Epv10_totalL "Epv10_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv10_totalL"} | 30.,Epv10_totalL,Modbus RTU,,5,4,914,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 915 | Epv11_todayH | PV11 energy today (High) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv11_todayH "Growatt_Epv11_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv11_todayH"] | Number:Energy Growatt_Epv11_todayH "Epv11_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv11_todayH"} | 30.,Epv11_todayH,Modbus RTU,,5,4,915,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 916 | Epv11_todayL | PV11 energy today (Low) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv11_todayL "Growatt_Epv11_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv11_todayL"] | Number:Energy Growatt_Epv11_todayL "Epv11_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv11_todayL"} | 30.,Epv11_todayL,Modbus RTU,,5,4,916,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 917 | Epv11_totalH | PV11 energy total (High) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv11_totalH "Growatt_Epv11_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv11_totalH"] | Number:Energy Growatt_Epv11_totalH "Epv11_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv11_totalH"} | 30.,Epv11_totalH,Modbus RTU,,5,4,917,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 918 | Epv11_totalL | PV11 energy total (Low) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv11_totalL "Growatt_Epv11_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv11_totalL"] | Number:Energy Growatt_Epv11_totalL "Epv11_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv11_totalL"} | 30.,Epv11_totalL,Modbus RTU,,5,4,918,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 919 | Epv12_todayH | PV12 energy today (High) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv12_todayH "Growatt_Epv12_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv12_todayH"] | Number:Energy Growatt_Epv12_todayH "Epv12_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv12_todayH"} | 30.,Epv12_todayH,Modbus RTU,,5,4,919,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 920 | Epv12_todayL | PV12 energy today (Low) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv12_todayL "Growatt_Epv12_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv12_todayL"] | Number:Energy Growatt_Epv12_todayL "Epv12_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv12_todayL"} | 30.,Epv12_todayL,Modbus RTU,,5,4,920,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 921 | Epv12_totalH | PV12 energy total (High) |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv12_totalH "Growatt_Epv12_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv12_totalH"] | Number:Energy Growatt_Epv12_totalH "Epv12_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv12_totalH"} | 30.,Epv12_totalH,Modbus RTU,,5,4,921,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 922 | Epv12_totalL | PV12 energy total (Low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv12_totalL "Growatt_Epv12_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv12_totalL"] | Number:Energy Growatt_Epv12_totalL "Epv12_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv12_totalL"} | 30.,Epv12_totalL,Modbus RTU,,5,4,922,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 923 | Epv13_todayH | PV13 energy today (High) |  |  | 0.1kWh |  | CHG/DisCHG | Storage | 0.1 | kWh | 1 | Type number : Epv13_todayH "Growatt_Epv13_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv13_todayH"] | Number:Energy Growatt_Epv13_todayH "Epv13_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv13_todayH"} | 30.,Epv13_todayH,Modbus RTU,,5,4,923,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 924 | Epv13_todayL | PV13 energy today (Low) |  |  | 0.1kWh |  | Lead acid/lithium battery temp | Storage | 0.1 | kWh | 1 | Type number : Epv13_todayL "Growatt_Epv13_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv13_todayL"] | Number:Energy Growatt_Epv13_todayL "Epv13_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv13_todayL"} | 30.,Epv13_todayL,Modbus RTU,,5,4,924,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 925 | Epv13_totalH | PV13 energy total (High) |  |  | 0.1kWh |  | No use | Storage | 0.1 | kWh | 1 | Type number : Epv13_totalH "Growatt_Epv13_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv13_totalH"] | Number:Energy Growatt_Epv13_totalH "Epv13_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv13_totalH"} | 30.,Epv13_totalH,Modbus RTU,,5,4,925,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 926 | Epv13_totalL | PV13 energy total (Low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv13_totalL "Growatt_Epv13_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv13_totalL"] | Number:Energy Growatt_Epv13_totalL "Epv13_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv13_totalL"} | 30.,Epv13_totalL,Modbus RTU,,5,4,926,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 927 | Epv14_todayH | PV14 energy today (High) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv14_todayH "Growatt_Epv14_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv14_todayH"] | Number:Energy Growatt_Epv14_todayH "Epv14_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv14_todayH"} | 30.,Epv14_todayH,Modbus RTU,,5,4,927,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 928 | Epv14_todayL | PV14 energy today (Low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv14_todayL "Growatt_Epv14_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv14_todayL"] | Number:Energy Growatt_Epv14_todayL "Epv14_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv14_todayL"} | 30.,Epv14_todayL,Modbus RTU,,5,4,928,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 929 | Epv14_totalH | PV14 energy total (High) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv14_totalH "Growatt_Epv14_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv14_totalH"] | Number:Energy Growatt_Epv14_totalH "Epv14_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv14_totalH"} | 30.,Epv14_totalH,Modbus RTU,,5,4,929,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 930 | Epv14_totalL | PV14 energy total (Low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv14_totalL "Growatt_Epv14_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv14_totalL"] | Number:Energy Growatt_Epv14_totalL "Epv14_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv14_totalL"} | 30.,Epv14_totalL,Modbus RTU,,5,4,930,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 931 | Epv15_todayH | PV15 energy today (High) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv15_todayH "Growatt_Epv15_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv15_todayH"] | Number:Energy Growatt_Epv15_todayH "Epv15_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv15_todayH"} | 30.,Epv15_todayH,Modbus RTU,,5,4,931,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 932 | Epv15_todayL | PV15 energy today (Low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv15_todayL "Growatt_Epv15_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv15_todayL"] | Number:Energy Growatt_Epv15_todayL "Epv15_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv15_todayL"} | 30.,Epv15_todayL,Modbus RTU,,5,4,932,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 933 | Epv15_totalH | PV15 energy total (High) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv15_totalH "Growatt_Epv15_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv15_totalH"] | Number:Energy Growatt_Epv15_totalH "Epv15_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv15_totalH"} | 30.,Epv15_totalH,Modbus RTU,,5,4,933,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 934 | Epv15_totalL | PV15 energy total (Low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv15_totalL "Growatt_Epv15_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv15_totalL"] | Number:Energy Growatt_Epv15_totalL "Epv15_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv15_totalL"} | 30.,Epv15_totalL,Modbus RTU,,5,4,934,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 935 | Epv16_todayH | PV16 energy today (High) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv16_todayH "Growatt_Epv16_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv16_todayH"] | Number:Energy Growatt_Epv16_todayH "Epv16_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv16_todayH"} | 30.,Epv16_todayH,Modbus RTU,,5,4,935,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 936 | Epv16_todayL | PV16 energy today (Low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv16_todayL "Growatt_Epv16_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv16_todayL"] | Number:Energy Growatt_Epv16_todayL "Epv16_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv16_todayL"} | 30.,Epv16_todayL,Modbus RTU,,5,4,936,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 937 | Epv16_totalH | PV16 energy total (High) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv16_totalH "Growatt_Epv16_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv16_totalH"] | Number:Energy Growatt_Epv16_totalH "Epv16_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv16_totalH"} | 30.,Epv16_totalH,Modbus RTU,,5,4,937,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 938 | Epv16_totalL | PV16 energy total (Low) |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv16_totalL "Growatt_Epv16_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv16_totalL"] | Number:Energy Growatt_Epv16_totalL "Epv16_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv16_totalL"} | 30.,Epv16_totalL,Modbus RTU,,5,4,938,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 939 | PIDPV9_Voltage | PID PV9PE Volt/ Flyspan |  | 0~1000V | 0.1V |  | Same as | USTimeSet | 0.1 | V | 1 | Type number : PIDPV9_Voltage "Growatt_PIDPV9_Voltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV9_Voltage"] | Number:ElectricPotential Growatt_PIDPV9_Voltage "PIDPV9_Voltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDPV9_Voltage"} | 30.,PIDPV9_Voltage,Modbus RTU,,5,4,939,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 940 | PIDPV9_Current | PID PV9PE Current |  | -10~10mA | 0.1mA |  | Same as | USTimeSet | 0.1 | mA | 1 | Type number : PIDPV9_Current "Growatt_PIDPV9_Current" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV9_Current"] | #N/A | 30.,PIDPV9_Current,Modbus RTU,,5,4,940,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 941 | PIDPV10_ | PID PV10PE/ Flyspan voltage (MAX |  | 0~1000V | 0.1V |  |  | BDC | 0.1 | V | 1 | Type number : PIDPV10_ "Growatt_PIDPV10_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDPV10_"] | Number:ElectricPotential Growatt_PIDPV10_ "PIDPV10_ [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDPV10_"} | 30.,PIDPV10_,Modbus RTU,,5,4,941,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 942 | PIDCurrentPV10_ | PID PV10PE Current |  | -10~10mA | 0.1mA |  |  | ALL | 0.1 | mA | 1 | Type number : PIDCurrentPV10_ "Growatt_PIDCurrentPV10_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDCurrentPV10_"] | #N/A | 30.,PIDCurrentPV10_,Modbus RTU,,5,4,942,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 943 | PIDVoltagePV11_ | PID PV11PE Volt/ |  | 0~1000V | 0.1V |  | Same as | USTimeSet | 0.1 | V | 1 | Type number : PIDVoltagePV11_ "Growatt_PIDVoltagePV11_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDVoltagePV11_"] | Number:ElectricPotential Growatt_PIDVoltagePV11_ "PIDVoltagePV11_ [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDVoltagePV11_"} | 30.,PIDVoltagePV11_,Modbus RTU,,5,4,943,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 944 | PIDCurrentPV11_ | PID PV11PE Current |  | -10~10mA | 0.1mA |  |  | ALL | 0.1 | mA | 1 | Type number : PIDCurrentPV11_ "Growatt_PIDCurrentPV11_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDCurrentPV11_"] | #N/A | 30.,PIDCurrentPV11_,Modbus RTU,,5,4,944,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 945 | PIDVoltagePV12_ | PID PV12PE Volt/ |  | 0~1000V | 0.1V |  | Same as | USTimeSet | 0.1 | V | 1 | Type number : PIDVoltagePV12_ "Growatt_PIDVoltagePV12_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDVoltagePV12_"] | Number:ElectricPotential Growatt_PIDVoltagePV12_ "PIDVoltagePV12_ [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDVoltagePV12_"} | 30.,PIDVoltagePV12_,Modbus RTU,,5,4,945,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 946 | PIDCurrentPV12_ | PID PV12PE Current |  | -10~10mA | 0.1mA |  |  | ALL | 0.1 | mA | 1 | Type number : PIDCurrentPV12_ "Growatt_PIDCurrentPV12_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDCurrentPV12_"] | #N/A | 30.,PIDCurrentPV12_,Modbus RTU,,5,4,946,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 947 | PIDVoltagePV13_ | PID PV13PE Volt/ |  | 0~1000V | 0.1V |  | Same as Time 1 | USTimeSet | 0.1 | V | 1 | Type number : PIDVoltagePV13_ "Growatt_PIDVoltagePV13_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDVoltagePV13_"] | Number:ElectricPotential Growatt_PIDVoltagePV13_ "PIDVoltagePV13_ [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDVoltagePV13_"} | 30.,PIDVoltagePV13_,Modbus RTU,,5,4,947,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 948 | PIDCurrentPV13_ | PID PV13PE Current |  | -10~10mA | 0.1mA |  |  | ALL | 0.1 | mA | 1 | Type number : PIDCurrentPV13_ "Growatt_PIDCurrentPV13_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDCurrentPV13_"] | #N/A | 30.,PIDCurrentPV13_,Modbus RTU,,5,4,948,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 949 | PIDVoltagePV14_ | PID PV14PE Volt/ |  | 0~1000V | 0.1V |  | Same as Time 1 | USTimeSet | 0.1 | V | 1 | Type number : PIDVoltagePV14_ "Growatt_PIDVoltagePV14_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDVoltagePV14_"] | Number:ElectricPotential Growatt_PIDVoltagePV14_ "PIDVoltagePV14_ [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDVoltagePV14_"} | 30.,PIDVoltagePV14_,Modbus RTU,,5,4,949,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 950 | PIDCurrentPV14_ | PID PV14PE Current |  | -10~10mA | 0.1mA |  |  | ALL | 0.1 | mA | 1 | Type number : PIDCurrentPV14_ "Growatt_PIDCurrentPV14_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDCurrentPV14_"] | #N/A | 30.,PIDCurrentPV14_,Modbus RTU,,5,4,950,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 951 | PIDVoltagePV15_ | PID PV15PE Volt/ |  | 0~1000V | 0.1V |  | Same as Time 1 | USTimeSet | 0.1 | V | 1 | Type number : PIDVoltagePV15_ "Growatt_PIDVoltagePV15_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDVoltagePV15_"] | Number:ElectricPotential Growatt_PIDVoltagePV15_ "PIDVoltagePV15_ [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDVoltagePV15_"} | 30.,PIDVoltagePV15_,Modbus RTU,,5,4,951,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 952 | PIDCurrentPV15_ | PID PV15PE Current |  | -10~10mA | 0.1mA |  |  | ALL | 0.1 | mA | 1 | Type number : PIDCurrentPV15_ "Growatt_PIDCurrentPV15_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDCurrentPV15_"] | #N/A | 30.,PIDCurrentPV15_,Modbus RTU,,5,4,952,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 953 | PIDVoltagePV16_ | PID PV16PE Volt/ |  | 0~1000V | 0.1V |  | Same as Time 1 | USTimeSet | 0.1 | V | 1 | Type number : PIDVoltagePV16_ "Growatt_PIDVoltagePV16_" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDVoltagePV16_"] | Number:ElectricPotential Growatt_PIDVoltagePV16_ "PIDVoltagePV16_ [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDVoltagePV16_"} | 30.,PIDVoltagePV16_,Modbus RTU,,5,4,953,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 954 | PIDCurrent | PID PV16PE Current |  | -10~10mA | 0.1mA |  |  | ALL | 0.1 | mA | 1 | Type number : PIDCurrent "Growatt_PIDCurrent" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PIDCurrent"] | #N/A | 30.,PIDCurrent,Modbus RTU,,5,4,954,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 955 | V_String17 | PV String 17 voltage |  |  | 0.1V |  | SxxBxx | ALL | 0.1 | V | 1 | Type number : V_String17 "Growatt_V_String17" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String17"] | Number:ElectricPotential Growatt_V_String17 "V_String17 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String17"} | 30.,V_String17,Modbus RTU,,5,4,955,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 956 | Curr_String17 | PV String 17 Current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String17 "Growatt_Curr_String17" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String17"] | Number:ElectricCurrent Growatt_Curr_String17 "Curr_String17 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String17"} | 30.,Curr_String17,Modbus RTU,,5,4,956,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 957 | V_String18 | PV String 18 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V_String18 "Growatt_V_String18" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String18"] | Number:ElectricPotential Growatt_V_String18 "V_String18 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String18"} | 30.,V_String18,Modbus RTU,,5,4,957,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 958 | Curr_String18 | PV String 18 Current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String18 "Growatt_Curr_String18" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String18"] | Number:ElectricCurrent Growatt_Curr_String18 "Curr_String18 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String18"} | 30.,Curr_String18,Modbus RTU,,5,4,958,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 959 | V_String19 | PV String 19 voltage |  |  | 0.1V |  | 255 means no this point | ALL | 0.1 | V | 1 | Type number : V_String19 "Growatt_V_String19" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String19"] | Number:ElectricPotential Growatt_V_String19 "V_String19 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String19"} | 30.,V_String19,Modbus RTU,,5,4,959,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 960 | Curr_String19 | PV String 19 Current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String19 "Growatt_Curr_String19" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String19"] | Number:ElectricCurrent Growatt_Curr_String19 "Curr_String19 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String19"} | 30.,Curr_String19,Modbus RTU,,5,4,960,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 961 | V_String20 | PV String 20 voltage |  |  | 0.1V |  | 255 means no this point | ALL | 0.1 | V | 1 | Type number : V_String20 "Growatt_V_String20" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String20"] | Number:ElectricPotential Growatt_V_String20 "V_String20 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String20"} | 30.,V_String20,Modbus RTU,,5,4,961,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 962 | Curr_String20 | PV String 20 Current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String20 "Growatt_Curr_String20" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String20"] | Number:ElectricCurrent Growatt_Curr_String20 "Curr_String20 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String20"} | 30.,Curr_String20,Modbus RTU,,5,4,962,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 963 | V_String21 | PV String 21 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V_String21 "Growatt_V_String21" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String21"] | Number:ElectricPotential Growatt_V_String21 "V_String21 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String21"} | 30.,V_String21,Modbus RTU,,5,4,963,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 964 | Curr_String21 | PV String 21 Current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String21 "Growatt_Curr_String21" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String21"] | Number:ElectricCurrent Growatt_Curr_String21 "Curr_String21 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String21"} | 30.,Curr_String21,Modbus RTU,,5,4,964,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 965 | V_String22 | PV String22 voltage |  |  | 0.1V |  | 255 means no this point | ALL | 0.1 | V | 1 | Type number : V_String22 "Growatt_V_String22" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String22"] | Number:ElectricPotential Growatt_V_String22 "V_String22 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String22"} | 30.,V_String22,Modbus RTU,,5,4,965,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 966 | Curr_String22 | PV String 22 Current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String22 "Growatt_Curr_String22" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String22"] | Number:ElectricCurrent Growatt_Curr_String22 "Curr_String22 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String22"} | 30.,Curr_String22,Modbus RTU,,5,4,966,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 967 | V_String23 | PV String 23 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V_String23 "Growatt_V_String23" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String23"] | Number:ElectricPotential Growatt_V_String23 "V_String23 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String23"} | 30.,V_String23,Modbus RTU,,5,4,967,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 968 | Curr_String23 | PV String 23 Current |  | -15~15A | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : Curr_String23 "Growatt_Curr_String23" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String23"] | Number:ElectricCurrent Growatt_Curr_String23 "Curr_String23 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String23"} | 30.,Curr_String23,Modbus RTU,,5,4,968,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 969 | V_String24 | PV String 24 voltage |  | -15A~15A | 0.1A |  | 255 means no this point | ALL | 0.1 | A | 1 | Type number : V_String24 "Growatt_V_String24" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String24"] | Number:ElectricCurrent Growatt_V_String24 "V_String24 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String24"} | 30.,V_String24,Modbus RTU,,5,4,969,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 970 | Curr_String24 | PV String 24 Current |  |  | 0.1V |  |  | TL_X-TL_XH | 0.1 | V | 1 | Type number : Curr_String24 "Growatt_Curr_String24" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String24"] | Number:ElectricPotential Growatt_Curr_String24 "Curr_String24 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String24"} | 30.,Curr_String24,Modbus RTU,,5,4,970,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 971 | V_String25 | PV String 25 voltage |  | -15A~15A | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : V_String25 "Growatt_V_String25" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String25"] | Number:ElectricCurrent Growatt_V_String25 "V_String25 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String25"} | 30.,V_String25,Modbus RTU,,5,4,971,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 972 | Curr_String25 | PV String 25 Current |  |  | 0.1V |  |  | TL_X-TL_XH | 0.1 | V | 1 | Type number : Curr_String25 "Growatt_Curr_String25" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String25"] | Number:ElectricPotential Growatt_Curr_String25 "Curr_String25 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String25"} | 30.,Curr_String25,Modbus RTU,,5,4,972,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 973 | V_String26 | PV String 26 voltage |  | -15~15A | 0.1A |  | System power L | ALL | 0.1 | A | 1 | Type number : V_String26 "Growatt_V_String26" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String26"] | Number:ElectricCurrent Growatt_V_String26 "V_String26 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String26"} | 30.,V_String26,Modbus RTU,,5,4,973,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 974 | Curr_String26 | PV String 26 Current |  |  | 0.1V |  |  | TL_X-TL_XH | 0.1 | V | 1 | Type number : Curr_String26 "Growatt_Curr_String26" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String26"] | Number:ElectricPotential Growatt_Curr_String26 "Curr_String26 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String26"} | 30.,Curr_String26,Modbus RTU,,5,4,974,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 975 | V_String27 | PV String 27 voltage |  | -15~15A | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : V_String27 "Growatt_V_String27" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String27"] | Number:ElectricCurrent Growatt_V_String27 "V_String27 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String27"} | 30.,V_String27,Modbus RTU,,5,4,975,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 976 | Curr_String27 | PV String 27 Current |  |  | 0.1V |  |  | TL_X-TL_XH | 0.1 | V | 1 | Type number : Curr_String27 "Growatt_Curr_String27" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String27"] | Number:ElectricPotential Growatt_Curr_String27 "Curr_String27 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String27"} | 30.,Curr_String27,Modbus RTU,,5,4,976,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 977 | V_String28 | PV String 28 voltage |  | -15~15A | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : V_String28 "Growatt_V_String28" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String28"] | Number:ElectricCurrent Growatt_V_String28 "V_String28 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String28"} | 30.,V_String28,Modbus RTU,,5,4,977,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 978 | Curr_String28 | PV String 28 Current |  |  | 0.1V |  |  | TL_X-TL_XH | 0.1 | V | 1 | Type number : Curr_String28 "Growatt_Curr_String28" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String28"] | Number:ElectricPotential Growatt_Curr_String28 "Curr_String28 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String28"} | 30.,Curr_String28,Modbus RTU,,5,4,978,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 979 | V_String29 | PV String 29 voltage |  | -15A~15A | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : V_String29 "Growatt_V_String29" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String29"] | Number:ElectricCurrent Growatt_V_String29 "V_String29 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String29"} | 30.,V_String29,Modbus RTU,,5,4,979,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 980 | Curr_String29 | PV String 29 Current |  |  | 0.1V |  |  | TL_X-TL_XH | 0.1 | V | 1 | Type number : Curr_String29 "Growatt_Curr_String29" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String29"] | Number:ElectricPotential Growatt_Curr_String29 "Curr_String29 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String29"} | 30.,Curr_String29,Modbus RTU,,5,4,980,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 981 | V_String30 | PV String 30 voltage |  | -15~15A | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : V_String30 "Growatt_V_String30" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String30"] | Number:ElectricCurrent Growatt_V_String30 "V_String30 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String30"} | 30.,V_String30,Modbus RTU,,5,4,981,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 982 | Curr_String30 | PV String 30 Current |  |  | 0.1V |  | reserved | SPA | 0.1 | V | 1 | Type number : Curr_String30 "Growatt_Curr_String30" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String30"] | Number:ElectricPotential Growatt_Curr_String30 "Curr_String30 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String30"} | 30.,Curr_String30,Modbus RTU,,5,4,982,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 983 | V_String31 | PV String 31 voltage |  | -15~15A | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : V_String31 "Growatt_V_String31" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String31"] | Number:ElectricCurrent Growatt_V_String31 "V_String31 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String31"} | 30.,V_String31,Modbus RTU,,5,4,983,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 984 | Curr_String31 | PV String 31 Current |  |  | 0.1V |  | Storage | SPA | 0.1 | V | 1 | Type number : Curr_String31 "Growatt_Curr_String31" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String31"] | Number:ElectricPotential Growatt_Curr_String31 "Curr_String31 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String31"} | 30.,Curr_String31,Modbus RTU,,5,4,984,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 985 | V_String32 | PV String 32 voltage |  | -15~15A | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : V_String32 "Growatt_V_String32" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.V_String32"] | Number:ElectricCurrent Growatt_V_String32 "V_String32 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V_String32"} | 30.,V_String32,Modbus RTU,,5,4,985,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 986 | Curr_String32 | PV String 32 Current |  |  |  |  | Storage | SPA |  |  | 0 | Type number : Curr_String32 "Growatt_Curr_String32" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Curr_String32"] | Number Growatt_Curr_String32 "Curr_String32" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Curr_String32"} | 30.,Curr_String32,Modbus RTU,,5,4,986,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 987 | StrUnmatch2 | Bit0~15: String 17~32 unmatch |  |  |  |  | SPH4-11K used | Storage |  |  | 0 | Type number : StrUnmatch2 "Growatt_StrUnmatch2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.StrUnmatch2"] | Number Growatt_StrUnmatch2 "StrUnmatch2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:StrUnmatch2"} | 30.,StrUnmatch2,Modbus RTU,,5,4,987,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 988 | StrCurrentUnblance2 | Bit0~15:String 17~32 current |  |  |  |  | Battery priority enable 1 | Storage |  |  | 0 | Type number : StrCurrentUnblance2 "Growatt_StrCurrentUnblance2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.StrCurrentUnblance2"] | Number Growatt_StrCurrentUnblance2 "StrCurrentUnblance2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:StrCurrentUnblance2"} | 30.,StrCurrentUnblance2,Modbus RTU,,5,4,988,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 989 | StrDisconnect2 | Bit0~15: String 17~32 disconnect | [5 empty] | Storage |  |  | 0 | Type number : StrDisconnect2 "Growatt_StrDisconnect2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.StrDisconnect2"] | Number Growatt_StrDisconnect2 "StrDisconnect2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:StrDisconnect2"} | 30.,StrDisconnect2,Modbus RTU,,5,4,989,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 990 | PVWarningValue | PV Warning Value (PV9-PV16) |  |  |  |  | Under Fre Delay | TL_X-TL_XH |  |  | 0 | Type number : PVWarningValue "Growatt_PVWarningValue" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PVWarningValue"] | Number Growatt_PVWarningValue "PVWarningValue" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PVWarningValue"} | 30.,PVWarningValue,Modbus RTU,,5,4,990,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 991 | StrWaringvalue1 | string1~string16 abnormal |  |  |  |  | Under Fre Delay Time | Storage |  |  | 0 | Type number : StrWaringvalue1 "Growatt_StrWaringvalue1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.StrWaringvalue1"] | Number Growatt_StrWaringvalue1 "StrWaringvalue1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:StrWaringvalue1"} | 30.,StrWaringvalue1,Modbus RTU,,5,4,991,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 992 | StrWaringvalue2 | string17~string32 abnormal |  |  |  |  | Upper temperature limit | Storage |  |  | 0 | Type number : StrWaringvalue2 "Growatt_StrWaringvalue2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.StrWaringvalue2"] | Number Growatt_StrWaringvalue2 "StrWaringvalue2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:StrWaringvalue2"} | 30.,StrWaringvalue2,Modbus RTU,,5,4,992,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 999 | SystemCmd | M3 to DSP system command |  |  |  |  | Clear battery low voltage error voltage point | Storage |  |  | 0 | Type number : SystemCmd "Growatt_SystemCmd" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.SystemCmd"] | Number Growatt_SystemCmd "SystemCmd" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SystemCmd"} | 30.,SystemCmd,Modbus RTU,,5,4,999,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1000 | uwSysWorkMode | System work mode |  | 0x00:waiting module |  |  |  | ALL |  |  | 0 | Type number : uwSysWorkMode "Growatt_uwSysWorkMode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwSysWorkMode"] | Number Growatt_uwSysWorkMode "uwSysWorkMode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwSysWorkMode"} | 30.,uwSysWorkMode,Modbus RTU,,5,4,1000,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1001 | Systemfaultword0 | System fault word0 |  |  |  |  | Lead-acid battery LV voltage | Storage |  |  | 0 | Type number : Systemfaultword0 "Growatt_Systemfaultword0" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Systemfaultword0"] | Number Growatt_Systemfaultword0 "Systemfaultword0" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Systemfaultword0"} | 30.,Systemfaultword0,Modbus RTU,,5,4,1001,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1002 | Systemfaultword1 | System fault word1 |  |  |  |  | Means these settings will be acting or not when next | Storage |  |  | 0 | Type number : Systemfaultword1 "Growatt_Systemfaultword1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Systemfaultword1"] | Number Growatt_Systemfaultword1 "Systemfaultword1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Systemfaultword1"} | 30.,Systemfaultword1,Modbus RTU,,5,4,1002,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1003 | Systemfaultword2 | System fault word2 |  |  |  |  | CC current | Storage |  |  | 0 | Type number : Systemfaultword2 "Growatt_Systemfaultword2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Systemfaultword2"] | Number Growatt_Systemfaultword2 "Systemfaultword2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Systemfaultword2"} | 30.,Systemfaultword2,Modbus RTU,,5,4,1003,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1004 | Systemfaultword3 | System fault word3 |  |  |  |  | 0xA0: Initialize safety defaults | ALL |  |  | 0 | Type number : Systemfaultword3 "Growatt_Systemfaultword3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Systemfaultword3"] | Number Growatt_Systemfaultword3 "Systemfaultword3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Systemfaultword3"} | 30.,Systemfaultword3,Modbus RTU,,5,4,1004,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1005 | Systemfaultword4 | System fault word4 |  |  |  |  | 0:disable | ALL |  |  | 0 | Type number : Systemfaultword4 "Growatt_Systemfaultword4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Systemfaultword4"] | Number Growatt_Systemfaultword4 "Systemfaultword4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Systemfaultword4"} | 30.,Systemfaultword4,Modbus RTU,,5,4,1005,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1006 | Systemfaultword5 | System fault word5 |  |  |  |  | Currently only bit0 and bit1 are used bit0 is used to manually clear the Debug data uploaded to the server bit1 is used to manually clear the fault codes that need to be powered off to clear | ALL |  |  | 0 | Type number : Systemfaultword5 "Growatt_Systemfaultword5" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Systemfaultword5"] | Number Growatt_Systemfaultword5 "Systemfaultword5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Systemfaultword5"} | 30.,Systemfaultword5,Modbus RTU,,5,4,1006,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1007 | Systemfaultword6 | System fault word6 |  |  |  |  | 0:Zero Power Output | ALL |  |  | 0 | Type number : Systemfaultword6 "Growatt_Systemfaultword6" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Systemfaultword6"] | Number Growatt_Systemfaultword6 "Systemfaultword6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Systemfaultword6"} | 30.,Systemfaultword6,Modbus RTU,,5,4,1007,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1008 | Systemfaultword7 | System fault word7 | [8 empty] | 0 | Type number : Systemfaultword7 "Growatt_Systemfaultword7" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Systemfaultword7"] | Number Growatt_Systemfaultword7 "Systemfaultword7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Systemfaultword7"} | 30.,Systemfaultword7,Modbus RTU,,5,4,1008,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1009 | Pdischarge1H | Discharge power(high) |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pdischarge1H "Growatt_Pdischarge1H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pdischarge1H"] | Number:Power Growatt_Pdischarge1H "Pdischarge1H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pdischarge1H"} | 31.,Pdischarge1H,Modbus RTU,,5,4,1009,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1010 | Pdischarge1L | Discharge power (low) |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pdischarge1L "Growatt_Pdischarge1L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pdischarge1L"] | Number:Power Growatt_Pdischarge1L "Pdischarge1L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pdischarge1L"} | 31.,Pdischarge1L,Modbus RTU,,5,4,1010,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1011 | Pcharge1H | Charge power(high) |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pcharge1H "Growatt_Pcharge1H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pcharge1H"] | Number:Power Growatt_Pcharge1H "Pcharge1H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pcharge1H"} | 32.,Pcharge1H,Modbus RTU,,5,4,1011,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1012 | Pcharge1L | Charge power (low) |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pcharge1L "Growatt_Pcharge1L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pcharge1L"] | Number:Power Growatt_Pcharge1L "Pcharge1L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pcharge1L"} | 32.,Pcharge1L,Modbus RTU,,5,4,1012,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1013 | Vbat | Battery voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vbat "Growatt_Vbat" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vbat"] | Number:ElectricPotential Growatt_Vbat "Vbat [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbat"} | 33.,Vbat,Modbus RTU,,5,4,1013,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1014 | SOC | State of charge Capacity |  | 0-100 | 0.01 |  | Discharge | Storage | 0.01 |  | 2 | Type number : SOC "Growatt_SOC" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.SOC"] | Number Growatt_SOC "SOC [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SOC"} | 34.,SOC,Modbus RTU,,5,4,1014,1,9410,2,0,Unsigned int,0,2,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1015 | PactouserRH | AC power to user H |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactouserRH "Growatt_PactouserRH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactouserRH"] | Number:Power Growatt_PactouserRH "PactouserRH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactouserRH"} | 34.,PactouserRH,Modbus RTU,,5,4,1015,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1016 | PactouserRL | AC power to user L |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactouserRL "Growatt_PactouserRL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactouserRL"] | Number:Power Growatt_PactouserRL "PactouserRL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactouserRL"} | 34.,PactouserRL,Modbus RTU,,5,4,1016,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1017 | PactouserSH | Pactouser S H |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactouserSH "Growatt_PactouserSH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactouserSH"] | Number:Power Growatt_PactouserSH "PactouserSH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactouserSH"} | 34.,PactouserSH,Modbus RTU,,5,4,1017,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1018 | PactouserSL | Pactouser S L |  |  | 0.1W |  | Line voltage | ALL | 0.1 | W | 1 | Type number : PactouserSL "Growatt_PactouserSL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactouserSL"] | Number:Power Growatt_PactouserSL "PactouserSL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactouserSL"} | 34.,PactouserSL,Modbus RTU,,5,4,1018,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1019 | PactouserTH | Pactouser T H |  |  | 0.1W |  | Line voltage | ALL | 0.1 | W | 1 | Type number : PactouserTH "Growatt_PactouserTH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactouserTH"] | Number:Power Growatt_PactouserTH "PactouserTH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactouserTH"} | 34.,PactouserTH,Modbus RTU,,5,4,1019,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1020 | PactouserTL | Pactouser T H |  |  | 0.1W |  | Line voltage | ALL | 0.1 | W | 1 | Type number : PactouserTL "Growatt_PactouserTL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactouserTL"] | Number:Power Growatt_PactouserTL "PactouserTL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactouserTL"} | 34.,PactouserTL,Modbus RTU,,5,4,1020,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1021 | PactouserTotalH | AC power to user total H |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactouserTotalH "Growatt_PactouserTotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactouserTotalH"] | Number:Power Growatt_PactouserTotalH "PactouserTotalH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactouserTotalH"} | 35.,PactouserTotalH,Modbus RTU,,5,4,1021,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1022 | PactouserTotalL | AC power to user total L |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactouserTotalL "Growatt_PactouserTotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactouserTotalL"] | Number:Power Growatt_PactouserTotalL "PactouserTotalL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactouserTotalL"} | 35.,PactouserTotalL,Modbus RTU,,5,4,1022,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1023 | PactogridRH | AC power to grid H |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactogridRH "Growatt_PactogridRH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactogridRH"] | Number:Power Growatt_PactogridRH "PactogridRH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactogridRH"} | 35.,PactogridRH,Modbus RTU,,5,4,1023,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1024 | PactogridRL | AC power to grid L |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactogridRL "Growatt_PactogridRL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactogridRL"] | Number:Power Growatt_PactogridRL "PactogridRL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactogridRL"} | 35.,PactogridRL,Modbus RTU,,5,4,1024,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1025 | PactogridSH |  |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactogridSH "Growatt_PactogridSH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactogridSH"] | Number:Power Growatt_PactogridSH "PactogridSH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactogridSH"} | 35.,PactogridSH,Modbus RTU,,5,4,1025,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1026 | PactogridSL |  |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactogridSL "Growatt_PactogridSL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactogridSL"] | Number:Power Growatt_PactogridSL "PactogridSL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactogridSL"} | 35.,PactogridSL,Modbus RTU,,5,4,1026,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1027 | PactogridTH |  |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactogridTH "Growatt_PactogridTH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactogridTH"] | Number:Power Growatt_PactogridTH "PactogridTH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactogridTH"} | 35.,PactogridTH,Modbus RTU,,5,4,1027,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1028 | PactogridTL |  |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactogridTL "Growatt_PactogridTL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactogridTL"] | Number:Power Growatt_PactogridTL "PactogridTL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactogridTL"} | 35.,PactogridTL,Modbus RTU,,5,4,1028,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1029 | PactogridtotalH | AC power to grid total H |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactogridtotalH "Growatt_PactogridtotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactogridtotalH"] | Number:Power Growatt_PactogridtotalH "PactogridtotalH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactogridtotalH"} | 36.,PactogridtotalH,Modbus RTU,,5,4,1029,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1030 | PactogridtotalL | AC power to grid total L |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PactogridtotalL "Growatt_PactogridtotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PactogridtotalL"] | Number:Power Growatt_PactogridtotalL "PactogridtotalL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PactogridtotalL"} | 36.,PactogridtotalL,Modbus RTU,,5,4,1030,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1031 | PLocalLoadRH | INV power to local load H |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : PLocalLoadRH "Growatt_PLocalLoadRH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PLocalLoadRH"] | Number:Power Growatt_PLocalLoadRH "PLocalLoadRH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PLocalLoadRH"} | 36.,PLocalLoadRH,Modbus RTU,,5,4,1031,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1032 | PLocalLoadRL | INV power to local load L |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : PLocalLoadRL "Growatt_PLocalLoadRL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PLocalLoadRL"] | Number:Power Growatt_PLocalLoadRL "PLocalLoadRL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PLocalLoadRL"} | 36.,PLocalLoadRL,Modbus RTU,,5,4,1032,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1033 | PLocalLoadSH |  |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : PLocalLoadSH "Growatt_PLocalLoadSH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PLocalLoadSH"] | Number:Power Growatt_PLocalLoadSH "PLocalLoadSH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PLocalLoadSH"} | 36.,PLocalLoadSH,Modbus RTU,,5,4,1033,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1034 | PLocalLoadSL |  |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : PLocalLoadSL "Growatt_PLocalLoadSL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PLocalLoadSL"] | Number:Power Growatt_PLocalLoadSL "PLocalLoadSL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PLocalLoadSL"} | 36.,PLocalLoadSL,Modbus RTU,,5,4,1034,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1035 | PLocalLoadTH |  |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : PLocalLoadTH "Growatt_PLocalLoadTH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PLocalLoadTH"] | Number:Power Growatt_PLocalLoadTH "PLocalLoadTH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PLocalLoadTH"} | 36.,PLocalLoadTH,Modbus RTU,,5,4,1035,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1036 | PLocalLoadTL |  |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : PLocalLoadTL "Growatt_PLocalLoadTL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PLocalLoadTL"] | Number:Power Growatt_PLocalLoadTL "PLocalLoadTL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PLocalLoadTL"} | 36.,PLocalLoadTL,Modbus RTU,,5,4,1036,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1037 | PLocalLoadtotalH | INV power to local load total H |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : PLocalLoadtotalH "Growatt_PLocalLoadtotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PLocalLoadtotalH"] | Number:Power Growatt_PLocalLoadtotalH "PLocalLoadtotalH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PLocalLoadtotalH"} | 37.,PLocalLoadtotalH,Modbus RTU,,5,4,1037,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1038 | PLocalLoadtotalL | INV power to local load total |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : PLocalLoadtotalL "Growatt_PLocalLoadtotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PLocalLoadtotalL"] | Number:Power Growatt_PLocalLoadtotalL "PLocalLoadtotalL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PLocalLoadtotalL"} | 37.,PLocalLoadtotalL,Modbus RTU,,5,4,1038,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1039 | IPMTemperature | REC Temperature |  |  | 0.1? |  |  | ALL | 0.1 | ? | 1 | Type number : IPMTemperature "Growatt_IPMTemperature" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.IPMTemperature"] | Number:Length Growatt_IPMTemperature "IPMTemperature [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:IPMTemperature"} | 37.,IPMTemperature,Modbus RTU,,5,4,1039,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1040 | BatteryTemp | Battery Temperature |  |  | 0.1°C |  |  | TL_X-TL_XH | 0.1 | °C | 1 | Type number : BatteryTemp "Growatt_BatteryTemp" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatteryTemp"] | Number:Temperature Growatt_BatteryTemp "BatteryTemp [%0.1f °C]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatteryTemp"} | 38.,BatteryTemp,Modbus RTU,,5,4,1040,1,9410,2,0,Unsigned int,0,1,°C,1,100,97,0,0,0,1.000000,0,255
| 4 | 1041 | SPDSPStatus | SP state | [5 empty] | Storage |  |  | 0 | Type number : SPDSPStatus "Growatt_SPDSPStatus" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.SPDSPStatus"] | Number Growatt_SPDSPStatus "SPDSPStatus" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SPDSPStatus"} | 38.,SPDSPStatus,Modbus RTU,,5,4,1041,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1042 | SPBusVolt | SP BUS2 Volt |  |  | 0.1V |  |  | Storage | 0.1 | V | 1 | Type number : SPBusVolt "Growatt_SPBusVolt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.SPBusVolt"] | Number:ElectricPotential Growatt_SPBusVolt "SPBusVolt [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SPBusVolt"} | 38.,SPBusVolt,Modbus RTU,,5,4,1042,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1044 | Etouser_todayH | Energy to user today high |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etouser_todayH "Growatt_Etouser_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etouser_todayH"] | Number:Energy Growatt_Etouser_todayH "Etouser_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etouser_todayH"} | 39.,Etouser_todayH,Modbus RTU,,5,4,1044,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1045 | Etouser_todayL | Energy to user today low |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etouser_todayL "Growatt_Etouser_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etouser_todayL"] | Number:Energy Growatt_Etouser_todayL "Etouser_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etouser_todayL"} | 39.,Etouser_todayL,Modbus RTU,,5,4,1045,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1046 | Etouser_totalH | Energy to user total high |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etouser_totalH "Growatt_Etouser_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etouser_totalH"] | Number:Energy Growatt_Etouser_totalH "Etouser_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etouser_totalH"} | 40.,Etouser_totalH,Modbus RTU,,5,4,1046,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
x | 4 | 1047 | Etouser_totalL | Energy to user total low |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etouser_totalL "Growatt_Etouser_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etouser_totalL"] | Number:Energy Growatt_Etouser_totalL "Etouser_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etouser_totalL"} | 41.,Etouser_totalL,Modbus RTU,,5,4,1047,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1048 | Etogrid_todayH | Energy to grid today high |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etogrid_todayH "Growatt_Etogrid_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etogrid_todayH"] | Number:Energy Growatt_Etogrid_todayH "Etogrid_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etogrid_todayH"} | 42.,Etogrid_todayH,Modbus RTU,,5,4,1048,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1049 | Etogrid_todayL | Energy to grid today low |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etogrid_todayL "Growatt_Etogrid_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etogrid_todayL"] | Number:Energy Growatt_Etogrid_todayL "Etogrid_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etogrid_todayL"} | 42.,Etogrid_todayL,Modbus RTU,,5,4,1049,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1050 | Etogrid_totalH | Energy to grid total high |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etogrid_totalH "Growatt_Etogrid_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etogrid_totalH"] | Number:Energy Growatt_Etogrid_totalH "Etogrid_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etogrid_totalH"} | 43.,Etogrid_totalH,Modbus RTU,,5,4,1050,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1051 | Etogrid_totalL | Energy to grid total low |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etogrid_totalL "Growatt_Etogrid_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etogrid_totalL"] | Number:Energy Growatt_Etogrid_totalL "Etogrid_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etogrid_totalL"} | 43.,Etogrid_totalL,Modbus RTU,,5,4,1051,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1052 | Edischarge1_todayH | Discharge energy1 today |  |  | 0.1kWh |  | SPA used | BMS | 0.1 | kWh | 1 | Type number : Edischarge1_todayH "Growatt_Edischarge1_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Edischarge1_todayH"] | Number:Energy Growatt_Edischarge1_todayH "Edischarge1_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Edischarge1_todayH"} | 44.,Edischarge1_todayH,Modbus RTU,,5,4,1052,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1053 | Edischarge1_todayL | Discharge energy1 today |  |  | 0.1kWh |  | SPA used | BMS | 0.1 | kWh | 1 | Type number : Edischarge1_todayL "Growatt_Edischarge1_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Edischarge1_todayL"] | Number:Energy Growatt_Edischarge1_todayL "Edischarge1_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Edischarge1_todayL"} | 44.,Edischarge1_todayL,Modbus RTU,,5,4,1053,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1054 | Edischarge1_totalH | Total discharge energy1 (high) |  |  | 0.1kWh |  | SPA used | BMS | 0.1 | kWh | 1 | Type number : Edischarge1_totalH "Growatt_Edischarge1_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Edischarge1_totalH"] | Number:Energy Growatt_Edischarge1_totalH "Edischarge1_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Edischarge1_totalH"} | 44.,Edischarge1_totalH,Modbus RTU,,5,4,1054,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1055 | Edischarge1_totalL | Total discharge energy1 (low) |  |  | 0.1kWh |  | SPA used | BMS | 0.1 | kWh | 1 | Type number : Edischarge1_totalL "Growatt_Edischarge1_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Edischarge1_totalL"] | Number:Energy Growatt_Edischarge1_totalL "Edischarge1_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Edischarge1_totalL"} | 44.,Edischarge1_totalL,Modbus RTU,,5,4,1055,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1056 | Echarge1_todayH | Charge1 energy today |  |  | 0.1kWh |  | Storage | BMS | 0.1 | kWh | 1 | Type number : Echarge1_todayH "Growatt_Echarge1_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Echarge1_todayH"] | Number:Energy Growatt_Echarge1_todayH "Echarge1_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Echarge1_todayH"} | 45.,Echarge1_todayH,Modbus RTU,,5,4,1056,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1057 | Echarge1_todayL | Charge1 energy today |  |  | 0.1kWh |  | reserved | BMS | 0.1 | kWh | 1 | Type number : Echarge1_todayL "Growatt_Echarge1_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Echarge1_todayL"] | Number:Energy Growatt_Echarge1_todayL "Echarge1_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Echarge1_todayL"} | 45.,Echarge1_todayL,Modbus RTU,,5,4,1057,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1058 | Echarge1_totalH | Charge1 energy total |  |  | 0.1kWh |  | self electric energy today L | BMS | 0.1 | kWh | 1 | Type number : Echarge1_totalH "Growatt_Echarge1_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Echarge1_totalH"] | Number:Energy Growatt_Echarge1_totalH "Echarge1_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Echarge1_totalH"} | 45.,Echarge1_totalH,Modbus RTU,,5,4,1058,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1059 | Echarge1_totalL | Charge1 energy total |  |  | 0.1kWh |  | self electric energy today H | BMS | 0.1 | kWh | 1 | Type number : Echarge1_totalL "Growatt_Echarge1_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Echarge1_totalL"] | Number:Energy Growatt_Echarge1_totalL "Echarge1_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Echarge1_totalL"} | 45.,Echarge1_totalL,Modbus RTU,,5,4,1059,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1060 | ElocalLoad_TodayH | Local load energy today |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : ElocalLoad_TodayH "Growatt_ElocalLoad_TodayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ElocalLoad_TodayH"] | Number:Energy Growatt_ElocalLoad_TodayH "ElocalLoad_TodayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ElocalLoad_TodayH"} | 46.,ElocalLoad_TodayH,Modbus RTU,,5,4,1060,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1061 | ElocalLoad_TodayL | Local load energy today |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : ElocalLoad_TodayL "Growatt_ElocalLoad_TodayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ElocalLoad_TodayL"] | Number:Energy Growatt_ElocalLoad_TodayL "ElocalLoad_TodayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ElocalLoad_TodayL"} | 46.,ElocalLoad_TodayL,Modbus RTU,,5,4,1061,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1062 | ElocalLoad_TotalH | Local load energy total |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : ElocalLoad_TotalH "Growatt_ElocalLoad_TotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ElocalLoad_TotalH"] | Number:Energy Growatt_ElocalLoad_TotalH "ElocalLoad_TotalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ElocalLoad_TotalH"} | 46.,ElocalLoad_TotalH,Modbus RTU,,5,4,1062,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1063 | ElocalLoad_TotalL | Local load energy total |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : ElocalLoad_TotalL "Growatt_ElocalLoad_TotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ElocalLoad_TotalL"] | Number:Energy Growatt_ElocalLoad_TotalL "ElocalLoad_TotalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ElocalLoad_TotalL"} | 46.,ElocalLoad_TotalL,Modbus RTU,,5,4,1063,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1064 | dwExportLimitApparentPower | ExportLimitApparentPower H |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : dwExportLimitApparentPower "Growatt_dwExportLimitApparentPower" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.dwExportLimitApparentPower"] | Number:Energy Growatt_dwExportLimitApparentPower "dwExportLimitApparentPower [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:dwExportLimitApparentPower"} | 46.,dwExportLimitApparentPower,Modbus RTU,,5,4,1064,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1065 | dwExportLimitApparentPower | ExportLimitApparentPower L |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : dwExportLimitApparentPower "Growatt_dwExportLimitApparentPower" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.dwExportLimitApparentPower"] | Number:Energy Growatt_dwExportLimitApparentPower "dwExportLimitApparentPower [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:dwExportLimitApparentPower"} | 46.,dwExportLimitApparentPower,Modbus RTU,,5,4,1065,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1067 | EPSFac | UPSfrequency |  | 5000/6000 | 0.01Hz |  |  | BMS | 0.01 | Hz | 2 | Type number : EPSFac "Growatt_EPSFac" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSFac"] | Number:Frequency Growatt_EPSFac "EPSFac [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSFac"} | 46.,EPSFac,Modbus RTU,,5,4,1067,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255
| 4 | 1068 | EPSVac1 | UPS phase R output voltage |  | 2300 | 0.1V |  |  | UPS | 0.1 | V | 1 | Type number : EPSVac1 "Growatt_EPSVac1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSVac1"] | Number:ElectricPotential Growatt_EPSVac1 "EPSVac1 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSVac1"} | 46.,EPSVac1,Modbus RTU,,5,4,1068,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 1069 | EPSIac1 | UPS phase R output current |  |  | 0.1A |  |  | BMS | 0.1 | A | 1 | Type number : EPSIac1 "Growatt_EPSIac1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSIac1"] | Number:ElectricCurrent Growatt_EPSIac1 "EPSIac1 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSIac1"} | 46.,EPSIac1,Modbus RTU,,5,4,1069,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 1070 | EPSPac1H | UPS phase R output power (H) |  |  | 0.1W |  |  | BMS | 0.1 | W | 1 | Type number : EPSPac1H "Growatt_EPSPac1H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac1H"] | Number:Power Growatt_EPSPac1H "EPSPac1H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac1H"} | 46.,EPSPac1H,Modbus RTU,,5,4,1070,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1071 | EPSPac1L | UPS phase R output power (L) |  |  | 0.1W |  | R SPH6K | BMS | 0.1 | W | 1 | Type number : EPSPac1L "Growatt_EPSPac1L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac1L"] | Number:Power Growatt_EPSPac1L "EPSPac1L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac1L"} | 46.,EPSPac1L,Modbus RTU,,5,4,1071,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1072 | EPSVac2 | UPS phase S output voltage |  |  | 0.1V |  |  | UPS | 0.1 | V | 1 | Type number : EPSVac2 "Growatt_EPSVac2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSVac2"] | Number:ElectricPotential Growatt_EPSVac2 "EPSVac2 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSVac2"} | 46.,EPSVac2,Modbus RTU,,5,4,1072,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 1073 | EPSIac2 | UPS phase S output current |  |  | 0.1A |  |  | BMS | 0.1 | A | 1 | Type number : EPSIac2 "Growatt_EPSIac2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSIac2"] | Number:ElectricCurrent Growatt_EPSIac2 "EPSIac2 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSIac2"} | 46.,EPSIac2,Modbus RTU,,5,4,1073,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 1074 | EPSPac2H | UPS phase S output power (H) |  |  | 0.1W |  |  | BMS | 0.1 | W | 1 | Type number : EPSPac2H "Growatt_EPSPac2H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac2H"] | Number:Power Growatt_EPSPac2H "EPSPac2H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac2H"} | 46.,EPSPac2H,Modbus RTU,,5,4,1074,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1075 | EPSPac2L | UPS phase S output power (L) |  |  | 0.1W |  |  | BMS | 0.1 | W | 1 | Type number : EPSPac2L "Growatt_EPSPac2L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac2L"] | Number:Power Growatt_EPSPac2L "EPSPac2L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac2L"} | 46.,EPSPac2L,Modbus RTU,,5,4,1075,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1076 | EPSVac3 | UPS phase T output voltage |  |  | 0.1V |  |  | UPS | 0.1 | V | 1 | Type number : EPSVac3 "Growatt_EPSVac3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSVac3"] | Number:ElectricPotential Growatt_EPSVac3 "EPSVac3 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSVac3"} | 46.,EPSVac3,Modbus RTU,,5,4,1076,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 1077 | EPSIac3 | UPS phase T output current |  |  | 0.1A |  |  | BMS | 0.1 | A | 1 | Type number : EPSIac3 "Growatt_EPSIac3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSIac3"] | Number:ElectricCurrent Growatt_EPSIac3 "EPSIac3 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSIac3"} | 46.,EPSIac3,Modbus RTU,,5,4,1077,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 1078 | EPSPac3H | UPS phase T output power (H) |  |  | 0.1W |  |  | UPS | 0.1 | W | 1 | Type number : EPSPac3H "Growatt_EPSPac3H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac3H"] | Number:Power Growatt_EPSPac3H "EPSPac3H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac3H"} | 46.,EPSPac3H,Modbus RTU,,5,4,1078,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1079 | EPSPac3L | UPS phase T output power (L) |  |  | 0.1W |  |  | UPS | 0.1 | W | 1 | Type number : EPSPac3L "Growatt_EPSPac3L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac3L"] | Number:Power Growatt_EPSPac3L "EPSPac3L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac3L"} | 46.,EPSPac3L,Modbus RTU,,5,4,1079,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1080 | Loadpercent | Load percent of UPS ouput |  | 0-100 | 0.01 |  | suggestive | ALL | 0.01 |  | 2 | Type number : Loadpercent "Growatt_Loadpercent" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Loadpercent"] | Number Growatt_Loadpercent "Loadpercent [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Loadpercent"} | 46.,Loadpercent,Modbus RTU,,5,4,1080,1,9410,2,0,Unsigned int,0,2,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1081 | PF | Power factor |  | 0-2 | 0.1 |  |  | ALL | 0.1 |  | 1 | Type number : PF "Growatt_PF" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PF"] | Number Growatt_PF "PF [%0.1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PF"} | 46.,PF,Modbus RTU,,5,4,1081,1,9410,2,0,Unsigned int,0,1,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1082 | BMS_StatusOld | StatusOld from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_StatusOld "Growatt_BMS_StatusOld" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_StatusOld"] | Number Growatt_BMS_StatusOld "BMS_StatusOld" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_StatusOld"} | 46.,BMS_StatusOld,Modbus RTU,,5,4,1082,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1083 | BMS_Status | Status from BMS | R/W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BMS_Status "Growatt_BMS_Status" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_Status"] | Number Growatt_BMS_Status "BMS_Status" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_Status"} | 47.,BMS_Status,Modbus RTU,,5,4,1083,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1084 | BMS_ErrorOld | Error info Old from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_ErrorOld "Growatt_BMS_ErrorOld" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_ErrorOld"] | Number Growatt_BMS_ErrorOld "BMS_ErrorOld" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_ErrorOld"} | 47.,BMS_ErrorOld,Modbus RTU,,5,4,1084,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1085 | BMS_Error | Errorinfomation from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_Error "Growatt_BMS_Error" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_Error"] | Number Growatt_BMS_Error "BMS_Error" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_Error"} | 48.,BMS_Error,Modbus RTU,,5,4,1085,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1086 | BMS_SOC | SOC from BMS |  |  |  |  | 1~100 | TL_X-TL_XH |  |  | 0 | Type number : BMS_SOC "Growatt_BMS_SOC" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_SOC"] | Number Growatt_BMS_SOC "BMS_SOC" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_SOC"} | 49.,BMS_SOC,Modbus RTU,,5,4,1086,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1087 | BMS_BatteryVolt | Battery voltage from BMS |  |  | 0.1V |  |  | TL_X-TL_XH | 0.1 | V | 1 | Type number : BMS_BatteryVolt "Growatt_BMS_BatteryVolt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_BatteryVolt"] | Number:ElectricPotential Growatt_BMS_BatteryVolt "BMS_BatteryVolt [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_BatteryVolt"} | 50.,BMS_BatteryVolt,Modbus RTU,,5,4,1087,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1088 | BMS_BatteryCur | Battery current from BMS |  |  | 0.1A |  |  | TL_X-TL_XH | 0.1 | A | 1 | Type number : BMS_BatteryCur "Growatt_BMS_BatteryCur" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_BatteryCur"] | Number:ElectricCurrent Growatt_BMS_BatteryCur "BMS_BatteryCur [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_BatteryCur"} | 51.,BMS_BatteryCur,Modbus RTU,,5,4,1088,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1089 | BMS_BatteryTemp | Battery temperature from BMS |  |  | 0.1°C |  |  | TL_X-TL_XH | 0.1 | °C | 1 | Type number : BMS_BatteryTemp "Growatt_BMS_BatteryTemp" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_BatteryTemp"] | Number:Temperature Growatt_BMS_BatteryTemp "BMS_BatteryTemp [%0.1f °C]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_BatteryTemp"} | 52.,BMS_BatteryTemp,Modbus RTU,,5,4,1089,1,9410,2,0,Unsigned int,0,1,°C,1,100,97,0,0,0,1.000000,0,255
| 4 | 1090 | BMS_MaxCurr | Max. charge/discharge current from BMS (pylon) |  |  |  |  | bitfield | TL_X-TL_XH |  |  | 0 | Type number : BMS_MaxCurr "Growatt_BMS_MaxCurr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_MaxCurr"] | Number Growatt_BMS_MaxCurr "BMS_MaxCurr" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_MaxCurr"} | 52.,BMS_MaxCurr,Modbus RTU,,5,4,1090,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1091 | BMS_GaugeRM | Gauge RM from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_GaugeRM "Growatt_BMS_GaugeRM" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_GaugeRM"] | Number Growatt_BMS_GaugeRM "BMS_GaugeRM" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_GaugeRM"} | 52.,BMS_GaugeRM,Modbus RTU,,5,4,1091,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1092 | BMS_GaugeFCC | Gauge FCC from BMS |  |  |  |  | 0:No BDC | TL_X-TL_XH |  |  | 0 | Type number : BMS_GaugeFCC "Growatt_BMS_GaugeFCC" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_GaugeFCC"] | Number Growatt_BMS_GaugeFCC "BMS_GaugeFCC" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_GaugeFCC"} | 52.,BMS_GaugeFCC,Modbus RTU,,5,4,1092,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1093 | BMS_FW | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_FW "Growatt_BMS_FW" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_FW"] | Number Growatt_BMS_FW "BMS_FW" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_FW"} | 52.,BMS_FW,Modbus RTU,,5,4,1093,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1094 | BMS_DeltaVolt | Delta V from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_DeltaVolt "Growatt_BMS_DeltaVolt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_DeltaVolt"] | Number Growatt_BMS_DeltaVolt "BMS_DeltaVolt" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_DeltaVolt"} | 52.,BMS_DeltaVolt,Modbus RTU,,5,4,1094,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1095 | BMS_CycleCnt | Cycle Count from BMS |  |  |  |  | Total discharge energy | TL_X-TL_XH |  |  | 0 | Type number : BMS_CycleCnt "Growatt_BMS_CycleCnt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_CycleCnt"] | Number Growatt_BMS_CycleCnt "BMS_CycleCnt" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_CycleCnt"} | 52.,BMS_CycleCnt,Modbus RTU,,5,4,1095,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1096 | BMS_SOH | SOH from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_SOH "Growatt_BMS_SOH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_SOH"] | Number Growatt_BMS_SOH "BMS_SOH" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_SOH"} | 53.,BMS_SOH,Modbus RTU,,5,4,1096,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1097 | BMS_ConstantVolt | CV voltage from BMS |  |  |  |  | Charge energy today | TL_X-TL_XH |  |  | 0 | Type number : BMS_ConstantVolt "Growatt_BMS_ConstantVolt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_ConstantVolt"] | Number Growatt_BMS_ConstantVolt "BMS_ConstantVolt" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_ConstantVolt"} | 53.,BMS_ConstantVolt,Modbus RTU,,5,4,1097,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1098 | BMS_WarnInfoOld | Warning info old from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_WarnInfoOld "Growatt_BMS_WarnInfoOld" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_WarnInfoOld"] | Number Growatt_BMS_WarnInfoOld "BMS_WarnInfoOld" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_WarnInfoOld"} | 53.,BMS_WarnInfoOld,Modbus RTU,,5,4,1098,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1099 | BMS_WarnInfo | Warning info from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_WarnInfo "Growatt_BMS_WarnInfo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_WarnInfo"] | Number Growatt_BMS_WarnInfo "BMS_WarnInfo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_WarnInfo"} | 54.,BMS_WarnInfo,Modbus RTU,,5,4,1099,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1100 | BMS_GaugeICCurrrr | Gauge IC current from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_GaugeICCurrrr "Growatt_BMS_GaugeICCurrrr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_GaugeICCurrrr"] | Number Growatt_BMS_GaugeICCurrrr "BMS_GaugeICCurrrr" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_GaugeICCurrrr"} | 54.,BMS_GaugeICCurrrr,Modbus RTU,,5,4,1100,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1101 | BMS_MCUVersion | MCU Software version from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_MCUVersion "Growatt_BMS_MCUVersion" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_MCUVersion"] | Number Growatt_BMS_MCUVersion "BMS_MCUVersion" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_MCUVersion"} | 54.,BMS_MCUVersion,Modbus RTU,,5,4,1101,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1102 | BMS_GaugeVersion | Gauge Version from BMS |  |  |  |  | inv start delay time | TL_X-TL_XH |  |  | 0 | Type number : BMS_GaugeVersion "Growatt_BMS_GaugeVersion" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_GaugeVersion"] | Number Growatt_BMS_GaugeVersion "BMS_GaugeVersion" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_GaugeVersion"} | 54.,BMS_GaugeVersion,Modbus RTU,,5,4,1102,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1103 | BMS_wGaugeFRVersion_L | Gauge FR Version L16 from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_wGaugeFRVersion_L "Growatt_BMS_wGaugeFRVersion_L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_wGaugeFRVersion_L"] | Number Growatt_BMS_wGaugeFRVersion_L "BMS_wGaugeFRVersion_L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_wGaugeFRVersion_L"} | 54.,BMS_wGaugeFRVersion_L,Modbus RTU,,5,4,1103,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1104 | BMS_wGaugeFRVersion_H | Gauge FR Version H16 from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_wGaugeFRVersion_H "Growatt_BMS_wGaugeFRVersion_H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_wGaugeFRVersion_H"] | Number Growatt_BMS_wGaugeFRVersion_H "BMS_wGaugeFRVersion_H" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_wGaugeFRVersion_H"} | 54.,BMS_wGaugeFRVersion_H,Modbus RTU,,5,4,1104,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1105 | BMS_BMSInfo | BMSInformation from BMS |  |  |  |  | Charge energy total | TL_X-TL_XH |  |  | 0 | Type number : BMS_BMSInfo "Growatt_BMS_BMSInfo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_BMSInfo"] | Number Growatt_BMS_BMSInfo "BMS_BMSInfo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_BMSInfo"} | 55.,BMS_BMSInfo,Modbus RTU,,5,4,1105,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1106 | BMS_PackInfo | Pack Information from BMS |  |  |  |  | bitfield | TL_X-TL_XH |  |  | 0 | Type number : BMS_PackInfo "Growatt_BMS_PackInfo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_PackInfo"] | Number Growatt_BMS_PackInfo "BMS_PackInfo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_PackInfo"} | 55.,BMS_PackInfo,Modbus RTU,,5,4,1106,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1107 | BMS_UsingCap | Using Cap from BMS | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_UsingCap "Growatt_BMS_UsingCap" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_UsingCap"] | Number Growatt_BMS_UsingCap "BMS_UsingCap" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_UsingCap"} | 55.,BMS_UsingCap,Modbus RTU,,5,4,1107,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1108 | uwMaxCellVolt | Maximum single battery voltage |  |  | 0.001V |  | UL | ALL | 0.001 | V | 3 | Type number : uwMaxCellVolt "Growatt_uwMaxCellVolt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwMaxCellVolt"] | Number:ElectricPotential Growatt_uwMaxCellVolt "uwMaxCellVolt [%0.001f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwMaxCellVolt"} | 56.,uwMaxCellVolt,Modbus RTU,,5,4,1108,1,9410,2,0,Unsigned int,0,3,V,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1109 | uwMinCellVolt | Lowest single battery voltage |  |  | 0.001V |  | UL | ALL | 0.001 | V | 3 | Type number : uwMinCellVolt "Growatt_uwMinCellVolt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwMinCellVolt"] | Number:ElectricPotential Growatt_uwMinCellVolt "uwMinCellVolt [%0.001f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwMinCellVolt"} | 57.,uwMinCellVolt,Modbus RTU,,5,4,1109,1,9410,2,0,Unsigned int,0,3,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 1110 | bModuleNum | Battery parallel number |  |  | 1 |  |  | TL_X-TL_XH | 1 |  | 0 | Type number : bModuleNum "Growatt_bModuleNum" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.bModuleNum"] | Number Growatt_bModuleNum "bModuleNum [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bModuleNum"} | 57.,bModuleNum,Modbus RTU,,5,4,1110,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1112 | uwMaxVoltCellNo | MaxVoltCellNo |  |  | 1 |  | UL | ALL | 1 |  | 0 | Type number : uwMaxVoltCellNo "Growatt_uwMaxVoltCellNo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwMaxVoltCellNo"] | Number Growatt_uwMaxVoltCellNo "uwMaxVoltCellNo [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwMaxVoltCellNo"} | 57.,uwMaxVoltCellNo,Modbus RTU,,5,4,1112,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1113 | uwMinVoltCellNo | MinVoltCellNo |  |  | 1 |  | UL | ALL | 1 |  | 0 | Type number : uwMinVoltCellNo "Growatt_uwMinVoltCellNo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwMinVoltCellNo"] | Number Growatt_uwMinVoltCellNo "uwMinVoltCellNo [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwMinVoltCellNo"} | 57.,uwMinVoltCellNo,Modbus RTU,,5,4,1113,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1114 | uwMaxTemprCell_10T | MaxTemprCell_10T |  |  | 0.1? |  | UL | ALL | 0.1 | ? | 1 | Type number : uwMaxTemprCell_10T "Growatt_uwMaxTemprCell_10T" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwMaxTemprCell_10T"] | Number:Length Growatt_uwMaxTemprCell_10T "uwMaxTemprCell_10T [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwMaxTemprCell_10T"} | 57.,uwMaxTemprCell_10T,Modbus RTU,,5,4,1114,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
| 4 | 1115 | uwMinTemprCell_10T | MinTemprCell_10T |  |  | 0.1? |  | UL | ALL | 0.1 | ? | 1 | Type number : uwMinTemprCell_10T "Growatt_uwMinTemprCell_10T" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwMinTemprCell_10T"] | Number:Length Growatt_uwMinTemprCell_10T "uwMinTemprCell_10T [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwMinTemprCell_10T"} | 57.,uwMinTemprCell_10T,Modbus RTU,,5,4,1115,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
| 4 | 1116 | uwMaxTemprCellNo | MaxVoltTemprCellNo |  |  | 1 |  | UL | ALL | 1 |  | 0 | Type number : uwMaxTemprCellNo "Growatt_uwMaxTemprCellNo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwMaxTemprCellNo"] | Number Growatt_uwMaxTemprCellNo "uwMaxTemprCellNo [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwMaxTemprCellNo"} | 57.,uwMaxTemprCellNo,Modbus RTU,,5,4,1116,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1117 | uwMinTemprCellNo | MinVoltTemprCellNo |  |  | 1 |  | UL | ALL | 1 |  | 0 | Type number : uwMinTemprCellNo "Growatt_uwMinTemprCellNo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwMinTemprCellNo"] | Number Growatt_uwMinTemprCellNo "uwMinTemprCellNo [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwMinTemprCellNo"} | 57.,uwMinTemprCellNo,Modbus RTU,,5,4,1117,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1118 | ProtectpackID | Faulty Battery Address |  |  | 1 |  | ASCII | TL_X-TL_XH | 1 |  | 0 | Type number : ProtectpackID "Growatt_ProtectpackID" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ProtectpackID"] | Number Growatt_ProtectpackID "ProtectpackID [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ProtectpackID"} | 57.,ProtectpackID,Modbus RTU,,5,4,1118,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1119 | MaxSOC | Parallel maximum SOC |  |  | 0.01 |  |  | ALL | 0.01 |  | 2 | Type number : MaxSOC "Growatt_MaxSOC" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MaxSOC"] | Number Growatt_MaxSOC "MaxSOC [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MaxSOC"} | 57.,MaxSOC,Modbus RTU,,5,4,1119,1,9410,2,0,Unsigned int,0,2,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1120 | MinSOC | Parallel minimum SOC |  |  | 0.01 |  |  | ALL | 0.01 |  | 2 | Type number : MinSOC "Growatt_MinSOC" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MinSOC"] | Number Growatt_MinSOC "MinSOC [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MinSOC"} | 57.,MinSOC,Modbus RTU,,5,4,1120,1,9410,2,0,Unsigned int,0,2,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1121 | BMS_Error2 | Battery Protection 2 | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_Error2 "Growatt_BMS_Error2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_Error2"] | Number Growatt_BMS_Error2 "BMS_Error2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_Error2"} | 57.,BMS_Error2,Modbus RTU,,5,4,1121,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1122 | BMS_Error3 | Battery Protection3 | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_Error3 "Growatt_BMS_Error3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_Error3"] | Number Growatt_BMS_Error3 "BMS_Error3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_Error3"} | 57.,BMS_Error3,Modbus RTU,,5,4,1122,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1123 | BMS_WarnInfo2 | Battery Warn2 | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BMS_WarnInfo2 "Growatt_BMS_WarnInfo2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_WarnInfo2"] | Number Growatt_BMS_WarnInfo2 "BMS_WarnInfo2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_WarnInfo2"} | 57.,BMS_WarnInfo2,Modbus RTU,,5,4,1123,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1124 | ACChargeEnergyTodayH | AC Charge Energy today kWh |  |  | 0.1kWh |  |  | TL_X-TL_XH | 0.1 | kWh | 1 | Type number : ACChargeEnergyTodayH "Growatt_ACChargeEnergyTodayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ACChargeEnergyTodayH"] | Number:Energy Growatt_ACChargeEnergyTodayH "ACChargeEnergyTodayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ACChargeEnergyTodayH"} | 58.,ACChargeEnergyTodayH,Modbus RTU,,5,4,1124,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1125 | ACChargeEnergyTodayL | AC Charge Energy today kWh |  |  | 0.1kWh |  |  | TL_X-TL_XH | 0.1 | kWh | 1 | Type number : ACChargeEnergyTodayL "Growatt_ACChargeEnergyTodayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ACChargeEnergyTodayL"] | Number:Energy Growatt_ACChargeEnergyTodayL "ACChargeEnergyTodayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ACChargeEnergyTodayL"} | 58.,ACChargeEnergyTodayL,Modbus RTU,,5,4,1125,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1126 | ACChargeEnergyTotalH | Energy total | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : ACChargeEnergyTotalH "Growatt_ACChargeEnergyTotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ACChargeEnergyTotalH"] | Number Growatt_ACChargeEnergyTotalH "ACChargeEnergyTotalH" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ACChargeEnergyTotalH"} | 58.,ACChargeEnergyTotalH,Modbus RTU,,5,4,1126,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1127 | ACChargeEnergyTotalL | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : ACChargeEnergyTotalL "Growatt_ACChargeEnergyTotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ACChargeEnergyTotalL"] | Number Growatt_ACChargeEnergyTotalL "ACChargeEnergyTotalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ACChargeEnergyTotalL"} | 58.,ACChargeEnergyTotalL,Modbus RTU,,5,4,1127,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1128 | ACChargePowerH | AC Charge Power | W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : ACChargePowerH "Growatt_ACChargePowerH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ACChargePowerH"] | Number Growatt_ACChargePowerH "ACChargePowerH" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ACChargePowerH"} | 59.,ACChargePowerH,Modbus RTU,,5,4,1128,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1129 | ACChargePowerL | AC Charge Power | W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : ACChargePowerL "Growatt_ACChargePowerL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ACChargePowerL"] | Number Growatt_ACChargePowerL "ACChargePowerL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ACChargePowerL"} | 59.,ACChargePowerL,Modbus RTU,,5,4,1129,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1130 | 70PctINVPoweradjust | uwGridPower_70_AdjEE_SP | W |  |  |  |  | BDC |  |  | 0 | Type number : 70PctINVPoweradjust "Growatt_70PctINVPoweradjust" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.70PctINVPoweradjust"] | Number Growatt_70PctINVPoweradjust "70PctINVPoweradjust" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:70PctINVPoweradjust"} | 59.,70PctINVPoweradjust,Modbus RTU,,5,4,1130,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1131 | ExtraACPowertogrid_H | Extra inverte AC Power to grid | [5 empty] | PV9_32 |  |  | 0 | Type number : ExtraACPowertogrid_H "Growatt_ExtraACPowertogrid_H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ExtraACPowertogrid_H"] | Number Growatt_ExtraACPowertogrid_H "ExtraACPowertogrid_H" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ExtraACPowertogrid_H"} | 59.,ExtraACPowertogrid_H,Modbus RTU,,5,4,1131,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1132 | ExtraACPowertogrid_L | Extrainverte AC Power to grid Low | [5 empty] | PV9_32 |  |  | 0 | Type number : ExtraACPowertogrid_L "Growatt_ExtraACPowertogrid_L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ExtraACPowertogrid_L"] | Number Growatt_ExtraACPowertogrid_L "ExtraACPowertogrid_L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ExtraACPowertogrid_L"} | 59.,ExtraACPowertogrid_L,Modbus RTU,,5,4,1132,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1133 | Eextra_todayH | Extra inverter PowerTOUser_Extra today (high) | R |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eextra_todayH "Growatt_Eextra_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eextra_todayH"] | Number:Energy Growatt_Eextra_todayH "Eextra_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eextra_todayH"} | 59.,Eextra_todayH,Modbus RTU,,5,4,1133,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1134 | Eextra_todayL | Extra inverter PowerTOUser_Extra today (low) | R |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eextra_todayL "Growatt_Eextra_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eextra_todayL"] | Number:Energy Growatt_Eextra_todayL "Eextra_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eextra_todayL"} | 59.,Eextra_todayL,Modbus RTU,,5,4,1134,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1135 | Eextra_totalH | Extra inverter PowerTOUser_Extra total(high) |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eextra_totalH "Growatt_Eextra_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eextra_totalH"] | Number:Energy Growatt_Eextra_totalH "Eextra_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eextra_totalH"} | 59.,Eextra_totalH,Modbus RTU,,5,4,1135,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1136 | Eextra_totalL | Extra inverter PowerTOUser_Extra total(low) |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eextra_totalL "Growatt_Eextra_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eextra_totalL"] | Number:Energy Growatt_Eextra_totalL "Eextra_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eextra_totalL"} | 59.,Eextra_totalL,Modbus RTU,,5,4,1136,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1137 | Esystem_today | System electric energy today H |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Esystem_today "Growatt_Esystem_today" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esystem_today"] | Number:Energy Growatt_Esystem_today "Esystem_today [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esystem_today"} | 60.,Esystem_today,Modbus RTU,,5,4,1137,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1138 | Esystem_today | System electric energy today L |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Esystem_today "Growatt_Esystem_today" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esystem_today"] | Number:Energy Growatt_Esystem_today "Esystem_today [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esystem_today"} | 60.,Esystem_today,Modbus RTU,,5,4,1138,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1139 | Esystem_totalH | System electric energy total H |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Esystem_totalH "Growatt_Esystem_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esystem_totalH"] | Number:Energy Growatt_Esystem_totalH "Esystem_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esystem_totalH"} | 60.,Esystem_totalH,Modbus RTU,,5,4,1139,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1140 | Esystem_totalL | System electric energy total L |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Esystem_totalL "Growatt_Esystem_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esystem_totalL"] | Number:Energy Growatt_Esystem_totalL "Esystem_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esystem_totalL"} | 60.,Esystem_totalL,Modbus RTU,,5,4,1140,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1141 | Eself_todayH | self electric energy today H |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Eself_todayH "Growatt_Eself_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eself_todayH"] | Number:Energy Growatt_Eself_todayH "Eself_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eself_todayH"} | 61.,Eself_todayH,Modbus RTU,,5,4,1141,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1142 | Eself_todayL | self electric energy today L |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Eself_todayL "Growatt_Eself_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eself_todayL"] | Number:Energy Growatt_Eself_todayL "Eself_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eself_todayL"} | 61.,Eself_todayL,Modbus RTU,,5,4,1142,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1143 | Eself_totalH | self electric energy total H |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Eself_totalH "Growatt_Eself_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eself_totalH"] | Number:Energy Growatt_Eself_totalH "Eself_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eself_totalH"} | 61.,Eself_totalH,Modbus RTU,,5,4,1143,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1144 | Eself_totalL | self electric energy total L |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Eself_totalL "Growatt_Eself_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eself_totalL"] | Number:Energy Growatt_Eself_totalL "Eself_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eself_totalL"} | 61.,Eself_totalL,Modbus RTU,,5,4,1144,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1145 | PSystemH | System power H |  |  | 0.1W |  | ratio | TL_X-TL_XH | 0.1 | W | 1 | Type number : PSystemH "Growatt_PSystemH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PSystemH"] | Number:Power Growatt_PSystemH "PSystemH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PSystemH"} | 62.,PSystemH,Modbus RTU,,5,4,1145,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1146 | PSystemL | System power L |  |  | 0.1W |  | 0:50Hz | TL_X-TL_XH | 0.1 | W | 1 | Type number : PSystemL "Growatt_PSystemL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PSystemL"] | Number:Power Growatt_PSystemL "PSystemL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PSystemL"} | 62.,PSystemL,Modbus RTU,,5,4,1146,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1147 | PSelfH | self power H |  |  | 0.1W |  | ASCII | TL_X-TL_XH | 0.1 | W | 1 | Type number : PSelfH "Growatt_PSelfH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PSelfH"] | Number:Power Growatt_PSelfH "PSelfH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PSelfH"} | 63.,PSelfH,Modbus RTU,,5,4,1147,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 1148 | PSelfL | self power L |  |  | 0.1W |  | 1 : Communication addr=1 | TL_X-TL_XH | 0.1 | W | 1 | Type number : PSelfL "Growatt_PSelfL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PSelfL"] | Number:Power Growatt_PSelfL "PSelfL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PSelfL"} | 63.,PSelfL,Modbus RTU,,5,4,1148,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
X | 4 | 1149 | EPVAll_TodayH | PV electric energy today H |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : EPVAll_TodayH "Growatt_EPVAll_TodayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPVAll_TodayH"] | Number:Energy Growatt_EPVAll_TodayH "EPVAll_TodayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPVAll_TodayH"} | 64.,EPVAll_TodayH,Modbus RTU,,5,4,1149,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 1150 | EPVAll_TodayL | PV electric energy today L | [5 empty] | PV9_32 |  |  | 0 | Type number : EPVAll_TodayL "Growatt_EPVAll_TodayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPVAll_TodayL"] | Number Growatt_EPVAll_TodayL "EPVAll_TodayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPVAll_TodayL"} | 64.,EPVAll_TodayL,Modbus RTU,,5,4,1150,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1151 | AcDischargePackSn | Discharge number power pack serial | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : AcDischargePackSn "Growatt_AcDischargePackSn" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.AcDischargePackSn"] | Number Growatt_AcDischargePackSn "AcDischargePackSn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AcDischargePackSn"} | 64.,AcDischargePackSn,Modbus RTU,,5,4,1151,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1152 | Accdischargepower_H | Cumulativedischarge power high | R | 0,1 | kWH |  |  | TL_X-TL_XH |  | kWH | 0 | Type number : Accdischargepower_H "Growatt_Accdischargepower_H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Accdischargepower_H"] | Number:Energy Growatt_Accdischargepower_H "Accdischargepower_H" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Accdischargepower_H"} | 64.,Accdischargepower_H,Modbus RTU,,5,4,1152,1,9410,4,0,Unsigned int,0,0,kWH,1,100,97,0,0,0,1.000000,0,255
| 4 | 1153 | Accdischargepower_L | Cumulativedischarge power low | R | 0,1 | kWH |  |  | TL_X-TL_XH |  | kWH | 0 | Type number : Accdischargepower_L "Growatt_Accdischargepower_L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Accdischargepower_L"] | Number:Energy Growatt_Accdischargepower_L "Accdischargepower_L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Accdischargepower_L"} | 64.,Accdischargepower_L,Modbus RTU,,5,4,1153,1,9410,4,0,Unsigned int,0,0,kWH,1,100,97,0,0,0,1.000000,0,255
| 4 | 1154 | AccChargePackSn | charge power pack serial number | R |  |  |  |  | BDC |  |  | 0 | Type number : AccChargePackSn "Growatt_AccChargePackSn" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.AccChargePackSn"] | Number Growatt_AccChargePackSn "AccChargePackSn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AccChargePackSn"} | 64.,AccChargePackSn,Modbus RTU,,5,4,1154,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1155 | AccChargepower_H | Cumulative charge power H | R | 0,1 | kWH |  |  | BDC |  | kWH | 0 | Type number : AccChargepower_H "Growatt_AccChargepower_H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.AccChargepower_H"] | Number:Energy Growatt_AccChargepower_H "AccChargepower_H" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AccChargepower_H"} | 64.,AccChargepower_H,Modbus RTU,,5,4,1155,1,9410,4,0,Unsigned int,0,0,kWH,1,100,97,0,0,0,1.000000,0,255
| 4 | 1156 | AccChargepower_L | Cumulative charge power L | R | 0,1 | kWH |  |  | BDC |  | kWH | 0 | Type number : AccChargepower_L "Growatt_AccChargepower_L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.AccChargepower_L"] | Number:Energy Growatt_AccChargepower_L "AccChargepower_L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AccChargepower_L"} | 64.,AccChargepower_L,Modbus RTU,,5,4,1156,1,9410,4,0,Unsigned int,0,0,kWH,1,100,97,0,0,0,1.000000,0,255
| 4 | 1157 | FirstBattFaultSn | FirstBattFaultSn | R |  |  |  |  | PV9_32 |  |  | 0 | Type number : FirstBattFaultSn "Growatt_FirstBattFaultSn" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.FirstBattFaultSn"] | Number Growatt_FirstBattFaultSn "FirstBattFaultSn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FirstBattFaultSn"} | 64.,FirstBattFaultSn,Modbus RTU,,5,4,1157,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1158 | Second | Second | R |  |  |  | Bat First | Storage |  |  | 0 | Type number : Second "Growatt_Second" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Second"] | Number Growatt_Second "Second" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Second"} | 64.,Second,Modbus RTU,,5,4,1158,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1159 | Third | Third | R |  |  |  | 0:No self check | ALL |  |  | 0 | Type number : Third "Growatt_Third" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Third"] | Number Growatt_Third "Third" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Third"} | 64.,Third,Modbus RTU,,5,4,1159,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1160 | Fourth | Fourth | R |  |  |  |  | PV9_32 |  |  | 0 | Type number : Fourth "Growatt_Fourth" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Fourth"] | Number Growatt_Fourth "Fourth" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Fourth"} | 64.,Fourth,Modbus RTU,,5,4,1160,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1161 | Batteryhistoryfaultcode1 | Battery history fault code 1 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : Batteryhistoryfaultcode1 "Growatt_Batteryhistoryfaultcode1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Batteryhistoryfaultcode1"] | Number Growatt_Batteryhistoryfaultcode1 "Batteryhistoryfaultcode1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Batteryhistoryfaultcode1"} | 64.,Batteryhistoryfaultcode1,Modbus RTU,,5,4,1161,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1162 | Batteryhistoryfaultcode2 | Battery history fault code 2 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : Batteryhistoryfaultcode2 "Growatt_Batteryhistoryfaultcode2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Batteryhistoryfaultcode2"] | Number Growatt_Batteryhistoryfaultcode2 "Batteryhistoryfaultcode2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Batteryhistoryfaultcode2"} | 64.,Batteryhistoryfaultcode2,Modbus RTU,,5,4,1162,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1163 | Batteryhistoryfaultcode3 | Battery history fault code 3 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : Batteryhistoryfaultcode3 "Growatt_Batteryhistoryfaultcode3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Batteryhistoryfaultcode3"] | Number Growatt_Batteryhistoryfaultcode3 "Batteryhistoryfaultcode3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Batteryhistoryfaultcode3"} | 64.,Batteryhistoryfaultcode3,Modbus RTU,,5,4,1163,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1164 | Batteryhistoryfaultcode4 | Battery history fault code 4 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : Batteryhistoryfaultcode4 "Growatt_Batteryhistoryfaultcode4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Batteryhistoryfaultcode4"] | Number Growatt_Batteryhistoryfaultcode4 "Batteryhistoryfaultcode4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Batteryhistoryfaultcode4"} | 64.,Batteryhistoryfaultcode4,Modbus RTU,,5,4,1164,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1165 | Batteryhistoryfaultcode5 | Battery history fault code 5 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : Batteryhistoryfaultcode5 "Growatt_Batteryhistoryfaultcode5" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Batteryhistoryfaultcode5"] | Number Growatt_Batteryhistoryfaultcode5 "Batteryhistoryfaultcode5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Batteryhistoryfaultcode5"} | 64.,Batteryhistoryfaultcode5,Modbus RTU,,5,4,1165,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1166 | Batteryhistoryfaultcode6 | Battery history fault code 6 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : Batteryhistoryfaultcode6 "Growatt_Batteryhistoryfaultcode6" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Batteryhistoryfaultcode6"] | Number Growatt_Batteryhistoryfaultcode6 "Batteryhistoryfaultcode6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Batteryhistoryfaultcode6"} | 64.,Batteryhistoryfaultcode6,Modbus RTU,,5,4,1166,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1167 | Batteryhistoryfaultcode7 | Battery history fault code 7 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : Batteryhistoryfaultcode7 "Growatt_Batteryhistoryfaultcode7" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Batteryhistoryfaultcode7"] | Number Growatt_Batteryhistoryfaultcode7 "Batteryhistoryfaultcode7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Batteryhistoryfaultcode7"} | 64.,Batteryhistoryfaultcode7,Modbus RTU,,5,4,1167,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1168 | Batteryhistoryfaultcode8 | Battery history fault code 8 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : Batteryhistoryfaultcode8 "Growatt_Batteryhistoryfaultcode8" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Batteryhistoryfaultcode8"] | Number Growatt_Batteryhistoryfaultcode8 "Batteryhistoryfaultcode8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Batteryhistoryfaultcode8"} | 64.,Batteryhistoryfaultcode8,Modbus RTU,,5,4,1168,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1169 | Numberofbatterycodes | Number of battery codes PACK number + BIC forward and | R |  |  |  |  | ALL |  |  | 0 | Type number : Numberofbatterycodes "Growatt_Numberofbatterycodes" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Numberofbatterycodes"] | Number Growatt_Numberofbatterycodes "Numberofbatterycodes" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Numberofbatterycodes"} | 64.,Numberofbatterycodes,Modbus RTU,,5,4,1169,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1199 | NewEPowerCalcFlag | Intelligent reading is used to identify software compatibility features | [5 empty] | ALL |  |  | 0 | Type number : NewEPowerCalcFlag "Growatt_NewEPowerCalcFlag" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.NewEPowerCalcFlag"] | Number Growatt_NewEPowerCalcFlag "NewEPowerCalcFlag" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewEPowerCalcFlag"} | 64.,NewEPowerCalcFlag,Modbus RTU,,5,4,1199,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1200 | MaxCellVolt | Maximum cell voltage | R |  | 0.001V |  |  | ALL | 0.001 | V | 3 | Type number : MaxCellVolt "Growatt_MaxCellVolt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MaxCellVolt"] | Number:ElectricPotential Growatt_MaxCellVolt "MaxCellVolt [%0.001f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MaxCellVolt"} | 64.,MaxCellVolt,Modbus RTU,,5,4,1200,1,9410,2,0,Unsigned int,0,3,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 1201 | MinCellVolt | Minimum cell voltage | R |  | 0.001V |  |  | ALL | 0.001 | V | 3 | Type number : MinCellVolt "Growatt_MinCellVolt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MinCellVolt"] | Number:ElectricPotential Growatt_MinCellVolt "MinCellVolt [%0.001f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MinCellVolt"} | 64.,MinCellVolt,Modbus RTU,,5,4,1201,1,9410,2,0,Unsigned int,0,3,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 1202 | ModuleNum | Number of Battery modules | R |  |  |  |  | ALL |  |  | 0 | Type number : ModuleNum "Growatt_ModuleNum" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ModuleNum"] | Number Growatt_ModuleNum "ModuleNum" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ModuleNum"} | 64.,ModuleNum,Modbus RTU,,5,4,1202,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1203 | TotalCellNum | Total number of cells | R |  |  |  |  | ALL |  |  | 0 | Type number : TotalCellNum "Growatt_TotalCellNum" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.TotalCellNum"] | Number Growatt_TotalCellNum "TotalCellNum" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TotalCellNum"} | 64.,TotalCellNum,Modbus RTU,,5,4,1203,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1204 | MaxVoltCellNo | MaxVoltCellNo | R |  |  |  |  | ALL |  |  | 0 | Type number : MaxVoltCellNo "Growatt_MaxVoltCellNo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MaxVoltCellNo"] | Number Growatt_MaxVoltCellNo "MaxVoltCellNo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MaxVoltCellNo"} | 64.,MaxVoltCellNo,Modbus RTU,,5,4,1204,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1205 | MinVoltCellNo | MinVoltCellNo | R |  |  |  |  | ALL |  |  | 0 | Type number : MinVoltCellNo "Growatt_MinVoltCellNo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MinVoltCellNo"] | Number Growatt_MinVoltCellNo "MinVoltCellNo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MinVoltCellNo"} | 64.,MinVoltCellNo,Modbus RTU,,5,4,1205,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1206 | MaxTemprCell_10T |  | R |  | 0.1? |  |  | ALL | 0.1 | ? | 1 | Type number : MaxTemprCell_10T "Growatt_MaxTemprCell_10T" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MaxTemprCell_10T"] | Number:Length Growatt_MaxTemprCell_10T "MaxTemprCell_10T [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MaxTemprCell_10T"} | 64.,MaxTemprCell_10T,Modbus RTU,,5,4,1206,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
| 4 | 1207 | MinTemprCell_10T |  | R |  | 0.1? |  |  | ALL | 0.1 | ? | 1 | Type number : MinTemprCell_10T "Growatt_MinTemprCell_10T" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MinTemprCell_10T"] | Number:Length Growatt_MinTemprCell_10T "MinTemprCell_10T [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MinTemprCell_10T"} | 64.,MinTemprCell_10T,Modbus RTU,,5,4,1207,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
| 4 | 1208 | MaxTemprCellNo | MaxTemprCellNo | R |  |  |  |  | ALL |  |  | 0 | Type number : MaxTemprCellNo "Growatt_MaxTemprCellNo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MaxTemprCellNo"] | Number Growatt_MaxTemprCellNo "MaxTemprCellNo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MaxTemprCellNo"} | 64.,MaxTemprCellNo,Modbus RTU,,5,4,1208,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1209 | MinTemprCellNo | MinTemprCellNo | R |  |  |  |  | ALL |  |  | 0 | Type number : MinTemprCellNo "Growatt_MinTemprCellNo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MinTemprCellNo"] | Number Growatt_MinTemprCellNo "MinTemprCellNo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MinTemprCellNo"} | 64.,MinTemprCellNo,Modbus RTU,,5,4,1209,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1210 | ProtectPackID | Fault Pack ID | R |  |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : ProtectPackID "Growatt_ProtectPackID" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ProtectPackID"] | Number Growatt_ProtectPackID "ProtectPackID" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ProtectPackID"} | 64.,ProtectPackID,Modbus RTU,,5,4,1210,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1211 | MaxSOC | Parallel maximum SOC | R | 0,01 |  |  |  | ALL |  |  | 0 | Type number : MaxSOC "Growatt_MaxSOC" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MaxSOC"] | Number Growatt_MaxSOC "MaxSOC" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MaxSOC"} | 64.,MaxSOC,Modbus RTU,,5,4,1211,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1212 | MinSOC | Parallel minimum SOC | R | 0,01 |  |  |  | ALL |  |  | 0 | Type number : MinSOC "Growatt_MinSOC" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.MinSOC"] | Number Growatt_MinSOC "MinSOC" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MinSOC"} | 64.,MinSOC,Modbus RTU,,5,4,1212,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1213 | BatProtect1Add | BatProtect1Add | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatProtect1Add "Growatt_BatProtect1Add" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatProtect1Add"] | Number Growatt_BatProtect1Add "BatProtect1Add" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatProtect1Add"} | 64.,BatProtect1Add,Modbus RTU,,5,4,1213,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1214 | BatProtect2Add | BatProtect2Add | R |  |  |  | 0:Not | TL_X-TL_XH |  |  | 0 | Type number : BatProtect2Add "Growatt_BatProtect2Add" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatProtect2Add"] | Number Growatt_BatProtect2Add "BatProtect2Add" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatProtect2Add"} | 64.,BatProtect2Add,Modbus RTU,,5,4,1214,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1215 | BatWarn1Add | BatWarn1Add | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatWarn1Add "Growatt_BatWarn1Add" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatWarn1Add"] | Number Growatt_BatWarn1Add "BatWarn1Add" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatWarn1Add"} | 64.,BatWarn1Add,Modbus RTU,,5,4,1215,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1216 | BMS_HighestSoftVersion | BMS_HighestSoftVersion | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BMS_HighestSoftVersion "Growatt_BMS_HighestSoftVersion" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_HighestSoftVersion"] | Number Growatt_BMS_HighestSoftVersion "BMS_HighestSoftVersion" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_HighestSoftVersion"} | 64.,BMS_HighestSoftVersion,Modbus RTU,,5,4,1216,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1217 | BMS_Hardware | BMS_HardwareVersion | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BMS_Hardware "Growatt_BMS_Hardware" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_Hardware"] | Number Growatt_BMS_Hardware "BMS_Hardware" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_Hardware"} | 64.,BMS_Hardware,Modbus RTU,,5,4,1217,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1218 | BMS_RequestType | BMS_RequestType | R |  |  |  | Limited | TL_X-TL_XH |  |  | 0 | Type number : BMS_RequestType "Growatt_BMS_RequestType" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_RequestType"] | Number Growatt_BMS_RequestType "BMS_RequestType" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_RequestType"} | 64.,BMS_RequestType,Modbus RTU,,5,4,1218,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 1248 | bKeyAgingTestOkFlag | Success sign of key detection before aging |  | 1:Finished test |  |  | 0 LoadFirst 1 | TL_X-TL_XH |  |  | 0 | Type number : bKeyAgingTestOkFlag "Growatt_bKeyAgingTestOkFlag" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.bKeyAgingTestOkFlag"] | Number Growatt_bKeyAgingTestOkFlag "bKeyAgingTestOkFlag" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bKeyAgingTestOkFlag"} | 64.,bKeyAgingTestOkFlag,Modbus RTU,,5,4,1248,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 2000 | InverterStatus | Inverter run state |  | 0:waiting, |  |  |  | ALL |  |  | 0 | Type number : InverterStatus "Growatt_InverterStatus" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.InverterStatus"] | Number Growatt_InverterStatus "InverterStatus" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:InverterStatus"} | 64.,InverterStatus,Modbus RTU,,5,4,2000,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 2035 | PacH | Output power (high) |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PacH "Growatt_PacH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PacH"] | Number:Power Growatt_PacH "PacH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PacH"} | 64.,PacH,Modbus RTU,,5,4,2035,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 2036 | PacL | Output power (low) |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PacL "Growatt_PacL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PacL"] | Number:Power Growatt_PacL "PacL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PacL"} | 64.,PacL,Modbus RTU,,5,4,2036,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 2037 | Fac | Grid frequency |  |  | 0.01Hz |  |  | PV9_32 | 0.01 | Hz | 2 | Type number : Fac "Growatt_Fac" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Fac"] | Number:Frequency Growatt_Fac "Fac [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Fac"} | 64.,Fac,Modbus RTU,,5,4,2037,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255
| 4 | 2038 | Vac1 | Three/single phase grid voltage |  |  | 0.1V |  | ASCII | ALL | 0.1 | V | 1 | Type number : Vac1 "Growatt_Vac1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac1"] | Number:ElectricPotential Growatt_Vac1 "Vac1 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac1"} | 64.,Vac1,Modbus RTU,,5,4,2038,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 2039 | Iac1 | Three/single phase grid output current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Iac1 "Growatt_Iac1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Iac1"] | Number:ElectricCurrent Growatt_Iac1 "Iac1 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Iac1"} | 64.,Iac1,Modbus RTU,,5,4,2039,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 2040 | Pac1H | Three/single phase grid output watt |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac1H "Growatt_Pac1H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac1H"] | Number:Power Growatt_Pac1H "Pac1H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac1H"} | 64.,Pac1H,Modbus RTU,,5,4,2040,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 2041 | Pac1L | Three/single phase grid output watt |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac1L "Growatt_Pac1L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac1L"] | Number:Power Growatt_Pac1L "Pac1L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac1L"} | 64.,Pac1L,Modbus RTU,,5,4,2041,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 2053 | EactodayH | Today generate energy (high) |  |  | 0.1kWH |  |  | BMS | 0.1 | kWH | 1 | Type number : EactodayH "Growatt_EactodayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactodayH"] | Number:Energy Growatt_EactodayH "EactodayH [%0.1f kWH]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactodayH"} | 64.,EactodayH,Modbus RTU,,5,4,2053,1,9410,4,0,Unsigned int,0,1,kWH,1,100,97,0,0,0,1.000000,0,255
| 4 | 2054 | EactodayL | Today generate energy (low) |  |  | 0.1kWH |  |  | BMS | 0.1 | kWH | 1 | Type number : EactodayL "Growatt_EactodayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactodayL"] | Number:Energy Growatt_EactodayL "EactodayL [%0.1f kWH]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactodayL"} | 64.,EactodayL,Modbus RTU,,5,4,2054,1,9410,4,0,Unsigned int,0,1,kWH,1,100,97,0,0,0,1.000000,0,255
| 4 | 2055 | EactotalH | Total generate energy (high) |  |  | 0.1kWH |  |  | BMS | 0.1 | kWH | 1 | Type number : EactotalH "Growatt_EactotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactotalH"] | Number:Energy Growatt_EactotalH "EactotalH [%0.1f kWH]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactotalH"} | 64.,EactotalH,Modbus RTU,,5,4,2055,1,9410,4,0,Unsigned int,0,1,kWH,1,100,97,0,0,0,1.000000,0,255
| 4 | 2056 | EactotalL | Total generate energy (low) |  |  | 0.1kWH |  | self electric energy total H | BMS | 0.1 | kWH | 1 | Type number : EactotalL "Growatt_EactotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactotalL"] | Number:Energy Growatt_EactotalL "EactotalL [%0.1f kWH]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactotalL"} | 64.,EactotalL,Modbus RTU,,5,4,2056,1,9410,4,0,Unsigned int,0,1,kWH,1,100,97,0,0,0,1.000000,0,255
| 4 | 2057 | TimetotalH | Work time total (high) |  |  | 0.5s |  | Longitude | ALL | 0.5 | s | 1 | Type number : TimetotalH "Growatt_TimetotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.TimetotalH"] | Number:Time Growatt_TimetotalH "TimetotalH [%0.5f s]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TimetotalH"} | 64.,TimetotalH,Modbus RTU,,5,4,2057,1,9410,2,0,Unsigned int,0,1,s,1,100,97,0,0,0,1.000000,0,255
| 4 | 2058 | TimetotalL | Work time total (low) |  |  | 0.5s |  | Bit 0: Hungary | ALL | 0.5 | s | 1 | Type number : TimetotalL "Growatt_TimetotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.TimetotalL"] | Number:Time Growatt_TimetotalL "TimetotalL [%0.5f s]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TimetotalL"} | 64.,TimetotalL,Modbus RTU,,5,4,2058,1,9410,2,0,Unsigned int,0,1,s,1,100,97,0,0,0,1.000000,0,255
| 4 | 2093 | Temp1 | Inverter temperature |  |  | 0.1°C |  | 0%~100.0%,US regulations | ALL | 0.1 | °C | 1 | Type number : Temp1 "Growatt_Temp1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp1"] | Number:Temperature Growatt_Temp1 "Temp1 [%0.1f °C]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp1"} | 64.,Temp1,Modbus RTU,,5,4,2093,1,9410,2,0,Unsigned int,0,1,°C,1,100,97,0,0,0,1.000000,0,255
| 4 | 2094 | Temp2 | The inside IPM in inverter Temperature |  |  | 0.1°C |  |  | ALL | 0.1 | °C | 1 | Type number : Temp2 "Growatt_Temp2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp2"] | Number:Temperature Growatt_Temp2 "Temp2 [%0.1f °C]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp2"} | 64.,Temp2,Modbus RTU,,5,4,2094,1,9410,2,0,Unsigned int,0,1,°C,1,100,97,0,0,0,1.000000,0,255
| 4 | 2095 | Temp3 | Boost temperature |  |  | 0.1°C |  |  | ALL | 0.1 | °C | 1 | Type number : Temp3 "Growatt_Temp3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp3"] | Number:Temperature Growatt_Temp3 "Temp3 [%0.1f °C]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp3"} | 64.,Temp3,Modbus RTU,,5,4,2095,1,9410,2,0,Unsigned int,0,1,°C,1,100,97,0,0,0,1.000000,0,255
| 4 | 2096 | Temp4 | [6 empty] | ALL |  |  | 0 | Type number : Temp4 "Growatt_Temp4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp4"] | Number Growatt_Temp4 "Temp4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp4"} | 64.,Temp4,Modbus RTU,,5,4,2096,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 2097 | uwBatVolt_DSP | BatVolt_DSP |  |  | 0.1V |  | ASCII | ALL | 0.1 | V | 1 | Type number : uwBatVolt_DSP "Growatt_uwBatVolt_DSP" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwBatVolt_DSP"] | Number:ElectricPotential Growatt_uwBatVolt_DSP "uwBatVolt_DSP [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwBatVolt_DSP"} | 64.,uwBatVolt_DSP,Modbus RTU,,5,4,2097,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 2098 | PBusVoltage | P Bus inside Voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : PBusVoltage "Growatt_PBusVoltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PBusVoltage"] | Number:ElectricPotential Growatt_PBusVoltage "PBusVoltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PBusVoltage"} | 64.,PBusVoltage,Modbus RTU,,5,4,2098,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 2099 | NBusVoltage | N Bus inside Voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : NBusVoltage "Growatt_NBusVoltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.NBusVoltage"] | Number:ElectricPotential Growatt_NBusVoltage "NBusVoltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NBusVoltage"} | 64.,NBusVoltage,Modbus RTU,,5,4,2099,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 2100 | RemoteCtrlEn | [5 empty] | ASCII | TL_X-TL_XH |  |  | 0 | Type number : RemoteCtrlEn "Growatt_RemoteCtrlEn" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.RemoteCtrlEn"] | Number Growatt_RemoteCtrlEn "RemoteCtrlEn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:RemoteCtrlEn"} | 64.,RemoteCtrlEn,Modbus RTU,,5,4,2100,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 2101 | RemoteCtrlPower | [5 empty] | ASCII | TL_X-TL_XH |  |  | 0 | Type number : RemoteCtrlPower "Growatt_RemoteCtrlPower" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.RemoteCtrlPower"] | Number Growatt_RemoteCtrlPower "RemoteCtrlPower" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:RemoteCtrlPower"} | 64.,RemoteCtrlPower,Modbus RTU,,5,4,2101,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 2102 | ExtraACPowertogrid_H | Extra inverte AC Power to grid High | [5 empty] | PV9_32 |  |  | 0 | Type number : ExtraACPowertogrid_H "Growatt_ExtraACPowertogrid_H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ExtraACPowertogrid_H"] | Number Growatt_ExtraACPowertogrid_H "ExtraACPowertogrid_H" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ExtraACPowertogrid_H"} | 64.,ExtraACPowertogrid_H,Modbus RTU,,5,4,2102,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 2103 | ExtraACPowertogrid_L | Extrainverte AC Power to grid Low | [5 empty] | PV9_32 |  |  | 0 | Type number : ExtraACPowertogrid_L "Growatt_ExtraACPowertogrid_L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ExtraACPowertogrid_L"] | Number Growatt_ExtraACPowertogrid_L "ExtraACPowertogrid_L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ExtraACPowertogrid_L"} | 64.,ExtraACPowertogrid_L,Modbus RTU,,5,4,2103,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 2104 | Eextra_todayH | Extra inverter PowerTOUser_Extra today (high) | R |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eextra_todayH "Growatt_Eextra_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eextra_todayH"] | Number:Energy Growatt_Eextra_todayH "Eextra_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eextra_todayH"} | 64.,Eextra_todayH,Modbus RTU,,5,4,2104,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2105 | Eextra_todayL | Extra inverter PowerTOUser_Extra today (low) | R |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eextra_todayL "Growatt_Eextra_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eextra_todayL"] | Number:Energy Growatt_Eextra_todayL "Eextra_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eextra_todayL"} | 64.,Eextra_todayL,Modbus RTU,,5,4,2105,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2106 | Eextra_totalH | Extra inverter |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eextra_totalH "Growatt_Eextra_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eextra_totalH"] | Number:Energy Growatt_Eextra_totalH "Eextra_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eextra_totalH"} | 64.,Eextra_totalH,Modbus RTU,,5,4,2106,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2107 | Eextra_totalL | Extra inverter PowerTOUser_Extra total(low) |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eextra_totalL "Growatt_Eextra_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eextra_totalL"] | Number:Energy Growatt_Eextra_totalL "Eextra_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eextra_totalL"} | 64.,Eextra_totalL,Modbus RTU,,5,4,2107,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2108 | Esystem_todayH | System electric energy today H |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Esystem_todayH "Growatt_Esystem_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esystem_todayH"] | Number:Energy Growatt_Esystem_todayH "Esystem_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esystem_todayH"} | 64.,Esystem_todayH,Modbus RTU,,5,4,2108,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2109 | Esystem_todayL | System electric energy today L |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Esystem_todayL "Growatt_Esystem_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esystem_todayL"] | Number:Energy Growatt_Esystem_todayL "Esystem_todayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esystem_todayL"} | 64.,Esystem_todayL,Modbus RTU,,5,4,2109,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2110 | Esystem_totalH | System electric energy total H |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Esystem_totalH "Growatt_Esystem_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esystem_totalH"] | Number:Energy Growatt_Esystem_totalH "Esystem_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esystem_totalH"} | 64.,Esystem_totalH,Modbus RTU,,5,4,2110,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2111 | Esystem_totalL | System electric energy total L |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Esystem_totalL "Growatt_Esystem_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esystem_totalL"] | Number:Energy Growatt_Esystem_totalL "Esystem_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esystem_totalL"} | 64.,Esystem_totalL,Modbus RTU,,5,4,2111,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2112 | EACharge_Today | ACCharge energy today |  |  | 0.1kwh |  |  | BMS | 0.1 | kwh | 1 | Type number : EACharge_Today "Growatt_EACharge_Today" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EACharge_Today"] | Number:Energy Growatt_EACharge_Today "EACharge_Today [%0.1f kwh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EACharge_Today"} | 64.,EACharge_Today,Modbus RTU,,5,4,2112,1,9410,4,0,Unsigned int,0,1,kwh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2113 | EACharge_Today_L | ACCharge energy today |  |  | 0.1kwh |  |  | BMS | 0.1 | kwh | 1 | Type number : EACharge_Today_L "Growatt_EACharge_Today_L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EACharge_Today_L"] | Number:Energy Growatt_EACharge_Today_L "EACharge_Today_L [%0.1f kwh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EACharge_Today_L"} | 64.,EACharge_Today_L,Modbus RTU,,5,4,2113,1,9410,4,0,Unsigned int,0,1,kwh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2114 | EACharge_Total_H | ACCharge energy total |  |  | 0.1kwh |  |  | BMS | 0.1 | kwh | 1 | Type number : EACharge_Total_H "Growatt_EACharge_Total_H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EACharge_Total_H"] | Number:Energy Growatt_EACharge_Total_H "EACharge_Total_H [%0.1f kwh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EACharge_Total_H"} | 64.,EACharge_Total_H,Modbus RTU,,5,4,2114,1,9410,4,0,Unsigned int,0,1,kwh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2115 | EACharge_Total_L | ACCharge energy total |  |  | 0.1kwh |  |  | BMS | 0.1 | kwh | 1 | Type number : EACharge_Total_L "Growatt_EACharge_Total_L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EACharge_Total_L"] | Number:Energy Growatt_EACharge_Total_L "EACharge_Total_L [%0.1f kwh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EACharge_Total_L"} | 64.,EACharge_Total_L,Modbus RTU,,5,4,2115,1,9410,4,0,Unsigned int,0,1,kwh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2116 | ACchargePowerH | Grid power to local load |  |  | 0.1kwh |  |  | TL_X-TL_XH | 0.1 | kwh | 1 | Type number : ACchargePowerH "Growatt_ACchargePowerH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ACchargePowerH"] | Number:Energy Growatt_ACchargePowerH "ACchargePowerH [%0.1f kwh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ACchargePowerH"} | 64.,ACchargePowerH,Modbus RTU,,5,4,2116,1,9410,4,0,Unsigned int,0,1,kwh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2117 | ACChargePowerL | Grid power to local load |  |  | 0.1kwh |  |  | TL_X-TL_XH | 0.1 | kwh | 1 | Type number : ACChargePowerL "Growatt_ACChargePowerL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ACChargePowerL"] | Number:Energy Growatt_ACChargePowerL "ACChargePowerL [%0.1f kwh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ACChargePowerL"} | 64.,ACChargePowerL,Modbus RTU,,5,4,2117,1,9410,4,0,Unsigned int,0,1,kwh,1,100,97,0,0,0,1.000000,0,255
| 4 | 2118 | Priority |  |  | 0:Load First |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : Priority "Growatt_Priority" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Priority"] | Number Growatt_Priority "Priority" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Priority"} | 64.,Priority,Modbus RTU,,5,4,2118,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 2119 | BatteryType |  |  | 0:Lead-acid |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatteryType "Growatt_BatteryType" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatteryType"] | Number Growatt_BatteryType "BatteryType" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatteryType"} | 64.,BatteryType,Modbus RTU,,5,4,2119,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 2120 | AutoProofreadCMD | Aging mode | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : AutoProofreadCMD "Growatt_AutoProofreadCMD" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.AutoProofreadCMD"] | Number Growatt_AutoProofreadCMD "AutoProofreadCMD" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AutoProofreadCMD"} | 64.,AutoProofreadCMD,Modbus RTU,,5,4,2120,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 2124 | reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : reserved "Growatt_reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.reserved"] | Number Growatt_reserved "reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:reserved"} | 64.,reserved,Modbus RTU,,5,4,2124,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3000 | InverterStatus | Inverter run state | [5 empty] | ALL |  |  | 0 | Type number : InverterStatus "Growatt_InverterStatus" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.InverterStatus"] | Number Growatt_InverterStatus "InverterStatus" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:InverterStatus"} | 64.,InverterStatus,Modbus RTU,,5,4,3000,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3001 | PpvH | PV total power |  |  | 0.1W |  | ASCII | TL_X-TL_XH | 0.1 | W | 1 | Type number : PpvH "Growatt_PpvH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PpvH"] | Number:Power Growatt_PpvH "PpvH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PpvH"} | 64.,PpvH,Modbus RTU,,5,4,3001,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3002 | PpvL | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : PpvL "Growatt_PpvL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PpvL"] | Number Growatt_PpvL "PpvL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PpvL"} | 64.,PpvL,Modbus RTU,,5,4,3002,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3003 | Vpv1 | PV1 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv1 "Growatt_Vpv1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv1"] | Number:ElectricPotential Growatt_Vpv1 "Vpv1 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv1"} | 64.,Vpv1,Modbus RTU,,5,4,3003,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3004 | Ipv1 | PV1 input current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Ipv1 "Growatt_Ipv1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ipv1"] | Number:ElectricCurrent Growatt_Ipv1 "Ipv1 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ipv1"} | 64.,Ipv1,Modbus RTU,,5,4,3004,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3005 | Ppv1H | PV1 power |  |  | 0.1W |  | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : Ppv1H "Growatt_Ppv1H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv1H"] | Number:Power Growatt_Ppv1H "Ppv1H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv1H"} | 64.,Ppv1H,Modbus RTU,,5,4,3005,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3006 | Ppv1L | [6 empty] | USTimeSet |  |  | 0 | Type number : Ppv1L "Growatt_Ppv1L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv1L"] | Number Growatt_Ppv1L "Ppv1L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv1L"} | 64.,Ppv1L,Modbus RTU,,5,4,3006,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3007 | Vpv2 | PV2 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv2 "Growatt_Vpv2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv2"] | Number:ElectricPotential Growatt_Vpv2 "Vpv2 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv2"} | 64.,Vpv2,Modbus RTU,,5,4,3007,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3008 | Ipv2 | PV2 input current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Ipv2 "Growatt_Ipv2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ipv2"] | Number:ElectricCurrent Growatt_Ipv2 "Ipv2 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ipv2"} | 64.,Ipv2,Modbus RTU,,5,4,3008,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3009 | Ppv2H | PV2 power |  |  | 0.1W |  | bit0~6: min; bit7~11: hour; bit12~14, | USTimeSet | 0.1 | W | 1 | Type number : Ppv2H "Growatt_Ppv2H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv2H"] | Number:Power Growatt_Ppv2H "Ppv2H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv2H"} | 64.,Ppv2H,Modbus RTU,,5,4,3009,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3010 | Ppv2L | [5 empty] | bit0~6:min; bit7~11:hour; bit12~14, 0:loadfirst; | USTimeSet |  |  | 0 | Type number : Ppv2L "Growatt_Ppv2L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv2L"] | Number Growatt_Ppv2L "Ppv2L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv2L"} | 64.,Ppv2L,Modbus RTU,,5,4,3010,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3011 | Vpv3 | PV3 voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vpv3 "Growatt_Vpv3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv3"] | Number:ElectricPotential Growatt_Vpv3 "Vpv3 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv3"} | 64.,Vpv3,Modbus RTU,,5,4,3011,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3012 | Ipv3 | PV3 input current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Ipv3 "Growatt_Ipv3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ipv3"] | Number:ElectricCurrent Growatt_Ipv3 "Ipv3 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ipv3"} | 64.,Ipv3,Modbus RTU,,5,4,3012,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3013 | Ppv3H | PV3 power |  |  | 0.1W |  |  | USTimeSet | 0.1 | W | 1 | Type number : Ppv3H "Growatt_Ppv3H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv3H"] | Number:Power Growatt_Ppv3H "Ppv3H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv3H"} | 64.,Ppv3H,Modbus RTU,,5,4,3013,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3014 | Ppv3L | [5 empty] | With Time Month1 | USTimeSet |  |  | 0 | Type number : Ppv3L "Growatt_Ppv3L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv3L"] | Number Growatt_Ppv3L "Ppv3L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv3L"} | 64.,Ppv3L,Modbus RTU,,5,4,3014,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3015 | Vpv4 | PV4 voltage | [5 empty] | ALL |  |  | 0 | Type number : Vpv4 "Growatt_Vpv4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vpv4"] | Number Growatt_Vpv4 "Vpv4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpv4"} | 64.,Vpv4,Modbus RTU,,5,4,3015,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3016 | Ipv4 | PV4 input current | [5 empty] | ALL |  |  | 0 | Type number : Ipv4 "Growatt_Ipv4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ipv4"] | Number Growatt_Ipv4 "Ipv4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ipv4"} | 64.,Ipv4,Modbus RTU,,5,4,3016,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3017 | Ppv4H | PV4 power |  |  |  |  | bit0~3:month_L; bit4~7: month_H | TL_X-TL_XH US |  |  | 0 | Type number : Ppv4H "Growatt_Ppv4H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv4H"] | Number Growatt_Ppv4H "Ppv4H" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv4H"} | 64.,Ppv4H,Modbus RTU,,5,4,3017,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3018 | Ppv4L | [5 empty] | Bit8-bit15 The major version number ranges from 0-256. In principle, it cannot be changed | TL_X-TL_XH |  |  | 0 | Type number : Ppv4L "Growatt_Ppv4L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ppv4L"] | Number Growatt_Ppv4L "Ppv4L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ppv4L"} | 64.,Ppv4L,Modbus RTU,,5,4,3018,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3019 | PsysH | System output power |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : PsysH "Growatt_PsysH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PsysH"] | Number:Power Growatt_PsysH "PsysH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PsysH"} | 64.,PsysH,Modbus RTU,,5,4,3019,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3020 | PsysL | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : PsysL "Growatt_PsysL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PsysL"] | Number Growatt_PsysL "PsysL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PsysL"} | 64.,PsysL,Modbus RTU,,5,4,3020,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3021 | QacH | reactive power |  |  | 0.1W |  | Battery temperature lower | TL_X-TL_XH | 0.1 | W | 1 | Type number : QacH "Growatt_QacH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.QacH"] | Number:Power Growatt_QacH "QacH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:QacH"} | 64.,QacH,Modbus RTU,,5,4,3021,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3022 | QacL | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : QacL "Growatt_QacL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.QacL"] | Number Growatt_QacL "QacL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:QacL"} | 64.,QacL,Modbus RTU,,5,4,3022,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3023 | PacH | Output power |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PacH "Growatt_PacH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PacH"] | Number:Power Growatt_PacH "PacH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PacH"} | 64.,PacH,Modbus RTU,,5,4,3023,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3024 | PacL | [6 empty] | ALL |  |  | 0 | Type number : PacL "Growatt_PacL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PacL"] | Number Growatt_PacL "PacL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PacL"} | 64.,PacL,Modbus RTU,,5,4,3024,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3025 | Fac | Grid frequency |  |  | 0.01Hz |  |  | PV9_32 | 0.01 | Hz | 2 | Type number : Fac "Growatt_Fac" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Fac"] | Number:Frequency Growatt_Fac "Fac [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Fac"} | 64.,Fac,Modbus RTU,,5,4,3025,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255
| 4 | 3026 | Vac1 | Three/single phase grid voltage |  |  | 0.1V |  | ASCII | ALL | 0.1 | V | 1 | Type number : Vac1 "Growatt_Vac1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac1"] | Number:ElectricPotential Growatt_Vac1 "Vac1 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac1"} | 64.,Vac1,Modbus RTU,,5,4,3026,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3027 | Iac1 | Three/single phase grid output current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Iac1 "Growatt_Iac1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Iac1"] | Number:ElectricCurrent Growatt_Iac1 "Iac1 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Iac1"} | 64.,Iac1,Modbus RTU,,5,4,3027,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3028 | Pac1H | Three/single phase grid output watt |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac1H "Growatt_Pac1H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac1H"] | Number:Power Growatt_Pac1H "Pac1H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac1H"} | 64.,Pac1H,Modbus RTU,,5,4,3028,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3029 | Pac1L | VA | [5 empty] | ALL |  |  | 0 | Type number : Pac1L "Growatt_Pac1L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac1L"] | Number Growatt_Pac1L "Pac1L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac1L"} | 64.,Pac1L,Modbus RTU,,5,4,3029,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3030 | Vac2 | Three phase grid voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vac2 "Growatt_Vac2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac2"] | Number:ElectricPotential Growatt_Vac2 "Vac2 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac2"} | 64.,Vac2,Modbus RTU,,5,4,3030,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3031 | Iac2 | Three phase grid output current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Iac2 "Growatt_Iac2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Iac2"] | Number:ElectricCurrent Growatt_Iac2 "Iac2 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Iac2"} | 64.,Iac2,Modbus RTU,,5,4,3031,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3032 | Pac2H | Three phase grid output power |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac2H "Growatt_Pac2H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac2H"] | Number:Power Growatt_Pac2H "Pac2H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac2H"} | 64.,Pac2H,Modbus RTU,,5,4,3032,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3033 | Pac2L | [6 empty] | ALL |  |  | 0 | Type number : Pac2L "Growatt_Pac2L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac2L"] | Number Growatt_Pac2L "Pac2L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac2L"} | 64.,Pac2L,Modbus RTU,,5,4,3033,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3034 | Vac3 | Three phase grid voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vac3 "Growatt_Vac3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac3"] | Number:ElectricPotential Growatt_Vac3 "Vac3 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac3"} | 64.,Vac3,Modbus RTU,,5,4,3034,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3035 | Iac3 | Three phase grid output current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Iac3 "Growatt_Iac3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Iac3"] | Number:ElectricCurrent Growatt_Iac3 "Iac3 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Iac3"} | 64.,Iac3,Modbus RTU,,5,4,3035,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3036 | Pac3H | Three phase grid output power |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pac3H "Growatt_Pac3H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac3H"] | Number:Power Growatt_Pac3H "Pac3H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac3H"} | 64.,Pac3H,Modbus RTU,,5,4,3036,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3037 | Pac3L | [6 empty] | ALL |  |  | 0 | Type number : Pac3L "Growatt_Pac3L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pac3L"] | Number Growatt_Pac3L "Pac3L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pac3L"} | 64.,Pac3L,Modbus RTU,,5,4,3037,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3038 | Vac_RS | Three phase grid voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vac_RS "Growatt_Vac_RS" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac_RS"] | Number:ElectricPotential Growatt_Vac_RS "Vac_RS [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac_RS"} | 64.,Vac_RS,Modbus RTU,,5,4,3038,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3039 | Vac_ST | Three phase grid voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vac_ST "Growatt_Vac_ST" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac_ST"] | Number:ElectricPotential Growatt_Vac_ST "Vac_ST [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac_ST"} | 64.,Vac_ST,Modbus RTU,,5,4,3039,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3040 | Vac_TR | Three phase grid voltage |  |  | 0.1V |  | ASCII | ALL | 0.1 | V | 1 | Type number : Vac_TR "Growatt_Vac_TR" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vac_TR"] | Number:ElectricPotential Growatt_Vac_TR "Vac_TR [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vac_TR"} | 64.,Vac_TR,Modbus RTU,,5,4,3040,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3041 | PtousertotalH | Total forward power |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : PtousertotalH "Growatt_PtousertotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PtousertotalH"] | Number:Power Growatt_PtousertotalH "PtousertotalH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PtousertotalH"} | 64.,PtousertotalH,Modbus RTU,,5,4,3041,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3042 | PtousertotalL | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : PtousertotalL "Growatt_PtousertotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PtousertotalL"] | Number Growatt_PtousertotalL "PtousertotalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PtousertotalL"} | 64.,PtousertotalL,Modbus RTU,,5,4,3042,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3043 | PtogridtotalH | Total reverse power |  |  | 0.1W |  | 0:230V | TL_X-TL_XH | 0.1 | W | 1 | Type number : PtogridtotalH "Growatt_PtogridtotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PtogridtotalH"] | Number:Power Growatt_PtogridtotalH "PtogridtotalH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PtogridtotalH"} | 64.,PtogridtotalH,Modbus RTU,,5,4,3043,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3044 | PtogridtotalL | [5 empty] | 0:disable | TL_X-TL_XH |  |  | 0 | Type number : PtogridtotalL "Growatt_PtogridtotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PtogridtotalL"] | Number Growatt_PtogridtotalL "PtogridtotalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PtogridtotalL"} | 64.,PtogridtotalL,Modbus RTU,,5,4,3044,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3045 | PtoloadtotalH | Total load power |  |  | 0.1W |  |  | TL_X-TL_XH | 0.1 | W | 1 | Type number : PtoloadtotalH "Growatt_PtoloadtotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PtoloadtotalH"] | Number:Power Growatt_PtoloadtotalH "PtoloadtotalH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PtoloadtotalH"} | 64.,PtoloadtotalH,Modbus RTU,,5,4,3045,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3046 | PtoloadtotalL | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : PtoloadtotalL "Growatt_PtoloadtotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PtoloadtotalL"] | Number Growatt_PtoloadtotalL "PtoloadtotalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PtoloadtotalL"} | 64.,PtoloadtotalL,Modbus RTU,,5,4,3046,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3047 | TimetotalH | Work time total |  |  | 0.5s |  | Latitude | ALL | 0.5 | s | 1 | Type number : TimetotalH "Growatt_TimetotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.TimetotalH"] | Number:Time Growatt_TimetotalH "TimetotalH [%0.5f s]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TimetotalH"} | 64.,TimetotalH,Modbus RTU,,5,4,3047,1,9410,2,0,Unsigned int,0,1,s,1,100,97,0,0,0,1.000000,0,255
| 4 | 3048 | TimetotalL | [5 empty] | Reserved | ALL |  |  | 0 | Type number : TimetotalL "Growatt_TimetotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.TimetotalL"] | Number Growatt_TimetotalL "TimetotalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TimetotalL"} | 64.,TimetotalL,Modbus RTU,,5,4,3048,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3049 | EactodayH | Today generate energy |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : EactodayH "Growatt_EactodayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactodayH"] | Number:Energy Growatt_EactodayH "EactodayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactodayH"} | 64.,EactodayH,Modbus RTU,,5,4,3049,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3050 | EactodayL | [6 empty] | BMS |  |  | 0 | Type number : EactodayL "Growatt_EactodayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactodayL"] | Number Growatt_EactodayL "EactodayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactodayL"} | 64.,EactodayL,Modbus RTU,,5,4,3050,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3051 | EactotalH | Total generate energy |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : EactotalH "Growatt_EactotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactotalH"] | Number:Energy Growatt_EactotalH "EactotalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactotalH"} | 64.,EactotalH,Modbus RTU,,5,4,3051,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3052 | EactotalL | [5 empty] | self power H | BMS |  |  | 0 | Type number : EactotalL "Growatt_EactotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EactotalL"] | Number Growatt_EactotalL "EactotalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EactotalL"} | 64.,EactotalL,Modbus RTU,,5,4,3052,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3053 | Epv_totalH | PV energy total |  |  | 0.1kWh |  |  | UPS | 0.1 | kWh | 1 | Type number : Epv_totalH "Growatt_Epv_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv_totalH"] | Number:Energy Growatt_Epv_totalH "Epv_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv_totalH"} | 64.,Epv_totalH,Modbus RTU,,5,4,3053,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3054 | Epv_totalL | [5 empty] | ApparentPower | PowerGeneration |  |  | 0 | Type number : Epv_totalL "Growatt_Epv_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv_totalL"] | Number Growatt_Epv_totalL "Epv_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv_totalL"} | 64.,Epv_totalL,Modbus RTU,,5,4,3054,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3055 | Epv1_todayH | PV1 energy today |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv1_todayH "Growatt_Epv1_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv1_todayH"] | Number:Energy Growatt_Epv1_todayH "Epv1_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv1_todayH"} | 64.,Epv1_todayH,Modbus RTU,,5,4,3055,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3056 | Epv1_todayL | [6 empty] | PowerGeneration |  |  | 0 | Type number : Epv1_todayL "Growatt_Epv1_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv1_todayL"] | Number Growatt_Epv1_todayL "Epv1_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv1_todayL"} | 64.,Epv1_todayL,Modbus RTU,,5,4,3056,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3057 | Epv1_totalH | PV1 energy total |  |  | 0.1kWh |  |  | PowerGeneration | 0.1 | kWh | 1 | Type number : Epv1_totalH "Growatt_Epv1_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv1_totalH"] | Number:Energy Growatt_Epv1_totalH "Epv1_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv1_totalH"} | 64.,Epv1_totalH,Modbus RTU,,5,4,3057,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3058 | Epv1_totalL | [6 empty] | PowerGeneration |  |  | 0 | Type number : Epv1_totalL "Growatt_Epv1_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv1_totalL"] | Number Growatt_Epv1_totalL "Epv1_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv1_totalL"} | 64.,Epv1_totalL,Modbus RTU,,5,4,3058,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3059 | Epv2_todayH | PV2 energy today |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv2_todayH "Growatt_Epv2_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv2_todayH"] | Number:Energy Growatt_Epv2_todayH "Epv2_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv2_todayH"} | 64.,Epv2_todayH,Modbus RTU,,5,4,3059,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3060 | Epv2_todayL | [6 empty] | Storage |  |  | 0 | Type number : Epv2_todayL "Growatt_Epv2_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv2_todayL"] | Number Growatt_Epv2_todayL "Epv2_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv2_todayL"} | 64.,Epv2_todayL,Modbus RTU,,5,4,3060,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3061 | Epv2_totalH | PV2 energy total |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv2_totalH "Growatt_Epv2_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv2_totalH"] | Number:Energy Growatt_Epv2_totalH "Epv2_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv2_totalH"} | 64.,Epv2_totalH,Modbus RTU,,5,4,3061,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3062 | Epv2_totalL | [6 empty] | Storage |  |  | 0 | Type number : Epv2_totalL "Growatt_Epv2_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv2_totalL"] | Number Growatt_Epv2_totalL "Epv2_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv2_totalL"} | 64.,Epv2_totalL,Modbus RTU,,5,4,3062,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3063 | Epv3_todayH | PV3 energy today |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv3_todayH "Growatt_Epv3_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv3_todayH"] | Number:Energy Growatt_Epv3_todayH "Epv3_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv3_todayH"} | 64.,Epv3_todayH,Modbus RTU,,5,4,3063,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3064 | Epv3_todayL | [6 empty] | Storage |  |  | 0 | Type number : Epv3_todayL "Growatt_Epv3_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv3_todayL"] | Number Growatt_Epv3_todayL "Epv3_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv3_todayL"} | 64.,Epv3_todayL,Modbus RTU,,5,4,3064,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3065 | Epv3_totalH | PV3 energy total |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv3_totalH "Growatt_Epv3_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv3_totalH"] | Number:Energy Growatt_Epv3_totalH "Epv3_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv3_totalH"} | 64.,Epv3_totalH,Modbus RTU,,5,4,3065,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3066 | Epv3_totalL | [6 empty] | Storage |  |  | 0 | Type number : Epv3_totalL "Growatt_Epv3_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv3_totalL"] | Number Growatt_Epv3_totalL "Epv3_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv3_totalL"} | 64.,Epv3_totalL,Modbus RTU,,5,4,3066,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3067 | Etouser_todayH | Today energy to user |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etouser_todayH "Growatt_Etouser_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etouser_todayH"] | Number:Energy Growatt_Etouser_todayH "Etouser_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etouser_todayH"} | 64.,Etouser_todayH,Modbus RTU,,5,4,3067,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3068 | Etouser_todayL | [6 empty] | PV9_32 |  |  | 0 | Type number : Etouser_todayL "Growatt_Etouser_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etouser_todayL"] | Number Growatt_Etouser_todayL "Etouser_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etouser_todayL"} | 64.,Etouser_todayL,Modbus RTU,,5,4,3068,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3069 | Etouser_totalH | Total energy to user |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etouser_totalH "Growatt_Etouser_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etouser_totalH"] | Number:Energy Growatt_Etouser_totalH "Etouser_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etouser_totalH"} | 64.,Etouser_totalH,Modbus RTU,,5,4,3069,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3070 | Etouser_totalL | [6 empty] | PV9_32 |  |  | 0 | Type number : Etouser_totalL "Growatt_Etouser_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etouser_totalL"] | Number Growatt_Etouser_totalL "Etouser_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etouser_totalL"} | 64.,Etouser_totalL,Modbus RTU,,5,4,3070,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3071 | Etogrid_todayH | Today energy to grid |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etogrid_todayH "Growatt_Etogrid_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etogrid_todayH"] | Number:Energy Growatt_Etogrid_todayH "Etogrid_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etogrid_todayH"} | 64.,Etogrid_todayH,Modbus RTU,,5,4,3071,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3072 | Etogrid_todayL | [6 empty] | PV9_32 |  |  | 0 | Type number : Etogrid_todayL "Growatt_Etogrid_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etogrid_todayL"] | Number Growatt_Etogrid_todayL "Etogrid_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etogrid_todayL"} | 64.,Etogrid_todayL,Modbus RTU,,5,4,3072,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3073 | Etogrid_totalH | Total energy to grid |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Etogrid_totalH "Growatt_Etogrid_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etogrid_totalH"] | Number:Energy Growatt_Etogrid_totalH "Etogrid_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etogrid_totalH"} | 64.,Etogrid_totalH,Modbus RTU,,5,4,3073,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3074 | Etogrid_totalL | [6 empty] | PV9_32 |  |  | 0 | Type number : Etogrid_totalL "Growatt_Etogrid_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Etogrid_totalL"] | Number Growatt_Etogrid_totalL "Etogrid_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Etogrid_totalL"} | 64.,Etogrid_totalL,Modbus RTU,,5,4,3074,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3075 | Eload_todayH | Today energy of user load |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eload_todayH "Growatt_Eload_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eload_todayH"] | Number:Energy Growatt_Eload_todayH "Eload_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eload_todayH"} | 64.,Eload_todayH,Modbus RTU,,5,4,3075,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3076 | Eload_todayL | [6 empty] | BMS |  |  | 0 | Type number : Eload_todayL "Growatt_Eload_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eload_todayL"] | Number Growatt_Eload_todayL "Eload_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eload_todayL"} | 64.,Eload_todayL,Modbus RTU,,5,4,3076,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3077 | Eload_totalH | Total energy of user load |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eload_totalH "Growatt_Eload_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eload_totalH"] | Number:Energy Growatt_Eload_totalH "Eload_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eload_totalH"} | 64.,Eload_totalH,Modbus RTU,,5,4,3077,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3078 | Eload_totalL | [6 empty] | BMS |  |  | 0 | Type number : Eload_totalL "Growatt_Eload_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eload_totalL"] | Number Growatt_Eload_totalL "Eload_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eload_totalL"} | 64.,Eload_totalL,Modbus RTU,,5,4,3078,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3079 | Epv4_todayH | PV4 energy today |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv4_todayH "Growatt_Epv4_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv4_todayH"] | Number:Energy Growatt_Epv4_todayH "Epv4_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv4_todayH"} | 64.,Epv4_todayH,Modbus RTU,,5,4,3079,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3080 | Epv4_todayL | [6 empty] | Storage |  |  | 0 | Type number : Epv4_todayL "Growatt_Epv4_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv4_todayL"] | Number Growatt_Epv4_todayL "Epv4_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv4_todayL"} | 64.,Epv4_todayL,Modbus RTU,,5,4,3080,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3081 | Epv4_totalH | PV4 energy total |  |  | 0.1kWh |  |  | Storage | 0.1 | kWh | 1 | Type number : Epv4_totalH "Growatt_Epv4_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv4_totalH"] | Number:Energy Growatt_Epv4_totalH "Epv4_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv4_totalH"} | 64.,Epv4_totalH,Modbus RTU,,5,4,3081,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3082 | Epv4_totalL | [6 empty] | Storage |  |  | 0 | Type number : Epv4_totalL "Growatt_Epv4_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv4_totalL"] | Number Growatt_Epv4_totalL "Epv4_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv4_totalL"} | 64.,Epv4_totalL,Modbus RTU,,5,4,3082,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3083 | Epv_todayH | PV energy today |  |  | 0.1kWh |  |  | UPS | 0.1 | kWh | 1 | Type number : Epv_todayH "Growatt_Epv_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv_todayH"] | Number:Energy Growatt_Epv_todayH "Epv_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv_todayH"} | 64.,Epv_todayH,Modbus RTU,,5,4,3083,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3084 | Epv_todayL | [6 empty] | UPS |  |  | 0 | Type number : Epv_todayL "Growatt_Epv_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Epv_todayL"] | Number Growatt_Epv_todayL "Epv_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Epv_todayL"} | 64.,Epv_todayL,Modbus RTU,,5,4,3084,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3085 | Reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3085,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3086 | DeratingMode | DeratingMode |  |  |  |  | SPA | SPA |  |  | 0 | Type number : DeratingMode "Growatt_DeratingMode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DeratingMode"] | Number Growatt_DeratingMode "DeratingMode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DeratingMode"} | 64.,DeratingMode,Modbus RTU,,5,4,3086,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3087 | ISO | PV ISO value |  |  | 1K? |  |  | ALL | 1 | K? | 0 | Type number : ISO "Growatt_ISO" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ISO"] | #N/A | 64.,ISO,Modbus RTU,,5,4,3087,1,9410,2,0,Unsigned int,0,0,K?,1,100,97,0,0,0,1.000000,0,255
| 4 | 3088 | DCI_R | R DCI Curr |  |  | 0.1mA |  | SPA used | SPA | 0.1 | mA | 1 | Type number : DCI_R "Growatt_DCI_R" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DCI_R"] | #N/A | 64.,DCI_R,Modbus RTU,,5,4,3088,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 3089 | DCI_S | S DCI Curr |  |  | 0.1mA |  | SPA used | SPA | 0.1 | mA | 1 | Type number : DCI_S "Growatt_DCI_S" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DCI_S"] | #N/A | 64.,DCI_S,Modbus RTU,,5,4,3089,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 3090 | DCI_T | T DCI Curr |  |  | 0.1mA |  | SPA used | SPA | 0.1 | mA | 1 | Type number : DCI_T "Growatt_DCI_T" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DCI_T"] | #N/A | 64.,DCI_T,Modbus RTU,,5,4,3090,1,9410,2,0,Unsigned int,0,1,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 3091 | GFCI | GFCI Curr |  |  | 1mA |  |  | PV9_32 | 1 | mA | 0 | Type number : GFCI "Growatt_GFCI" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.GFCI"] | #N/A | 64.,GFCI,Modbus RTU,,5,4,3091,1,9410,2,0,Unsigned int,0,0,mA,1,100,97,0,0,0,1.000000,0,255
| 4 | 3092 | BusVoltage | total bus voltage |  |  | 0.1V |  |  | TL_X-TL_XH | 0.1 | V | 1 | Type number : BusVoltage "Growatt_BusVoltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BusVoltage"] | Number:ElectricPotential Growatt_BusVoltage "BusVoltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BusVoltage"} | 64.,BusVoltage,Modbus RTU,,5,4,3092,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3093 | Temp1 | Inverter temperature |  |  | 0.1? |  | 0%~100.0%,US regulations | ALL | 0.1 | ? | 1 | Type number : Temp1 "Growatt_Temp1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp1"] | Number:Length Growatt_Temp1 "Temp1 [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp1"} | 64.,Temp1,Modbus RTU,,5,4,3093,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
| 4 | 3094 | Temp2 | The inside IPM in inverter temperature |  |  | 0.1? |  |  | ALL | 0.1 | ? | 1 | Type number : Temp2 "Growatt_Temp2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp2"] | Number:Length Growatt_Temp2 "Temp2 [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp2"} | 64.,Temp2,Modbus RTU,,5,4,3094,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
| 4 | 3095 | Temp3 | Boost temperature |  |  | 0.1? |  |  | ALL | 0.1 | ? | 1 | Type number : Temp3 "Growatt_Temp3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp3"] | Number:Length Growatt_Temp3 "Temp3 [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp3"} | 64.,Temp3,Modbus RTU,,5,4,3095,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
| 4 | 3096 | Temp4 | Reserved |  |  | 0.1? |  | 1:A road strength | ALL | 0.1 | ? | 1 | Type number : Temp4 "Growatt_Temp4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp4"] | Number:Length Growatt_Temp4 "Temp4 [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp4"} | 64.,Temp4,Modbus RTU,,5,4,3096,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
| 4 | 3097 | Temp5 | Commmunication broad temperature |  |  | 0.1? |  |  | ALL | 0.1 | ? | 1 | Type number : Temp5 "Growatt_Temp5" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Temp5"] | Number:Length Growatt_Temp5 "Temp5 [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Temp5"} | 64.,Temp5,Modbus RTU,,5,4,3097,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
| 4 | 3098 | PBusVoltage | P Bus inside Voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : PBusVoltage "Growatt_PBusVoltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PBusVoltage"] | Number:ElectricPotential Growatt_PBusVoltage "PBusVoltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PBusVoltage"} | 64.,PBusVoltage,Modbus RTU,,5,4,3098,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3099 | NBusVoltage | N Bus inside Voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : NBusVoltage "Growatt_NBusVoltage" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.NBusVoltage"] | Number:ElectricPotential Growatt_NBusVoltage "NBusVoltage [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NBusVoltage"} | 64.,NBusVoltage,Modbus RTU,,5,4,3099,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3100 | IPF | Inverter output PF now | [5 empty] | ALL |  |  | 0 | Type number : IPF "Growatt_IPF" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.IPF"] | Number Growatt_IPF "IPF" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:IPF"} | 64.,IPF,Modbus RTU,,5,4,3100,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3101 | RealOPPercent | Real Output power Percent |  |  | 0.01 |  | ASCII | TL_X-TL_XH | 0.01 |  | 2 | Type number : RealOPPercent "Growatt_RealOPPercent" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.RealOPPercent"] | Number Growatt_RealOPPercent "RealOPPercent [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:RealOPPercent"} | 64.,RealOPPercent,Modbus RTU,,5,4,3101,1,9410,2,0,Unsigned int,0,2,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3102 | OPFullwattH | Output Maxpower Limited |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : OPFullwattH "Growatt_OPFullwattH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.OPFullwattH"] | Number:Power Growatt_OPFullwattH "OPFullwattH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OPFullwattH"} | 64.,OPFullwattH,Modbus RTU,,5,4,3102,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3103 | OPFullwattL | [6 empty] | ALL |  |  | 0 | Type number : OPFullwattL "Growatt_OPFullwattL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.OPFullwattL"] | Number Growatt_OPFullwattL "OPFullwattL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OPFullwattL"} | 64.,OPFullwattL,Modbus RTU,,5,4,3103,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3104 | StandbyFlag | Inverter standby flag | [5 empty] | Storage |  |  | 0 | Type number : StandbyFlag "Growatt_StandbyFlag" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.StandbyFlag"] | Number Growatt_StandbyFlag "StandbyFlag" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:StandbyFlag"} | 64.,StandbyFlag,Modbus RTU,,5,4,3104,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3105 | FaultMaincode | Inverter fault maincode | [5 empty] | PV9_32 |  |  | 0 | Type number : FaultMaincode "Growatt_FaultMaincode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.FaultMaincode"] | Number Growatt_FaultMaincode "FaultMaincode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FaultMaincode"} | 64.,FaultMaincode,Modbus RTU,,5,4,3105,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3106 | WarnMaincode | Inverter Warning maincode | [5 empty] | ALL |  |  | 0 | Type number : WarnMaincode "Growatt_WarnMaincode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.WarnMaincode"] | Number Growatt_WarnMaincode "WarnMaincode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:WarnMaincode"} | 64.,WarnMaincode,Modbus RTU,,5,4,3106,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3107 | FaultSubcode | Inverter fault subcode | [5 empty] | PV9_32 |  |  | 0 | Type number : FaultSubcode "Growatt_FaultSubcode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.FaultSubcode"] | Number Growatt_FaultSubcode "FaultSubcode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FaultSubcode"} | 64.,FaultSubcode,Modbus RTU,,5,4,3107,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3108 | WarnSubcode | Inverter Warning subcode |  |  |  |  | ASCII | ALL |  |  | 0 | Type number : WarnSubcode "Growatt_WarnSubcode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.WarnSubcode"] | Number Growatt_WarnSubcode "WarnSubcode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:WarnSubcode"} | 64.,WarnSubcode,Modbus RTU,,5,4,3108,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3111 | uwPresentFFTValue_CHANNEL_A | PresentFFTValue [CHANNEL_A] |  |  |  |  | UL | ALL |  |  | 0 | Type number : uwPresentFFTValue_CHANNEL_A "Growatt_uwPresentFFTValue_CHANNEL_A" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwPresentFFTValue_CHANNEL_A"] | Number Growatt_uwPresentFFTValue_CHANNEL_A "uwPresentFFTValue_CHANNEL_A" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwPresentFFTValue_CHANNEL_A"} | 64.,uwPresentFFTValue_CHANNEL_A,Modbus RTU,,5,4,3111,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3112 | bAfciStatus | AFCI Status | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : bAfciStatus "Growatt_bAfciStatus" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.bAfciStatus"] | Number Growatt_bAfciStatus "bAfciStatus" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bAfciStatus"} | 64.,bAfciStatus,Modbus RTU,,5,4,3112,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3113 | uwStrength_CHANNEL_A | AFCI Strength[CHANNEL_A] | [5 empty] | ALL |  |  | 0 | Type number : uwStrength_CHANNEL_A "Growatt_uwStrength_CHANNEL_A" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwStrength_CHANNEL_A"] | Number Growatt_uwStrength_CHANNEL_A "uwStrength_CHANNEL_A" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwStrength_CHANNEL_A"} | 64.,uwStrength_CHANNEL_A,Modbus RTU,,5,4,3113,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3114 | uwSelfCheckValue_CHANNEL_A | AFCI SelfCheck[CHANNEL_A] | [5 empty] | ALL |  |  | 0 | Type number : uwSelfCheckValue_CHANNEL_A "Growatt_uwSelfCheckValue_CHANNEL_A" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwSelfCheckValue_CHANNEL_A"] | Number Growatt_uwSelfCheckValue_CHANNEL_A "uwSelfCheckValue_CHANNEL_A" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwSelfCheckValue_CHANNEL_A"} | 64.,uwSelfCheckValue_CHANNEL_A,Modbus RTU,,5,4,3114,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3115 | invstartdelaytime | inv start delay time |  |  | 1S |  |  | ALL | 1 | S | 0 | Type number : invstartdelaytime "Growatt_invstartdelaytime" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.invstartdelaytime"] | Number:Time Growatt_invstartdelaytime "invstartdelaytime [%1f S]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:invstartdelaytime"} | 64.,invstartdelaytime,Modbus RTU,,5,4,3115,1,9410,2,0,Unsigned int,0,0,S,1,100,97,0,0,0,1.000000,0,255
| 4 | 3116 | Reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3116,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3117 | Reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3117,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3118 | BDC_OnOffState | BDC connect state | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BDC_OnOffState "Growatt_BDC_OnOffState" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BDC_OnOffState"] | Number Growatt_BDC_OnOffState "BDC_OnOffState" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BDC_OnOffState"} | 64.,BDC_OnOffState,Modbus RTU,,5,4,3118,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3119 | DryContactState | Current status of DryContact |  |  |  |  | SPA | SPA |  |  | 0 | Type number : DryContactState "Growatt_DryContactState" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DryContactState"] | Number Growatt_DryContactState "DryContactState" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DryContactState"} | 64.,DryContactState,Modbus RTU,,5,4,3119,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3120 | Reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3120,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3121 | PselfH | self-use power |  |  | 0.1W |  | ASCII | TL_X-TL_XH | 0.1 | W | 1 | Type number : PselfH "Growatt_PselfH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PselfH"] | Number:Power Growatt_PselfH "PselfH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PselfH"} | 64.,PselfH,Modbus RTU,,5,4,3121,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3122 | PselfL | [5 empty] | 0: 9600 bps | TL_X-TL_XH |  |  | 0 | Type number : PselfL "Growatt_PselfL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PselfL"] | Number Growatt_PselfL "PselfL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PselfL"} | 64.,PselfL,Modbus RTU,,5,4,3122,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3123 | Esys_todayH | System energy today |  |  | 0.1kwh |  |  | PV9_32 | 0.1 | kwh | 1 | Type number : Esys_todayH "Growatt_Esys_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esys_todayH"] | Number:Energy Growatt_Esys_todayH "Esys_todayH [%0.1f kwh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esys_todayH"} | 64.,Esys_todayH,Modbus RTU,,5,4,3123,1,9410,4,0,Unsigned int,0,1,kwh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3124 | Esys_todayL | [6 empty] | PV9_32 |  |  | 0 | Type number : Esys_todayL "Growatt_Esys_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esys_todayL"] | Number Growatt_Esys_todayL "Esys_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esys_todayL"} | 64.,Esys_todayL,Modbus RTU,,5,4,3124,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3125 | Edischr_todayH | Today discharge energy |  |  | 0.1kWh |  | SPA used | BMS | 0.1 | kWh | 1 | Type number : Edischr_todayH "Growatt_Edischr_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Edischr_todayH"] | Number:Energy Growatt_Edischr_todayH "Edischr_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Edischr_todayH"} | 64.,Edischr_todayH,Modbus RTU,,5,4,3125,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3126 | Edischr_todayL | [6 empty] | BMS |  |  | 0 | Type number : Edischr_todayL "Growatt_Edischr_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Edischr_todayL"] | Number Growatt_Edischr_todayL "Edischr_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Edischr_todayL"} | 64.,Edischr_todayL,Modbus RTU,,5,4,3126,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3127 | Edischr_totalH | Total discharge energy |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Edischr_totalH "Growatt_Edischr_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Edischr_totalH"] | Number:Energy Growatt_Edischr_totalH "Edischr_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Edischr_totalH"} | 64.,Edischr_totalH,Modbus RTU,,5,4,3127,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3128 | Edischr_totalL | [6 empty] | BMS |  |  | 0 | Type number : Edischr_totalL "Growatt_Edischr_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Edischr_totalL"] | Number Growatt_Edischr_totalL "Edischr_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Edischr_totalL"} | 64.,Edischr_totalL,Modbus RTU,,5,4,3128,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3129 | Echr_todayH | Charge energy today |  |  | 0.1kWh |  | self electric | BMS | 0.1 | kWh | 1 | Type number : Echr_todayH "Growatt_Echr_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Echr_todayH"] | Number:Energy Growatt_Echr_todayH "Echr_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Echr_todayH"} | 64.,Echr_todayH,Modbus RTU,,5,4,3129,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3130 | Echr_todayL | [5 empty] | SPA used | BMS |  |  | 0 | Type number : Echr_todayL "Growatt_Echr_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Echr_todayL"] | Number Growatt_Echr_todayL "Echr_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Echr_todayL"} | 64.,Echr_todayL,Modbus RTU,,5,4,3130,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3131 | Echr_totalH | Charge energy total |  |  | 0.1kWh |  | self power L | BMS | 0.1 | kWh | 1 | Type number : Echr_totalH "Growatt_Echr_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Echr_totalH"] | Number:Energy Growatt_Echr_totalH "Echr_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Echr_totalH"} | 64.,Echr_totalH,Modbus RTU,,5,4,3131,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3132 | Echr_totalL | [5 empty] | SPA used | BMS |  |  | 0 | Type number : Echr_totalL "Growatt_Echr_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Echr_totalL"] | Number Growatt_Echr_totalL "Echr_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Echr_totalL"} | 64.,Echr_totalL,Modbus RTU,,5,4,3132,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3133 | Eacchr_todayH | Today energy of AC charge |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eacchr_todayH "Growatt_Eacchr_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eacchr_todayH"] | Number:Energy Growatt_Eacchr_todayH "Eacchr_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eacchr_todayH"} | 64.,Eacchr_todayH,Modbus RTU,,5,4,3133,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3134 | Eacchr_todayL | [6 empty] | BMS |  |  | 0 | Type number : Eacchr_todayL "Growatt_Eacchr_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eacchr_todayL"] | Number Growatt_Eacchr_todayL "Eacchr_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eacchr_todayL"} | 64.,Eacchr_todayL,Modbus RTU,,5,4,3134,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3135 | Eacchr_totalH | Total energy of AC charge |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eacchr_totalH "Growatt_Eacchr_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eacchr_totalH"] | Number:Energy Growatt_Eacchr_totalH "Eacchr_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eacchr_totalH"} | 64.,Eacchr_totalH,Modbus RTU,,5,4,3135,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3136 | Eacchr_totalL | [6 empty] | BMS |  |  | 0 | Type number : Eacchr_totalL "Growatt_Eacchr_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eacchr_totalL"] | Number Growatt_Eacchr_totalL "Eacchr_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eacchr_totalL"} | 64.,Eacchr_totalL,Modbus RTU,,5,4,3136,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3137 | Esys_totalH | [6 empty] | PV9_32 |  |  | 0 | Type number : Esys_totalH "Growatt_Esys_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esys_totalH"] | Number Growatt_Esys_totalH "Esys_totalH" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esys_totalH"} | 64.,Esys_totalH,Modbus RTU,,5,4,3137,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3138 | Esys_totalL | Total energy of system output \ |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Esys_totalL "Growatt_Esys_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Esys_totalL"] | Number:Energy Growatt_Esys_totalL "Esys_totalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Esys_totalL"} | 64.,Esys_totalL,Modbus RTU,,5,4,3138,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3139 | Eself_todayH | Today energy of Self output |  |  | 0.1kWh |  |  | PV9_32 | 0.1 | kWh | 1 | Type number : Eself_todayH "Growatt_Eself_todayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eself_todayH"] | Number:Energy Growatt_Eself_todayH "Eself_todayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eself_todayH"} | 64.,Eself_todayH,Modbus RTU,,5,4,3139,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3140 | Eself_todayL | [6 empty] | PV9_32 |  |  | 0 | Type number : Eself_todayL "Growatt_Eself_todayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eself_todayL"] | Number Growatt_Eself_todayL "Eself_todayL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eself_todayL"} | 64.,Eself_todayL,Modbus RTU,,5,4,3140,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3141 | Eself_totalH | Total energy of Self output |  |  | 0.1kwh |  |  | PV9_32 | 0.1 | kwh | 1 | Type number : Eself_totalH "Growatt_Eself_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eself_totalH"] | Number:Energy Growatt_Eself_totalH "Eself_totalH [%0.1f kwh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eself_totalH"} | 64.,Eself_totalH,Modbus RTU,,5,4,3141,1,9410,4,0,Unsigned int,0,1,kwh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3142 | Eself_totalL | [6 empty] | PV9_32 |  |  | 0 | Type number : Eself_totalL "Growatt_Eself_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eself_totalL"] | Number Growatt_Eself_totalL "Eself_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eself_totalL"} | 64.,Eself_totalL,Modbus RTU,,5,4,3142,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3143 | Reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3143,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3144 | Priority | Word Mode |  |  |  |  | 0:Invalid data 1:Reset setting parameters 2:Reset correction parameter 3:Clear historical power | TL_X-TL_XH |  |  | 0 | Type number : Priority "Growatt_Priority" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Priority"] | Number Growatt_Priority "Priority" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Priority"} | 64.,Priority,Modbus RTU,,5,4,3144,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3145 | EPSFac | UPS frequency |  |  | 0.01Hz |  |  | BMS | 0.01 | Hz | 2 | Type number : EPSFac "Growatt_EPSFac" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSFac"] | Number:Frequency Growatt_EPSFac "EPSFac [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSFac"} | 64.,EPSFac,Modbus RTU,,5,4,3145,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255
| 4 | 3146 | EPSVac1 | UPS phase R output voltage |  |  | 0.1V |  |  | UPS | 0.1 | V | 1 | Type number : EPSVac1 "Growatt_EPSVac1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSVac1"] | Number:ElectricPotential Growatt_EPSVac1 "EPSVac1 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSVac1"} | 64.,EPSVac1,Modbus RTU,,5,4,3146,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3147 | EPSIac1 | UPS phase R output current |  |  | 0.1A |  |  | BMS | 0.1 | A | 1 | Type number : EPSIac1 "Growatt_EPSIac1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSIac1"] | Number:ElectricCurrent Growatt_EPSIac1 "EPSIac1 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSIac1"} | 64.,EPSIac1,Modbus RTU,,5,4,3147,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3148 | EPSPac1H | UPS phase R output power |  |  | 0.1W |  |  | BMS | 0.1 | W | 1 | Type number : EPSPac1H "Growatt_EPSPac1H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac1H"] | Number:Power Growatt_EPSPac1H "EPSPac1H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac1H"} | 64.,EPSPac1H,Modbus RTU,,5,4,3148,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3149 | EPSPac1L | [5 empty] | R SPH6K | BMS |  |  | 0 | Type number : EPSPac1L "Growatt_EPSPac1L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac1L"] | Number Growatt_EPSPac1L "EPSPac1L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac1L"} | 64.,EPSPac1L,Modbus RTU,,5,4,3149,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3150 | EPSVac2 | UPS phase S output voltage |  |  | 0.1V |  | No use | UPS | 0.1 | V | 1 | Type number : EPSVac2 "Growatt_EPSVac2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSVac2"] | Number:ElectricPotential Growatt_EPSVac2 "EPSVac2 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSVac2"} | 64.,EPSVac2,Modbus RTU,,5,4,3150,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3151 | EPSIac2 | UPS phase S output current |  |  | 0.1A |  |  | BMS | 0.1 | A | 1 | Type number : EPSIac2 "Growatt_EPSIac2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSIac2"] | Number:ElectricCurrent Growatt_EPSIac2 "EPSIac2 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSIac2"} | 64.,EPSIac2,Modbus RTU,,5,4,3151,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3152 | EPSPac2H | UPS phase S output power |  |  | 0.1W |  |  | BMS | 0.1 | W | 1 | Type number : EPSPac2H "Growatt_EPSPac2H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac2H"] | Number:Power Growatt_EPSPac2H "EPSPac2H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac2H"} | 64.,EPSPac2H,Modbus RTU,,5,4,3152,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3153 | EPSPac2L | [6 empty] | BMS |  |  | 0 | Type number : EPSPac2L "Growatt_EPSPac2L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac2L"] | Number Growatt_EPSPac2L "EPSPac2L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac2L"} | 64.,EPSPac2L,Modbus RTU,,5,4,3153,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3154 | EPSVac3 | UPS phase T output voltage |  |  | 0.1V |  |  | UPS | 0.1 | V | 1 | Type number : EPSVac3 "Growatt_EPSVac3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSVac3"] | Number:ElectricPotential Growatt_EPSVac3 "EPSVac3 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSVac3"} | 64.,EPSVac3,Modbus RTU,,5,4,3154,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3155 | EPSIac3 | UPS phase T output current |  |  | 0.1A |  |  | BMS | 0.1 | A | 1 | Type number : EPSIac3 "Growatt_EPSIac3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSIac3"] | Number:ElectricCurrent Growatt_EPSIac3 "EPSIac3 [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSIac3"} | 64.,EPSIac3,Modbus RTU,,5,4,3155,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3156 | EPSPac3H | UPS phase T output power |  |  | 0.1W |  | Primary Value+1 | UPS | 0.1 | W | 1 | Type number : EPSPac3H "Growatt_EPSPac3H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac3H"] | Number:Power Growatt_EPSPac3H "EPSPac3H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac3H"} | 64.,EPSPac3H,Modbus RTU,,5,4,3156,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3157 | EPSPac3L | [6 empty] | UPS |  |  | 0 | Type number : EPSPac3L "Growatt_EPSPac3L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPac3L"] | Number Growatt_EPSPac3L "EPSPac3L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPac3L"} | 64.,EPSPac3L,Modbus RTU,,5,4,3157,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3158 | EPSPacH | UPS output power |  |  | 0.1W |  | No use | UPS | 0.1 | W | 1 | Type number : EPSPacH "Growatt_EPSPacH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPacH"] | Number:Power Growatt_EPSPacH "EPSPacH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPacH"} | 64.,EPSPacH,Modbus RTU,,5,4,3158,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3159 | EPSPacL | [6 empty] | UPS |  |  | 0 | Type number : EPSPacL "Growatt_EPSPacL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.EPSPacL"] | Number Growatt_EPSPacL "EPSPacL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EPSPacL"} | 64.,EPSPacL,Modbus RTU,,5,4,3159,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3160 | Loadpercent | Load percent of UPS ouput |  |  | 0.001 |  | suggestive | ALL | 0.001 |  | 3 | Type number : Loadpercent "Growatt_Loadpercent" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Loadpercent"] | Number Growatt_Loadpercent "Loadpercent [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Loadpercent"} | 64.,Loadpercent,Modbus RTU,,5,4,3160,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3161 | PF | Power factor |  |  | 0.1 |  |  | ALL | 0.1 |  | 1 | Type number : PF "Growatt_PF" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PF"] | Number Growatt_PF "PF [%0.1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PF"} | 64.,PF,Modbus RTU,,5,4,3161,1,9410,2,0,Unsigned int,0,1,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3162 | DCV | DC voltage |  |  | 1mV |  | SPA used | SPA | 1 | mV | 0 | Type number : DCV "Growatt_DCV" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.DCV"] | #N/A | 64.,DCV,Modbus RTU,,5,4,3162,1,9410,2,0,Unsigned int,0,0,mV,1,100,97,0,0,0,1.000000,0,255
| 4 | 3163 | Reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3163,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3164 | NewBdcFlag | Whether to parse BDC data separately | [5 empty] | ALL |  |  | 0 | Type number : NewBdcFlag "Growatt_NewBdcFlag" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.NewBdcFlag"] | Number Growatt_NewBdcFlag "NewBdcFlag" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewBdcFlag"} | 64.,NewBdcFlag,Modbus RTU,,5,4,3164,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3165 | BDCDeratingMode | BDCDeratingMode: | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BDCDeratingMode "Growatt_BDCDeratingMode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BDCDeratingMode"] | Number Growatt_BDCDeratingMode "BDCDeratingMode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BDCDeratingMode"} | 64.,BDCDeratingMode,Modbus RTU,,5,4,3165,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3166 | SysState_Mode | System work State and mode The upper 8 bits indicate the mode; | [5 empty] | Storage |  |  | 0 | Type number : SysState_Mode "Growatt_SysState_Mode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.SysState_Mode"] | Number Growatt_SysState_Mode "SysState_Mode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SysState_Mode"} | 64.,SysState_Mode,Modbus RTU,,5,4,3166,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3167 | FaultCode | Storge device fault code | [5 empty] | PV9_32 |  |  | 0 | Type number : FaultCode "Growatt_FaultCode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.FaultCode"] | Number Growatt_FaultCode "FaultCode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FaultCode"} | 64.,FaultCode,Modbus RTU,,5,4,3167,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3168 | WarnCode | Storge device warning code | [5 empty] | ALL |  |  | 0 | Type number : WarnCode "Growatt_WarnCode" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.WarnCode"] | Number Growatt_WarnCode "WarnCode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:WarnCode"} | 64.,WarnCode,Modbus RTU,,5,4,3168,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3169 | Vbat | Battery voltage |  |  | 0.01V |  |  | ALL | 0.01 | V | 2 | Type number : Vbat "Growatt_Vbat" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vbat"] | Number:ElectricPotential Growatt_Vbat "Vbat [%0.01f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbat"} | 64.,Vbat,Modbus RTU,,5,4,3169,1,9410,2,0,Unsigned int,0,2,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3170 | Ibat | Battery current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Ibat "Growatt_Ibat" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ibat"] | Number:ElectricCurrent Growatt_Ibat "Ibat [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ibat"} | 64.,Ibat,Modbus RTU,,5,4,3170,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3171 | ad | State of charge Capacity |  |  | 0.01 |  | Stop Discharge soc when | Storage | 0.01 |  | 2 | Type number : ad "Growatt_ad" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ad"] | Number Growatt_ad "ad [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ad"} | 64.,ad,Modbus RTU,,5,4,3171,1,9410,2,0,Unsigned int,0,2,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3172 | Vbus1 | Total BUS voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vbus1 "Growatt_Vbus1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vbus1"] | Number:ElectricPotential Growatt_Vbus1 "Vbus1 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbus1"} | 64.,Vbus1,Modbus RTU,,5,4,3172,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3173 | Vbus2 | On the BUS voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vbus2 "Growatt_Vbus2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vbus2"] | Number:ElectricPotential Growatt_Vbus2 "Vbus2 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbus2"} | 64.,Vbus2,Modbus RTU,,5,4,3173,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3174 | Ibb | BUCK-BOOST Current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Ibb "Growatt_Ibb" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Ibb"] | Number:ElectricCurrent Growatt_Ibb "Ibb [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Ibb"} | 64.,Ibb,Modbus RTU,,5,4,3174,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3175 | Illc | LLC Current |  |  | 0.1A |  |  | ALL | 0.1 | A | 1 | Type number : Illc "Growatt_Illc" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Illc"] | Number:ElectricCurrent Growatt_Illc "Illc [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Illc"} | 64.,Illc,Modbus RTU,,5,4,3175,1,9410,2,0,Unsigned int,0,1,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3176 | TempA | Temperture A |  |  | 0.1? |  |  | ALL | 0.1 | ? | 1 | Type number : TempA "Growatt_TempA" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.TempA"] | Number:Length Growatt_TempA "TempA [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TempA"} | 64.,TempA,Modbus RTU,,5,4,3176,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
| 4 | 3177 | TempB | Temperture B |  |  | 0.1? |  | 0:Not Reset | ALL | 0.1 | ? | 1 | Type number : TempB "Growatt_TempB" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.TempB"] | Number:Length Growatt_TempB "TempB [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TempB"} | 64.,TempB,Modbus RTU,,5,4,3177,1,9410,2,0,Unsigned int,0,1,?,1,100,97,0,0,0,1.000000,0,255
| 4 | 3178 | PdischrH | Discharge power |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PdischrH "Growatt_PdischrH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PdischrH"] | Number:Power Growatt_PdischrH "PdischrH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PdischrH"} | 64.,PdischrH,Modbus RTU,,5,4,3178,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3179 | PdischrL | [6 empty] | ALL |  |  | 0 | Type number : PdischrL "Growatt_PdischrL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PdischrL"] | Number Growatt_PdischrL "PdischrL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PdischrL"} | 64.,PdischrL,Modbus RTU,,5,4,3179,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3180 | PchrH | Charge power |  |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : PchrH "Growatt_PchrH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PchrH"] | Number:Power Growatt_PchrH "PchrH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PchrH"} | 64.,PchrH,Modbus RTU,,5,4,3180,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3181 | PchrL | [6 empty] | ALL |  |  | 0 | Type number : PchrL "Growatt_PchrL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.PchrL"] | Number Growatt_PchrL "PchrL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PchrL"} | 64.,PchrL,Modbus RTU,,5,4,3181,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3182 | Edischr_totalH | Discharge total energy of storge device |  |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Edischr_totalH "Growatt_Edischr_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Edischr_totalH"] | Number:Energy Growatt_Edischr_totalH "Edischr_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Edischr_totalH"} | 64.,Edischr_totalH,Modbus RTU,,5,4,3182,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3183 | Edischr_totalL | [6 empty] | BMS |  |  | 0 | Type number : Edischr_totalL "Growatt_Edischr_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Edischr_totalL"] | Number Growatt_Edischr_totalL "Edischr_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Edischr_totalL"} | 64.,Edischr_totalL,Modbus RTU,,5,4,3183,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3184 | Echr_totalH | Charge total energy of storge device |  |  | 0.1kWh |  | SPA used | BMS | 0.1 | kWh | 1 | Type number : Echr_totalH "Growatt_Echr_totalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Echr_totalH"] | Number:Energy Growatt_Echr_totalH "Echr_totalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Echr_totalH"} | 64.,Echr_totalH,Modbus RTU,,5,4,3184,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3185 | Echr_totalL | [5 empty] | SPA used | BMS |  |  | 0 | Type number : Echr_totalL "Growatt_Echr_totalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Echr_totalL"] | Number Growatt_Echr_totalL "Echr_totalL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Echr_totalL"} | 64.,Echr_totalL,Modbus RTU,,5,4,3185,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3186 | Reserved | Reserved |  |  |  |  | digital | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3186,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3187 | BDC1_Flag | BDC mark (charge and discharge, fault alarm code) | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BDC1_Flag "Growatt_BDC1_Flag" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BDC1_Flag"] | Number Growatt_BDC1_Flag "BDC1_Flag" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BDC1_Flag"} | 64.,BDC1_Flag,Modbus RTU,,5,4,3187,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3188 | Vbus2 | Lower BUS voltage |  |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vbus2 "Growatt_Vbus2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Vbus2"] | Number:ElectricPotential Growatt_Vbus2 "Vbus2 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbus2"} | 64.,Vbus2,Modbus RTU,,5,4,3188,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3189 | BmsMaxVoltCellNo | BmsMaxVoltCellNo | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BmsMaxVoltCellNo "Growatt_BmsMaxVoltCellNo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsMaxVoltCellNo"] | Number Growatt_BmsMaxVoltCellNo "BmsMaxVoltCellNo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsMaxVoltCellNo"} | 64.,BmsMaxVoltCellNo,Modbus RTU,,5,4,3189,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3190 | BmsMinVoltCellNo | BmsMinVoltCellNo | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BmsMinVoltCellNo "Growatt_BmsMinVoltCellNo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsMinVoltCellNo"] | Number Growatt_BmsMinVoltCellNo "BmsMinVoltCellNo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsMinVoltCellNo"} | 64.,BmsMinVoltCellNo,Modbus RTU,,5,4,3190,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3191 | BmsBatteryAvgTemp | BmsBatteryAvgTemp | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BmsBatteryAvgTemp "Growatt_BmsBatteryAvgTemp" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsBatteryAvgTemp"] | Number Growatt_BmsBatteryAvgTemp "BmsBatteryAvgTemp" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsBatteryAvgTemp"} | 64.,BmsBatteryAvgTemp,Modbus RTU,,5,4,3191,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3192 | BmsMaxCellTemp | BmsMaxCellTemp |  |  | 0.1°C |  |  | TL_X-TL_XH | 0.1 | °C | 1 | Type number : BmsMaxCellTemp "Growatt_BmsMaxCellTemp" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsMaxCellTemp"] | Number:Temperature Growatt_BmsMaxCellTemp "BmsMaxCellTemp [%0.1f °C]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsMaxCellTemp"} | 64.,BmsMaxCellTemp,Modbus RTU,,5,4,3192,1,9410,2,0,Unsigned int,0,1,°C,1,100,97,0,0,0,1.000000,0,255
| 4 | 3193 | BmsBatteryAvgTemp | BmsBatteryAvgTemp |  |  | 0.1°C |  |  | TL_X-TL_XH | 0.1 | °C | 1 | Type number : BmsBatteryAvgTemp "Growatt_BmsBatteryAvgTemp" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsBatteryAvgTemp"] | Number:Temperature Growatt_BmsBatteryAvgTemp "BmsBatteryAvgTemp [%0.1f °C]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsBatteryAvgTemp"} | 64.,BmsBatteryAvgTemp,Modbus RTU,,5,4,3193,1,9410,2,0,Unsigned int,0,1,°C,1,100,97,0,0,0,1.000000,0,255
| 4 | 3194 | BmsMaxCellTemp | BmsMaxCellTemp |  |  |  |  | Total energy of user load | TL_X-TL_XH |  |  | 0 | Type number : BmsMaxCellTemp "Growatt_BmsMaxCellTemp" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsMaxCellTemp"] | Number Growatt_BmsMaxCellTemp "BmsMaxCellTemp" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsMaxCellTemp"} | 64.,BmsMaxCellTemp,Modbus RTU,,5,4,3194,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3195 | BmsBatteryAvgTemp | BmsBatteryAvgTemp | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BmsBatteryAvgTemp "Growatt_BmsBatteryAvgTemp" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsBatteryAvgTemp"] | Number Growatt_BmsBatteryAvgTemp "BmsBatteryAvgTemp" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsBatteryAvgTemp"} | 64.,BmsBatteryAvgTemp,Modbus RTU,,5,4,3195,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3196 | BmsMaxSOC | BmsMaxSOC |  |  | 0.01 |  | Today energy of user load | TL_X-TL_XH | 0.01 |  | 2 | Type number : BmsMaxSOC "Growatt_BmsMaxSOC" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsMaxSOC"] | Number Growatt_BmsMaxSOC "BmsMaxSOC [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsMaxSOC"} | 64.,BmsMaxSOC,Modbus RTU,,5,4,3196,1,9410,2,0,Unsigned int,0,2,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3197 | BmsMinSOC | BmsMinSOC |  |  | 0.01 |  | Total energy to grid | TL_X-TL_XH | 0.01 |  | 2 | Type number : BmsMinSOC "Growatt_BmsMinSOC" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsMinSOC"] | Number Growatt_BmsMinSOC "BmsMinSOC [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsMinSOC"} | 64.,BmsMinSOC,Modbus RTU,,5,4,3197,1,9410,2,0,Unsigned int,0,2,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3198 | ParallelBatteryNum | ParallelBatteryNum | [5 empty] | ALL |  |  | 0 | Type number : ParallelBatteryNum "Growatt_ParallelBatteryNum" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.ParallelBatteryNum"] | Number Growatt_ParallelBatteryNum "ParallelBatteryNum" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ParallelBatteryNum"} | 64.,ParallelBatteryNum,Modbus RTU,,5,4,3198,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3199 | BmsDerateReason | BmsDerateReason | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BmsDerateReason "Growatt_BmsDerateReason" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsDerateReason"] | Number Growatt_BmsDerateReason "BmsDerateReason" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsDerateReason"} | 64.,BmsDerateReason,Modbus RTU,,5,4,3199,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3200 | BmsGaugeFCCAh | BmsGaugeFCC(Ah) | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BmsGaugeFCCAh "Growatt_BmsGaugeFCCAh" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsGaugeFCCAh"] | Number Growatt_BmsGaugeFCCAh "BmsGaugeFCCAh" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsGaugeFCCAh"} | 64.,BmsGaugeFCCAh,Modbus RTU,,5,4,3200,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3201 | BmsGaugeRMAh | BmsGaugeRM(Ah) | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BmsGaugeRMAh "Growatt_BmsGaugeRMAh" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsGaugeRMAh"] | Number Growatt_BmsGaugeRMAh "BmsGaugeRMAh" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsGaugeRMAh"} | 64.,BmsGaugeRMAh,Modbus RTU,,5,4,3201,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3202 | BmsError | BMS Protect1 | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BmsError "Growatt_BmsError" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsError"] | Number Growatt_BmsError "BmsError" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsError"} | 64.,BmsError,Modbus RTU,,5,4,3202,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3203 | BmsWarn | BMSWarn1 |  |  |  |  | Total energy to user | TL_X-TL_XH |  |  | 0 | Type number : BmsWarn "Growatt_BmsWarn" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsWarn"] | Number Growatt_BmsWarn "BmsWarn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsWarn"} | 64.,BmsWarn,Modbus RTU,,5,4,3203,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3204 | BmsFault | BMS Fault1 | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BmsFault "Growatt_BmsFault" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsFault"] | Number Growatt_BmsFault "BmsFault" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsFault"} | 64.,BmsFault,Modbus RTU,,5,4,3204,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3205 | BmsFault2 | BMS Fault2 | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BmsFault2 "Growatt_BmsFault2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsFault2"] | Number Growatt_BmsFault2 "BmsFault2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsFault2"} | 64.,BmsFault2,Modbus RTU,,5,4,3205,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3206 | Reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3206,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3207 | Reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3207,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3208 | Reserved | [5 empty] | digital | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3208,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3209 | Reserved | [5 empty] | The power rate when exportLimit | TL_X-TL_XH |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3209,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3210 | BatIsoStatus | Battery ISO detection status | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BatIsoStatus "Growatt_BatIsoStatus" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatIsoStatus"] | Number Growatt_BatIsoStatus "BatIsoStatus" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatIsoStatus"} | 64.,BatIsoStatus,Modbus RTU,,5,4,3210,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3211 | BattNeedCharge | battery work request |  | bit0:1: Prohibit chargin g,0: |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BattNeedCharge "Growatt_BattNeedCharge" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BattNeedCharge"] | Number Growatt_BattNeedCharge "BattNeedCharge" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BattNeedCharge"} | 64.,BattNeedCharge,Modbus RTU,,5,4,3211,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3212 | BMS_Status | battery working status | R | 0: dormancy |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BMS_Status "Growatt_BMS_Status" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_Status"] | Number Growatt_BMS_Status "BMS_Status" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_Status"} | 64.,BMS_Status,Modbus RTU,,5,4,3212,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3213 | BmsError2 | BMS Protect2 | R |  | 1 |  |  | TL_X-TL_XH | 1 |  | 0 | Type number : BmsError2 "Growatt_BmsError2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsError2"] | Number Growatt_BmsError2 "BmsError2 [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsError2"} | 64.,BmsError2,Modbus RTU,,5,4,3213,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3214 | BmsWarn2 | BMS Warn2 | R |  | 1 |  |  | TL_X-TL_XH | 1 |  | 0 | Type number : BmsWarn2 "Growatt_BmsWarn2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsWarn2"] | Number Growatt_BmsWarn2 "BmsWarn2 [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsWarn2"} | 64.,BmsWarn2,Modbus RTU,,5,4,3214,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3215 | BMS_SOC | BMS SOC | R |  | 0.01 |  | Output | TL_X-TL_XH | 0.01 |  | 2 | Type number : BMS_SOC "Growatt_BMS_SOC" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_SOC"] | Number Growatt_BMS_SOC "BMS_SOC [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_SOC"} | 64.,BMS_SOC,Modbus RTU,,5,4,3215,1,9410,2,0,Unsigned int,0,2,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3216 | BMS_BatteryVolt | BMS BatteryVolt | R |  | 0.01V |  | Today energy of AC charge | TL_X-TL_XH | 0.01 | V | 2 | Type number : BMS_BatteryVolt "Growatt_BMS_BatteryVolt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_BatteryVolt"] | Number:ElectricPotential Growatt_BMS_BatteryVolt "BMS_BatteryVolt [%0.01f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_BatteryVolt"} | 64.,BMS_BatteryVolt,Modbus RTU,,5,4,3216,1,9410,2,0,Unsigned int,0,2,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3217 | BMS_BatteryCurr | BMS BatteryCurr | R |  | 0.01A |  |  | TL_X-TL_XH | 0.01 | A | 2 | Type number : BMS_BatteryCurr "Growatt_BMS_BatteryCurr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_BatteryCurr"] | Number:ElectricCurrent Growatt_BMS_BatteryCurr "BMS_BatteryCurr [%0.01f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_BatteryCurr"} | 64.,BMS_BatteryCurr,Modbus RTU,,5,4,3217,1,9410,2,0,Unsigned int,0,2,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3218 | BMS_BatteryTemp | battery cell maximum temperature | R |  | 0.1°C |  | Total energy of AC charge | TL_X-TL_XH | 0.1 | °C | 1 | Type number : BMS_BatteryTemp "Growatt_BMS_BatteryTemp" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_BatteryTemp"] | Number:Temperature Growatt_BMS_BatteryTemp "BMS_BatteryTemp [%0.1f °C]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_BatteryTemp"} | 64.,BMS_BatteryTemp,Modbus RTU,,5,4,3218,1,9410,2,0,Unsigned int,0,1,°C,1,100,97,0,0,0,1.000000,0,255
| 4 | 3219 | BMS_MaxCurr | Maximum charging current | R |  | 0.01A |  | bitfield | TL_X-TL_XH | 0.01 | A | 2 | Type number : BMS_MaxCurr "Growatt_BMS_MaxCurr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_MaxCurr"] | Number:ElectricCurrent Growatt_BMS_MaxCurr "BMS_MaxCurr [%0.01f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_MaxCurr"} | 64.,BMS_MaxCurr,Modbus RTU,,5,4,3219,1,9410,2,0,Unsigned int,0,2,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3220 | BMS_MaxDischrCurr | Maximum discharge current | R |  | 0.01A |  | bitfield | TL_X-TL_XH | 0.01 | A | 2 | Type number : BMS_MaxDischrCurr "Growatt_BMS_MaxDischrCurr" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_MaxDischrCurr"] | Number:ElectricCurrent Growatt_BMS_MaxDischrCurr "BMS_MaxDischrCurr [%0.01f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_MaxDischrCurr"} | 64.,BMS_MaxDischrCurr,Modbus RTU,,5,4,3220,1,9410,2,0,Unsigned int,0,2,A,1,100,97,0,0,0,1.000000,0,255
| 4 | 3221 | BMS_CycleCnt | BMSCycleCnt | R |  | 1 |  |  | TL_X-TL_XH | 1 |  | 0 | Type number : BMS_CycleCnt "Growatt_BMS_CycleCnt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_CycleCnt"] | Number Growatt_BMS_CycleCnt "BMS_CycleCnt [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_CycleCnt"} | 64.,BMS_CycleCnt,Modbus RTU,,5,4,3221,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3222 | BMS_SOH | BMS SOH | R |  | 1 |  | 0-20000 | TL_X-TL_XH | 1 |  | 0 | Type number : BMS_SOH "Growatt_BMS_SOH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_SOH"] | Number Growatt_BMS_SOH "BMS_SOH [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_SOH"} | 64.,BMS_SOH,Modbus RTU,,5,4,3222,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3223 | BMS_ChargeVoltLimit | Battery charging voltage limit value | R |  | 0.01V |  |  | TL_X-TL_XH | 0.01 | V | 2 | Type number : BMS_ChargeVoltLimit "Growatt_BMS_ChargeVoltLimit" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_ChargeVoltLimit"] | Number:ElectricPotential Growatt_BMS_ChargeVoltLimit "BMS_ChargeVoltLimit [%0.01f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_ChargeVoltLimit"} | 64.,BMS_ChargeVoltLimit,Modbus RTU,,5,4,3223,1,9410,2,0,Unsigned int,0,2,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3224 | BMS_DischargeVoltLimit | Battery discharge voltage limit value |  |  |  |  | Today discharge energy | TL_X-TL_XH |  |  | 0 | Type number : BMS_DischargeVoltLimit "Growatt_BMS_DischargeVoltLimit" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMS_DischargeVoltLimit"] | Number Growatt_BMS_DischargeVoltLimit "BMS_DischargeVoltLimit" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_DischargeVoltLimit"} | 64.,BMS_DischargeVoltLimit,Modbus RTU,,5,4,3224,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3225 | BmsWarn3 | BMS Warn 3 | R |  | 1 |  | Today energy to user | TL_X-TL_XH | 1 |  | 0 | Type number : BmsWarn3 "Growatt_BmsWarn3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsWarn3"] | Number Growatt_BmsWarn3 "BmsWarn3 [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsWarn3"} | 64.,BmsWarn3,Modbus RTU,,5,4,3225,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3226 | BmsError3 | BMS Protect3 | R |  | 1 |  |  | TL_X-TL_XH | 1 |  | 0 | Type number : BmsError3 "Growatt_BmsError3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BmsError3"] | Number Growatt_BmsError3 "BmsError3 [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BmsError3"} | 64.,BmsError3,Modbus RTU,,5,4,3226,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3227 | Reserved | [5 empty] | ASCII | TL_X-TL_XH |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3227,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3228 | Reserved | [5 empty] | ASCII | TL_X-TL_XH |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3228,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3229 | Reserved | [5 empty] | ASCII | TL_X-TL_XH |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserved"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} | 64.,Reserved,Modbus RTU,,5,4,3229,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3230 | BMSSingleVoltMax | BMS Battery SingleVoltMax | R |  | 0.001V |  | Today energy to grid | TL_X-TL_XH | 0.001 | V | 3 | Type number : BMSSingleVoltMax "Growatt_BMSSingleVoltMax" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMSSingleVoltMax"] | Number:ElectricPotential Growatt_BMSSingleVoltMax "BMSSingleVoltMax [%0.001f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMSSingleVoltMax"} | 64.,BMSSingleVoltMax,Modbus RTU,,5,4,3230,1,9410,2,0,Unsigned int,0,3,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3231 | BMSSingleVoltMin | BMS Battery SingleVoltMin | R |  | 0.001V |  |  | TL_X-TL_XH | 0.001 | V | 3 | Type number : BMSSingleVoltMin "Growatt_BMSSingleVoltMin" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BMSSingleVoltMin"] | Number:ElectricPotential Growatt_BMSSingleVoltMin "BMSSingleVoltMin [%0.001f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMSSingleVoltMin"} | 64.,BMSSingleVoltMin,Modbus RTU,,5,4,3231,1,9410,2,0,Unsigned int,0,3,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3232 | BatLoadVolt | Battery LoadVolt | R |  | 0.01V |  |  | TL_X-TL_XH | 0.01 | V | 2 | Type number : BatLoadVolt "Growatt_BatLoadVolt" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatLoadVolt"] | Number:ElectricPotential Growatt_BatLoadVolt "BatLoadVolt [%0.01f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatLoadVolt"} | 64.,BatLoadVolt,Modbus RTU,,5,4,3232,1,9410,2,0,Unsigned int,0,2,V,1,100,97,0,0,0,1.000000,0,255
| 4 | 3234 | Debugdata1 | Debug data1 | R |  |  |  | SPA used | SPA |  |  | 0 | Type number : Debugdata1 "Growatt_Debugdata1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata1"] | Number Growatt_Debugdata1 "Debugdata1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata1"} | 64.,Debugdata1,Modbus RTU,,5,4,3234,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3235 | Debugdata2 | Debug data2 | R |  |  |  | SPA | SPA |  |  | 0 | Type number : Debugdata2 "Growatt_Debugdata2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata2"] | Number Growatt_Debugdata2 "Debugdata2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata2"} | 64.,Debugdata2,Modbus RTU,,5,4,3235,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3236 | Debugdata3 | Debug data3 | R |  |  |  | BatVolt(DSP) | SPA |  |  | 0 | Type number : Debugdata3 "Growatt_Debugdata3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata3"] | Number Growatt_Debugdata3 "Debugdata3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata3"} | 64.,Debugdata3,Modbus RTU,,5,4,3236,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3237 | Debugdata4 | Debug data4 | R |  |  |  | reserved | SPA |  |  | 0 | Type number : Debugdata4 "Growatt_Debugdata4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata4"] | Number Growatt_Debugdata4 "Debugdata4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata4"} | 64.,Debugdata4,Modbus RTU,,5,4,3237,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3238 | Debugdata5 | Debug data5 | R |  |  |  | SPA | SPA |  |  | 0 | Type number : Debugdata5 "Growatt_Debugdata5" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata5"] | Number Growatt_Debugdata5 "Debugdata5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata5"} | 64.,Debugdata5,Modbus RTU,,5,4,3238,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3239 | Debugdata6 | Debug data6 | R |  |  |  | SPA | SPA |  |  | 0 | Type number : Debugdata6 "Growatt_Debugdata6" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata6"] | Number Growatt_Debugdata6 "Debugdata6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata6"} | 64.,Debugdata6,Modbus RTU,,5,4,3239,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3240 | Debugdata7 | Debug data7 | R |  |  |  | SPA | SPA |  |  | 0 | Type number : Debugdata7 "Growatt_Debugdata7" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata7"] | Number Growatt_Debugdata7 "Debugdata7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata7"} | 64.,Debugdata7,Modbus RTU,,5,4,3240,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3241 | Debugdata8 | Debug data8 | R |  |  |  | SPA | SPA |  |  | 0 | Type number : Debugdata8 "Growatt_Debugdata8" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata8"] | Number Growatt_Debugdata8 "Debugdata8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata8"} | 64.,Debugdata8,Modbus RTU,,5,4,3241,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3242 | Debugdata9 | Debug data9 | R |  |  |  | SPA | SPA |  |  | 0 | Type number : Debugdata9 "Growatt_Debugdata9" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata9"] | Number Growatt_Debugdata9 "Debugdata9" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata9"} | 64.,Debugdata9,Modbus RTU,,5,4,3242,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3243 | Debugdata10 | Debug data10 | R |  |  |  | SPA used | SPA |  |  | 0 | Type number : Debugdata10 "Growatt_Debugdata10" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata10"] | Number Growatt_Debugdata10 "Debugdata10" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata10"} | 64.,Debugdata10,Modbus RTU,,5,4,3243,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3244 | Debugdata10 | Debug data10 | R |  |  |  | SPA used | SPA |  |  | 0 | Type number : Debugdata10 "Growatt_Debugdata10" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata10"] | Number Growatt_Debugdata10 "Debugdata10" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata10"} | 64.,Debugdata10,Modbus RTU,,5,4,3244,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3245 | Debugdata12 | Debug data12 | R |  |  |  | SPA used | SPA |  |  | 0 | Type number : Debugdata12 "Growatt_Debugdata12" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata12"] | Number Growatt_Debugdata12 "Debugdata12" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata12"} | 64.,Debugdata12,Modbus RTU,,5,4,3245,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3246 | Debugdata13 | Debug data13 | R |  |  |  | SPA used | SPA |  |  | 0 | Type number : Debugdata13 "Growatt_Debugdata13" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata13"] | Number Growatt_Debugdata13 "Debugdata13" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata13"} | 64.,Debugdata13,Modbus RTU,,5,4,3246,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3247 | Debugdata14 | Debug data14 | R |  |  |  | Remotely set power | SPA |  |  | 0 | Type number : Debugdata14 "Growatt_Debugdata14" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata14"] | Number Growatt_Debugdata14 "Debugdata14" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata14"} | 64.,Debugdata14,Modbus RTU,,5,4,3247,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3248 | Debugdata15 | Debug data15 | R |  |  |  | Remote setup enable | SPA |  |  | 0 | Type number : Debugdata15 "Growatt_Debugdata15" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata15"] | Number Growatt_Debugdata15 "Debugdata15" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata15"} | 64.,Debugdata15,Modbus RTU,,5,4,3248,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3249 | Debugdata16 | Debug data16 | R |  |  |  | SPA | SPA |  |  | 0 | Type number : Debugdata16 "Growatt_Debugdata16" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Debugdata16"] | Number Growatt_Debugdata16 "Debugdata16" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Debugdata16"} | 64.,Debugdata16,Modbus RTU,,5,4,3249,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3250 | Pex1H | PV inverter 1 output power H | R |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pex1H "Growatt_Pex1H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pex1H"] | Number:Power Growatt_Pex1H "Pex1H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pex1H"} | 64.,Pex1H,Modbus RTU,,5,4,3250,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3251 | Pex1L | PV inverter 1 output power L | R |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pex1L "Growatt_Pex1L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pex1L"] | Number:Power Growatt_Pex1L "Pex1L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pex1L"} | 64.,Pex1L,Modbus RTU,,5,4,3251,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3252 | Pex2H | PV inverter 2 output power H | R |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pex2H "Growatt_Pex2H" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pex2H"] | Number:Power Growatt_Pex2H "Pex2H [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pex2H"} | 64.,Pex2H,Modbus RTU,,5,4,3252,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3253 | Pex2L | PV inverter 2 output power L | R |  | 0.1W |  |  | ALL | 0.1 | W | 1 | Type number : Pex2L "Growatt_Pex2L" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Pex2L"] | Number:Power Growatt_Pex2L "Pex2L [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Pex2L"} | 64.,Pex2L,Modbus RTU,,5,4,3253,1,9410,4,0,Unsigned int,0,1,W,1,100,97,0,0,0,1.000000,0,255
| 4 | 3254 | Eex1TodayH | PV inverter 1 energy Today H | R |  | 0.1kWh |  | Energy today | BMS | 0.1 | kWh | 1 | Type number : Eex1TodayH "Growatt_Eex1TodayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eex1TodayH"] | Number:Energy Growatt_Eex1TodayH "Eex1TodayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eex1TodayH"} | 64.,Eex1TodayH,Modbus RTU,,5,4,3254,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3255 | Eex1TodayL | PV inverter 1 energy Today L | R |  | 0.1kWh |  | CAN ID : 0x323 | BMS | 0.1 | kWh | 1 | Type number : Eex1TodayL "Growatt_Eex1TodayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eex1TodayL"] | Number:Energy Growatt_Eex1TodayL "Eex1TodayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eex1TodayL"} | 64.,Eex1TodayL,Modbus RTU,,5,4,3255,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3256 | Eex2TodayH | PV inverter 2 energy Today H | R |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eex2TodayH "Growatt_Eex2TodayH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eex2TodayH"] | Number:Energy Growatt_Eex2TodayH "Eex2TodayH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eex2TodayH"} | 64.,Eex2TodayH,Modbus RTU,,5,4,3256,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3257 | Eex2TodayL | PV inverter 2 energy Today L | R |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eex2TodayL "Growatt_Eex2TodayL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eex2TodayL"] | Number:Energy Growatt_Eex2TodayL "Eex2TodayL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eex2TodayL"} | 64.,Eex2TodayL,Modbus RTU,,5,4,3257,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3258 | Eex1TotalH | PV inverter 1 energy Total H | R |  | 0.1kWh |  | CAN ID : 0x323 | BMS | 0.1 | kWh | 1 | Type number : Eex1TotalH "Growatt_Eex1TotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eex1TotalH"] | Number:Energy Growatt_Eex1TotalH "Eex1TotalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eex1TotalH"} | 64.,Eex1TotalH,Modbus RTU,,5,4,3258,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3259 | Eex1TotalL | PV inverter 1 energy Total L | R |  | 0.1kWh |  | CAN ID : 0x323 | BMS | 0.1 | kWh | 1 | Type number : Eex1TotalL "Growatt_Eex1TotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eex1TotalL"] | Number:Energy Growatt_Eex1TotalL "Eex1TotalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eex1TotalL"} | 64.,Eex1TotalL,Modbus RTU,,5,4,3259,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3260 | Eex2TotalH | PV inverter 2 energy Total H | R |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eex2TotalH "Growatt_Eex2TotalH" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eex2TotalH"] | Number:Energy Growatt_Eex2TotalH "Eex2TotalH [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eex2TotalH"} | 64.,Eex2TotalH,Modbus RTU,,5,4,3260,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3261 | Eex2TotalL | PV inverter 2 energy Total L | R |  | 0.1kWh |  |  | BMS | 0.1 | kWh | 1 | Type number : Eex2TotalL "Growatt_Eex2TotalL" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Eex2TotalL"] | Number:Energy Growatt_Eex2TotalL "Eex2TotalL [%0.1f kWh]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Eex2TotalL"} | 64.,Eex2TotalL,Modbus RTU,,5,4,3261,1,9410,4,0,Unsigned int,0,1,kWh,1,100,97,0,0,0,1.000000,0,255
| 4 | 3262 | uwBatNo | battery pack number | R |  |  |  | ASCII | ALL |  |  | 0 | Type number : uwBatNo "Growatt_uwBatNo" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.uwBatNo"] | Number Growatt_uwBatNo "uwBatNo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwBatNo"} | 64.,uwBatNo,Modbus RTU,,5,4,3262,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3263 | BatSerialNum1 | Battery pack serial numberSN[0]SN[1] | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNum1 "Growatt_BatSerialNum1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatSerialNum1"] | Number Growatt_BatSerialNum1 "BatSerialNum1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNum1"} | 64.,BatSerialNum1,Modbus RTU,,5,4,3263,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3264 | BatSerialNum2 | Battery pack serial numberSN[2]SN[3] | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNum2 "Growatt_BatSerialNum2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatSerialNum2"] | Number Growatt_BatSerialNum2 "BatSerialNum2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNum2"} | 64.,BatSerialNum2,Modbus RTU,,5,4,3264,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3265 | BatSerialNum3 | Battery pack serial numberSN[4]SN[5] | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNum3 "Growatt_BatSerialNum3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatSerialNum3"] | Number Growatt_BatSerialNum3 "BatSerialNum3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNum3"} | 64.,BatSerialNum3,Modbus RTU,,5,4,3265,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3266 | BatSerialNum4 | Battery pack serial numberSN[6]SN[7] | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNum4 "Growatt_BatSerialNum4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatSerialNum4"] | Number Growatt_BatSerialNum4 "BatSerialNum4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNum4"} | 64.,BatSerialNum4,Modbus RTU,,5,4,3266,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3267 | BatSerialNum5 | Battery pack serial numberSN[8]SN[9] | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNum5 "Growatt_BatSerialNum5" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatSerialNum5"] | Number Growatt_BatSerialNum5 "BatSerialNum5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNum5"} | 64.,BatSerialNum5,Modbus RTU,,5,4,3267,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3268 | BatSerialNum6 | Battery pack serial numberSN[10]SN[11] | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNum6 "Growatt_BatSerialNum6" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatSerialNum6"] | Number Growatt_BatSerialNum6 "BatSerialNum6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNum6"} | 64.,BatSerialNum6,Modbus RTU,,5,4,3268,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3269 | BatSerialNum7 | Battery pack serial numberSN[12]SN[13] | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNum7 "Growatt_BatSerialNum7" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatSerialNum7"] | Number Growatt_BatSerialNum7 "BatSerialNum7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNum7"} | 64.,BatSerialNum7,Modbus RTU,,5,4,3269,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3270 | BatSerialNum8 | Battery pack serial numberSN[14]SN[15] | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNum8 "Growatt_BatSerialNum8" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BatSerialNum8"] | Number Growatt_BatSerialNum8 "BatSerialNum8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNum8"} | 64.,BatSerialNum8,Modbus RTU,,5,4,3270,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | 3280 | bClrTodayDataFlag | Clear day data flag | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bClrTodayDataFlag "Growatt_bClrTodayDataFlag" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.bClrTodayDataFlag"] | Number Growatt_bClrTodayDataFlag "bClrTodayDataFlag" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bClrTodayDataFlag"} | 64.,bClrTodayDataFlag,Modbus RTU,,5,4,3280,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | '3271-3279 | Reserve | Reserve |  |  |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : Reserve "Growatt_Reserve" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.Reserve"] | Number Growatt_Reserve "Reserve" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserve"} | 64.,Reserve,Modbus RTU,,5,4,'3271-3279,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | '4000-4107 | BDCBlock1 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number). | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BDCBlock1 "Growatt_BDCBlock1" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BDCBlock1"] | Number Growatt_BDCBlock1 "BDCBlock1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BDCBlock1"} | 64.,BDCBlock1,Modbus RTU,,5,4,'4000-4107,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | '4108-4215 | BDCBlock2 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number). | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BDCBlock2 "Growatt_BDCBlock2" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BDCBlock2"] | Number Growatt_BDCBlock2 "BDCBlock2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BDCBlock2"} | 64.,BDCBlock2,Modbus RTU,,5,4,'4108-4215,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | '4864-4971 | BDCBlock3 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number). | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BDCBlock3 "Growatt_BDCBlock3" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BDCBlock3"] | Number Growatt_BDCBlock3 "BDCBlock3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BDCBlock3"} | 64.,BDCBlock3,Modbus RTU,,5,4,'4864-4971,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
| 4 | '4972-5079 | BDCBlock4 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number). | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BDCBlock4 "Growatt_BDCBlock4" [stateTopic="tele/WSABINV", transformationPattern="JSONPATH:$.BDCBlock4"] | Number Growatt_BDCBlock4 "BDCBlock4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BDCBlock4"} | 64.,BDCBlock4,Modbus RTU,,5,4,'4972-5079,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255
X | 3 | 0 | OnOff | Remote On/Off . On(1);Off(0)Inverter On(3);Off(2)BDC | R/W | 0?1?2? 3 |  | 1 |  | ALL |  |  | 0 | Type number : OnOff "Growatt_OnOff" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.OnOff", formatBeforePublish="OnOff%s"] | Number Growatt_OnOff "OnOff" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OnOff"} | 65.,OnOff,Modbus RTU,,5,3,0,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,OnOff,5,0,0,2,0
| 3 | 1 | SaftyFuncEn | Bit0: SPI enable Bit1: AutoTestStart Bit2: LVFRT enable Bit3:FreqDerating Enable Bit4: Softstart enable Bit5: DRMS enable Bit6:PowerVoltFunc Enable Bit7: HVFRT enable Bit8:ROCOF enable Bit9: Recover FreqDeratingMode Enable Bit10:Split phase enable Bit10~15:?? | W | 00:00 disable 1: enable |  |  |  | Storage |  |  | 0 | Type number : SaftyFuncEn "Growatt_SaftyFuncEn" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SaftyFuncEn", formatBeforePublish="SaftyFuncEn%s"] | Number Growatt_SaftyFuncEn "SaftyFuncEn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SaftyFuncEn"} |  | 1,1,SaftyFuncEn,5,1,0,2,0
| 3 | 2 | PFCMD | Set Holding register3,4,5,99 CMD will be memory or not(1/0), if not, these settings are the initial value. | W | 0or1 |  | 0 |  | ALL |  |  | 0 | Type number : PFCMD "Growatt_PFCMD" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFCMD", formatBeforePublish="PFCMD%s"] | Number Growatt_PFCMD "PFCMD" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFCMD"} |  | 1,1,PFCMD,5,2,0,2,0
| 3 | 3 | ActiveP | Inverter Max output active power percent | W | 0-100 or | % | 255 |  | TL_X-TL_XH |  | % | 0 | Type number : ActiveP "Growatt_ActiveP" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ActiveP", formatBeforePublish="ActiveP%s"] | Number Growatt_ActiveP "ActiveP" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ActiveP"} |  | 1,1,ActiveP,5,3,0,2,0
| 3 | 4 | ReactiveP | Inverter max output reactive power percent | W | -100-100 or 255 | % | % | 0x00: Disable; | TL_X-TL_XH |  | % | 0 | Type number : ReactiveP "Growatt_ReactiveP" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ReactiveP", formatBeforePublish="ReactiveP%s"] | Number Growatt_ReactiveP "ReactiveP" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ReactiveP"} |  | 1,1,ReactiveP,5,4,0,2,0
| 3 | 5 | Powerfactor | Inverter output power factors 10000 times | W | 0-20000, |  |  | Same as Time 1 | USTimeSet |  |  | 0 | Type number : Powerfactor "Growatt_Powerfactor" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Powerfactor", formatBeforePublish="Powerfactor%s"] | Number Growatt_Powerfactor "Powerfactor" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Powerfactor"} |  | 1,1,Powerfactor,5,5,0,2,0
| 3 | 6 | PmaxH | Normal power (high) |  |  | 0.1W | 0.1VA | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : PmaxH "Growatt_PmaxH" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PmaxH", formatBeforePublish="PmaxH%s"] | Number:Power Growatt_PmaxH "PmaxH [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PmaxH"} |  | 1,1,PmaxH,5,6,0,2,0
| 3 | 7 | PmaxL | Normal power (low) |  |  | 0.1W | 0.1VA | Same as Time 1 | USTimeSet | 0.1 | W | 1 | Type number : PmaxL "Growatt_PmaxL" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PmaxL", formatBeforePublish="PmaxL%s"] | Number:Power Growatt_PmaxL "PmaxL [%0.1f W]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PmaxL"} |  | 1,1,PmaxL,5,7,0,2,0
| 3 | 8 | Vnormal | Normal work PV voltage |  |  | 0.1V | 0.1V |  | ALL | 0.1 | V | 1 | Type number : Vnormal "Growatt_Vnormal" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vnormal", formatBeforePublish="Vnormal%s"] | Number:ElectricPotential Growatt_Vnormal "Vnormal [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vnormal"} |  | 1,1,Vnormal,5,8,0,2,0
| 3 | 9 | FwversionH | Firmware version | [5 empty] | PV9_32 |  |  | 0 | Type number : FwversionH "Growatt_FwversionH" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FwversionH", formatBeforePublish="FwversionH%s"] | Number Growatt_FwversionH "FwversionH" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FwversionH"} |  | 1,1,FwversionH,5,9,0,2,0
| 3 | 10 | Fwversion | Firmware version | [5 empty] | PV9_32 |  |  | 0 | Type number : Fwversion "Growatt_Fwversion" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Fwversion", formatBeforePublish="Fwversion%s"] | Number Growatt_Fwversion "Fwversion" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Fwversion"} |  | 1,1,Fwversion,5,10,0,2,0
| 3 | 11 | FwversionL | Firmware version (low) | [5 empty] | PV9_32 |  |  | 0 | Type number : FwversionL "Growatt_FwversionL" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FwversionL", formatBeforePublish="FwversionL%s"] | Number Growatt_FwversionL "FwversionL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FwversionL"} |  | 1,1,FwversionL,5,11,0,2,0
| 3 | 12 | Fwversion2H | Control Firmware version (high) | [5 empty] | PV9_32 |  |  | 0 | Type number : Fwversion2H "Growatt_Fwversion2H" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Fwversion2H", formatBeforePublish="Fwversion2H%s"] | Number Growatt_Fwversion2H "Fwversion2H" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Fwversion2H"} |  | 1,1,Fwversion2H,5,12,0,2,0
| 3 | 13 | Fwversion2M | Control Firmware version (middle) | [5 empty] | PV9_32 |  |  | 0 | Type number : Fwversion2M "Growatt_Fwversion2M" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Fwversion2M", formatBeforePublish="Fwversion2M%s"] | Number Growatt_Fwversion2M "Fwversion2M" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Fwversion2M"} |  | 1,1,Fwversion2M,5,13,0,2,0
| 3 | 14 | Fwversion2L | Control Firmware version (low) | [5 empty] | PV9_32 |  |  | 0 | Type number : Fwversion2L "Growatt_Fwversion2L" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Fwversion2L", formatBeforePublish="Fwversion2L%s"] | Number Growatt_Fwversion2L "Fwversion2L" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Fwversion2L"} |  | 1,1,Fwversion2L,5,14,0,2,0
| 3 | 15 | LCDlanguage | LCD language | W | 0-5 |  |  |  | ALL |  |  | 0 | Type number : LCDlanguage "Growatt_LCDlanguage" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LCDlanguage", formatBeforePublish="LCDlanguage%s"] | Number Growatt_LCDlanguage "LCDlanguage" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:LCDlanguage"} |  | 1,1,LCDlanguage,5,15,0,2,0
| 3 | 16 | CountrySelected | Country Selected or not | W | 0: need |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : CountrySelected "Growatt_CountrySelected" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.CountrySelected", formatBeforePublish="CountrySelected%s"] | Number Growatt_CountrySelected "CountrySelected" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CountrySelected"} |  | 1,1,CountrySelected,5,16,0,2,0
| 3 | 17 | Vpvstart | Input start voltage | W |  | 0.1V | 0.1V |  | ALL | 0.1 | V | 1 | Type number : Vpvstart "Growatt_Vpvstart" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vpvstart", formatBeforePublish="Vpvstart%s"] | Number:ElectricPotential Growatt_Vpvstart "Vpvstart [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vpvstart"} |  | 1,1,Vpvstart,5,17,0,2,0
| 3 | 18 | Timestart | Start time | W |  |  | 1s | Anti-backflow failure default setting power percentage | ALL |  |  | 0 | Type number : Timestart "Growatt_Timestart" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Timestart", formatBeforePublish="Timestart%s"] | Number Growatt_Timestart "Timestart" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Timestart"} |  | 1,1,Timestart,5,18,0,2,0
| 3 | 19 | RestartDelayTime | Restart Delay Time after fault back; | W |  |  | 1s | Bat First | Storage |  |  | 0 | Type number : RestartDelayTime "Growatt_RestartDelayTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.RestartDelayTime", formatBeforePublish="RestartDelayTime%s"] | Number Growatt_RestartDelayTime "RestartDelayTime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:RestartDelayTime"} |  | 1,1,RestartDelayTime,5,19,0,2,0
| 3 | 20 | wPowerStartSlope | Power start slope | W | 1-1000 | 0.001 |  | 0 | ALL | 0.001 |  | 3 | Type number : wPowerStartSlope "Growatt_wPowerStartSlope" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.wPowerStartSlope", formatBeforePublish="wPowerStartSlope%s"] | Number Growatt_wPowerStartSlope "wPowerStartSlope [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:wPowerStartSlope"} |  | 1,1,wPowerStartSlope,5,20,0,2,0
| 3 | 21 | wPowerRestartSlopeEE | Power restart slope | W | 1-1000 | 0.001 |  |  | ALL | 0.001 |  | 3 | Type number : wPowerRestartSlopeEE "Growatt_wPowerRestartSlopeEE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.wPowerRestartSlopeEE", formatBeforePublish="wPowerRestartSlopeEE%s"] | Number Growatt_wPowerRestartSlopeEE "wPowerRestartSlopeEE [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:wPowerRestartSlopeEE"} |  | 1,1,wPowerRestartSlopeEE,5,21,0,2,0
| 3 | 22 | wSelectBaudrate | Select communicationbaudrat e | W | 0-1 |  | 0 | 255: power is not be limited | ALL |  |  | 0 | Type number : wSelectBaudrate "Growatt_wSelectBaudrate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.wSelectBaudrate", formatBeforePublish="wSelectBaudrate%s"] | Number Growatt_wSelectBaudrate "wSelectBaudrate" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:wSelectBaudrate"} |  | 1,1,wSelectBaudrate,5,22,0,2,0
| 3 | 23 | SerialNO | Serial number 1-2 |  |  |  |  | Charge | Storage |  |  | 0 | Type number : SerialNO "Growatt_SerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNO", formatBeforePublish="SerialNO%s"] | Number Growatt_SerialNO "SerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNO"} |  | 1,1,SerialNO,5,23,0,2,0
| 3 | 24 | SerialNO | Serial number 3-4 |  |  |  |  | Stop | Storage |  |  | 0 | Type number : SerialNO "Growatt_SerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNO", formatBeforePublish="SerialNO%s"] | Number Growatt_SerialNO "SerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNO"} |  | 1,1,SerialNO,5,24,0,2,0
| 3 | 25 | SerialNO | Serial number 5-6 |  |  |  |  | AC Charge | Storage |  |  | 0 | Type number : SerialNO "Growatt_SerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNO", formatBeforePublish="SerialNO%s"] | Number Growatt_SerialNO "SerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNO"} |  | 1,1,SerialNO,5,25,0,2,0
| 3 | 26 | SerialNO | Serial number 7-8 | [5 empty] | Storage |  |  | 0 | Type number : SerialNO "Growatt_SerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNO", formatBeforePublish="SerialNO%s"] | Number Growatt_SerialNO "SerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNO"} |  | 1,1,SerialNO,5,26,0,2,0
| 3 | 27 | SerialNO | Serial number 9-10 | [5 empty] | Storage |  |  | 0 | Type number : SerialNO "Growatt_SerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNO", formatBeforePublish="SerialNO%s"] | Number Growatt_SerialNO "SerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNO"} |  | 1,1,SerialNO,5,27,0,2,0
| 3 | 28 | ModuleH | Inverter Module (high) |  | &*5 |  |  |  | ALL |  |  | 0 | Type number : ModuleH "Growatt_ModuleH" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ModuleH", formatBeforePublish="ModuleH%s"] | Number Growatt_ModuleH "ModuleH" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ModuleH"} |  | 1,1,ModuleH,5,28,0,2,0
| 3 | 29 | ModuleL | Inverter Module (low) |  | &*5 |  |  |  | ALL |  |  | 0 | Type number : ModuleL "Growatt_ModuleL" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ModuleL", formatBeforePublish="ModuleL%s"] | Number Growatt_ModuleL "ModuleL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ModuleL"} |  | 1,1,ModuleL,5,29,0,2,0
| 3 | 30 | ComAddr | Communicate address | W | 1-254 |  | 1 | total | TL_X-TL_XH |  |  | 0 | Type number : ComAddr "Growatt_ComAddr" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ComAddr", formatBeforePublish="ComAddr%s"] | Number Growatt_ComAddr "ComAddr" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ComAddr"} |  | 1,1,ComAddr,5,30,0,2,0
| 3 | 31 | FlashStart | Update firmware | W | 1 |  |  |  | PV9_32 |  |  | 0 | Type number : FlashStart "Growatt_FlashStart" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FlashStart", formatBeforePublish="FlashStart%s"] | Number Growatt_FlashStart "FlashStart" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FlashStart"} |  | 1,1,FlashStart,5,31,0,2,0
| 3 | 32 | ResetUserInfo | Reset User Information | W | 0x0001 |  |  | SPA/ reserve | Storage |  |  | 0 | Type number : ResetUserInfo "Growatt_ResetUserInfo" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ResetUserInfo", formatBeforePublish="ResetUserInfo%s"] | Number Growatt_ResetUserInfo "ResetUserInfo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ResetUserInfo"} |  | 1,1,ResetUserInfo,5,32,0,2,0
| 3 | 33 | Resettofactory | Reset to factory | W | 0x0001 |  |  | SPA/ reserve | Storage |  |  | 0 | Type number : Resettofactory "Growatt_Resettofactory" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Resettofactory", formatBeforePublish="Resettofactory%s"] | Number Growatt_Resettofactory "Resettofactory" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Resettofactory"} |  | 1,1,Resettofactory,5,33,0,2,0
| 3 | 34 | ManufacturerInfo8 | Manufacturer information (high) | [5 empty] | ALL |  |  | 0 | Type number : ManufacturerInfo8 "Growatt_ManufacturerInfo8" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ManufacturerInfo8", formatBeforePublish="ManufacturerInfo8%s"] | Number Growatt_ManufacturerInfo8 "ManufacturerInfo8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ManufacturerInfo8"} |  | 1,1,ManufacturerInfo8,5,34,0,2,0
| 3 | 35 | ManufacturerInfo7 | Manufacturer information (middle) | [5 empty] | ALL |  |  | 0 | Type number : ManufacturerInfo7 "Growatt_ManufacturerInfo7" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ManufacturerInfo7", formatBeforePublish="ManufacturerInfo7%s"] | Number Growatt_ManufacturerInfo7 "ManufacturerInfo7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ManufacturerInfo7"} |  | 1,1,ManufacturerInfo7,5,35,0,2,0
| 3 | 36 | ManufacturerInfo6 | Manufacturer information (low) | [5 empty] | ALL |  |  | 0 | Type number : ManufacturerInfo6 "Growatt_ManufacturerInfo6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ManufacturerInfo6", formatBeforePublish="ManufacturerInfo6%s"] | Number Growatt_ManufacturerInfo6 "ManufacturerInfo6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ManufacturerInfo6"} |  | 1,1,ManufacturerInfo6,5,36,0,2,0
| 3 | 37 | ManufacturerInfo5 | Manufacturer information (high) | [5 empty] | ALL |  |  | 0 | Type number : ManufacturerInfo5 "Growatt_ManufacturerInfo5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ManufacturerInfo5", formatBeforePublish="ManufacturerInfo5%s"] | Number Growatt_ManufacturerInfo5 "ManufacturerInfo5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ManufacturerInfo5"} |  | 1,1,ManufacturerInfo5,5,37,0,2,0
| 3 | 38 | ManufacturerInfo4 | Manufacturer information (middle) | [5 empty] | ALL |  |  | 0 | Type number : ManufacturerInfo4 "Growatt_ManufacturerInfo4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ManufacturerInfo4", formatBeforePublish="ManufacturerInfo4%s"] | Number Growatt_ManufacturerInfo4 "ManufacturerInfo4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ManufacturerInfo4"} |  | 1,1,ManufacturerInfo4,5,38,0,2,0
| 3 | 39 | ManufacturerInfo3 | Manufacturer information (low) | [5 empty] | ALL |  |  | 0 | Type number : ManufacturerInfo3 "Growatt_ManufacturerInfo3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ManufacturerInfo3", formatBeforePublish="ManufacturerInfo3%s"] | Number Growatt_ManufacturerInfo3 "ManufacturerInfo3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ManufacturerInfo3"} |  | 1,1,ManufacturerInfo3,5,39,0,2,0
| 3 | 40 | ManufacturerInfo2 | Manufacturer information (low) | [5 empty] | ALL |  |  | 0 | Type number : ManufacturerInfo2 "Growatt_ManufacturerInfo2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ManufacturerInfo2", formatBeforePublish="ManufacturerInfo2%s"] | Number Growatt_ManufacturerInfo2 "ManufacturerInfo2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ManufacturerInfo2"} |  | 1,1,ManufacturerInfo2,5,40,0,2,0
| 3 | 41 | ManufacturerInfo1 | Manufacturer information (high) | [5 empty] | ALL |  |  | 0 | Type number : ManufacturerInfo1 "Growatt_ManufacturerInfo1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ManufacturerInfo1", formatBeforePublish="ManufacturerInfo1%s"] | Number Growatt_ManufacturerInfo1 "ManufacturerInfo1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ManufacturerInfo1"} |  | 1,1,ManufacturerInfo1,5,41,0,2,0
| 3 | 42 | bfailsafeEn; | G100 fail safe | W | Enable:1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bfailsafeEn; "Growatt_bfailsafeEn;" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bfailsafeEn;", formatBeforePublish="bfailsafeEn;%s"] | Number Growatt_bfailsafeEn; "bfailsafeEn;" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bfailsafeEn;"} |  | 1,1,bfailsafeEn;,5,42,0,2,0
| 3 | 43 | DTC | Device Type Code |  | &*6 |  |  |  | BMS |  |  | 0 | Type number : DTC "Growatt_DTC" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.DTC", formatBeforePublish="DTC%s"] | Number Growatt_DTC "DTC" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DTC"} |  | 1,1,DTC,5,43,0,2,0
| 3 | 44 | TP | Input tracker num and output phase num |  |  |  |  | reserved | ALL |  |  | 0 | Type number : TP "Growatt_TP" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.TP", formatBeforePublish="TP%s"] | Number Growatt_TP "TP" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TP"} |  | 1,1,TP,5,44,0,2,0
| 3 | 45 | SysYear | System time-year | W | Year offset is 0 |  |  | 0: output power not allowed | ALL |  |  | 0 | Type number : SysYear "Growatt_SysYear" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SysYear", formatBeforePublish="SysYear%s"] | Number Growatt_SysYear "SysYear" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SysYear"} |  | 1,1,SysYear,5,45,0,2,0
| 3 | 46 | SysMonth | System time- Month | W |  |  |  |  | Storage |  |  | 0 | Type number : SysMonth "Growatt_SysMonth" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SysMonth", formatBeforePublish="SysMonth%s"] | Number Growatt_SysMonth "SysMonth" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SysMonth"} |  | 1,1,SysMonth,5,46,0,2,0
| 3 | 47 | SysDay | System time- Day | W |  |  |  |  | Storage |  |  | 0 | Type number : SysDay "Growatt_SysDay" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SysDay", formatBeforePublish="SysDay%s"] | Number Growatt_SysDay "SysDay" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SysDay"} |  | 1,1,SysDay,5,47,0,2,0
| 3 | 48 | SysHour | System time- Hour | W |  |  |  | System Enable | Storage |  |  | 0 | Type number : SysHour "Growatt_SysHour" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SysHour", formatBeforePublish="SysHour%s"] | Number Growatt_SysHour "SysHour" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SysHour"} |  | 1,1,SysHour,5,48,0,2,0
| 3 | 49 | SysMin | System time- Min | W |  |  |  | CV voltage(acid) | Storage |  |  | 0 | Type number : SysMin "Growatt_SysMin" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SysMin", formatBeforePublish="SysMin%s"] | Number Growatt_SysMin "SysMin" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SysMin"} |  | 1,1,SysMin,5,49,0,2,0
| 3 | 50 | SysSec | System time- Second | W |  |  |  |  | Storage |  |  | 0 | Type number : SysSec "Growatt_SysSec" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SysSec", formatBeforePublish="SysSec%s"] | Number Growatt_SysSec "SysSec" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SysSec"} |  | 1,1,SysSec,5,50,0,2,0
| 3 | 51 | SysWeekly | System Weekly | W | 0-6 |  |  | 0: self-use | ALL |  |  | 0 | Type number : SysWeekly "Growatt_SysWeekly" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SysWeekly", formatBeforePublish="SysWeekly%s"] | Number Growatt_SysWeekly "SysWeekly" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SysWeekly"} |  | 1,1,SysWeekly,5,51,0,2,0
| 3 | 52 | Vaclow | Grid voltage low limit protect | W |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vaclow "Growatt_Vaclow" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vaclow", formatBeforePublish="Vaclow%s"] | Number:ElectricPotential Growatt_Vaclow "Vaclow [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vaclow"} |  | 1,1,Vaclow,5,52,0,2,0
| 3 | 53 | Vachigh | Grid voltage high limit protect | W |  | 0.1V |  | Cycle | ALL | 0.1 | V | 1 | Type number : Vachigh "Growatt_Vachigh" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vachigh", formatBeforePublish="Vachigh%s"] | Number:ElectricPotential Growatt_Vachigh "Vachigh [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vachigh"} |  | 1,1,Vachigh,5,53,0,2,0
| 3 | 54 | Faclow | Grid frequency low limit protect | W |  | 0.01 |  |  | PV9_32 | 0.01 |  | 2 | Type number : Faclow "Growatt_Faclow" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Faclow", formatBeforePublish="Faclow%s"] | Number Growatt_Faclow "Faclow [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Faclow"} |  | 1,1,Faclow,5,54,0,2,0
| 3 | 55 | Fachigh | Grid high | W |  | 0.01 |  |  | PV9_32 | 0.01 |  | 2 | Type number : Fachigh "Growatt_Fachigh" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Fachigh", formatBeforePublish="Fachigh%s"] | Number Growatt_Fachigh "Fachigh [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Fachigh"} |  | 1,1,Fachigh,5,55,0,2,0
| 3 | 56 | Vaclow2 | Grid voltage low limit protect 2 | W |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vaclow2 "Growatt_Vaclow2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vaclow2", formatBeforePublish="Vaclow2%s"] | Number:ElectricPotential Growatt_Vaclow2 "Vaclow2 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vaclow2"} |  | 1,1,Vaclow2,5,56,0,2,0
| 3 | 57 | Vachigh2 | Grid voltage high limit protect 2 | W |  | 0.1V |  | Cycle | ALL | 0.1 | V | 1 | Type number : Vachigh2 "Growatt_Vachigh2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vachigh2", formatBeforePublish="Vachigh2%s"] | Number:ElectricPotential Growatt_Vachigh2 "Vachigh2 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vachigh2"} |  | 1,1,Vachigh2,5,57,0,2,0
| 3 | 58 | Faclow2 | Grid frequency low limit protect 2 | W |  | 0.01 |  |  | PV9_32 | 0.01 |  | 2 | Type number : Faclow2 "Growatt_Faclow2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Faclow2", formatBeforePublish="Faclow2%s"] | Number Growatt_Faclow2 "Faclow2 [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Faclow2"} |  | 1,1,Faclow2,5,58,0,2,0
| 3 | 59 | Fachigh2 | Grid high frequency limit protect 2 | W |  | 0.01 |  |  | PV9_32 | 0.01 |  | 2 | Type number : Fachigh2 "Growatt_Fachigh2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Fachigh2", formatBeforePublish="Fachigh2%s"] | Number Growatt_Fachigh2 "Fachigh2 [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Fachigh2"} |  | 1,1,Fachigh2,5,59,0,2,0
| 3 | 60 | Vaclow3 | Grid voltage protect 3 | W |  | 0.1V |  | Cycle | ALL | 0.1 | V | 1 | Type number : Vaclow3 "Growatt_Vaclow3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vaclow3", formatBeforePublish="Vaclow3%s"] | Number:ElectricPotential Growatt_Vaclow3 "Vaclow3 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vaclow3"} |  | 1,1,Vaclow3,5,60,0,2,0
| 3 | 61 | Vachigh3 | Grid voltage protect 3 | W |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vachigh3 "Growatt_Vachigh3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vachigh3", formatBeforePublish="Vachigh3%s"] | Number:ElectricPotential Growatt_Vachigh3 "Vachigh3 [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vachigh3"} |  | 1,1,Vachigh3,5,61,0,2,0
| 3 | 62 | Faclow3 | Grid frequency limit protect 3 | W |  | 0.01Hz |  |  | PV9_32 | 0.01 | Hz | 2 | Type number : Faclow3 "Growatt_Faclow3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Faclow3", formatBeforePublish="Faclow3%s"] | Number:Frequency Growatt_Faclow3 "Faclow3 [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Faclow3"} |  | 1,1,Faclow3,5,62,0,2,0
| 3 | 63 | Fachigh3 | Grid frequency limit protect 3 | W |  | 0.01Hz |  |  | PV9_32 | 0.01 | Hz | 2 | Type number : Fachigh3 "Growatt_Fachigh3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Fachigh3", formatBeforePublish="Fachigh3%s"] | Number:Frequency Growatt_Fachigh3 "Fachigh3 [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Fachigh3"} |  | 1,1,Fachigh3,5,63,0,2,0
| 3 | 64 | VaclowC | Grid low voltage limit connect to Grid | W |  | 0.1V |  | Cycle | ALL | 0.1 | V | 1 | Type number : VaclowC "Growatt_VaclowC" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.VaclowC", formatBeforePublish="VaclowC%s"] | Number:ElectricPotential Growatt_VaclowC "VaclowC [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:VaclowC"} |  | 1,1,VaclowC,5,64,0,2,0
| 3 | 65 | VachighC | Grid high voltage limit connect to Grid | W |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : VachighC "Growatt_VachighC" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.VachighC", formatBeforePublish="VachighC%s"] | Number:ElectricPotential Growatt_VachighC "VachighC [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:VachighC"} |  | 1,1,VachighC,5,65,0,2,0
| 3 | 66 | FaclowC | Grid low frequency | W |  | 0.01 |  |  | PV9_32 | 0.01 |  | 2 | Type number : FaclowC "Growatt_FaclowC" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FaclowC", formatBeforePublish="FaclowC%s"] | Number Growatt_FaclowC "FaclowC [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FaclowC"} |  | 1,1,FaclowC,5,66,0,2,0
| 3 | 67 | FachighC | Grid high frequency limit connect to Grid | W |  | 0.01 |  |  | PV9_32 | 0.01 |  | 2 | Type number : FachighC "Growatt_FachighC" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FachighC", formatBeforePublish="FachighC%s"] | Number Growatt_FachighC "FachighC [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FachighC"} |  | 1,1,FachighC,5,67,0,2,0
| 3 | 68 | Vactime | Grid voltage low protect time 1 limit | W |  | Cycle |  |  | ALL |  | Cycle | 0 | Type number : Vactime "Growatt_Vactime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vactime", formatBeforePublish="Vactime%s"] | Number Growatt_Vactime "Vactime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vactime"} |  | 1,1,Vactime,5,68,0,2,0
| 3 | 69 | Vactime | Grid voltage protect time H lim | W |  |  |  |  | ALL |  |  | 0 | Type number : Vactime "Growatt_Vactime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vactime", formatBeforePublish="Vactime%s"] | Number Growatt_Vactime "Vactime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vactime"} |  | 1,1,Vactime,5,69,0,2,0
| 3 | 70 | Vactime | Grid voltage protect time L lim | W |  |  |  |  | ALL |  |  | 0 | Type number : Vactime "Growatt_Vactime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vactime", formatBeforePublish="Vactime%s"] | Number Growatt_Vactime "Vactime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vactime"} |  | 1,1,Vactime,5,70,0,2,0
| 3 | 71 | Vactime | Grid voltage protect time H lim | W |  |  |  |  | ALL |  |  | 0 | Type number : Vactime "Growatt_Vactime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vactime", formatBeforePublish="Vactime%s"] | Number Growatt_Vactime "Vactime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vactime"} |  | 1,1,Vactime,5,71,0,2,0
| 3 | 72 | Factime | Grid frequency limit protect timeL | W |  | Cycle |  |  | PV9_32 |  | Cycle | 0 | Type number : Factime "Growatt_Factime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Factime", formatBeforePublish="Factime%s"] | Number Growatt_Factime "Factime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Factime"} |  | 1,1,Factime,5,72,0,2,0
| 3 | 73 | Factime | Grid frequency limit protect timeH | W |  | Cycle |  |  | PV9_32 |  | Cycle | 0 | Type number : Factime "Growatt_Factime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Factime", formatBeforePublish="Factime%s"] | Number Growatt_Factime "Factime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Factime"} |  | 1,1,Factime,5,73,0,2,0
| 3 | 74 | Factime | Grid frequency limit protect timeL | W |  | Cycle |  |  | PV9_32 |  | Cycle | 0 | Type number : Factime "Growatt_Factime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Factime", formatBeforePublish="Factime%s"] | Number Growatt_Factime "Factime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Factime"} |  | 1,1,Factime,5,74,0,2,0
| 3 | 75 | Factime | Grid frequency limit protect timeH | W |  | Cycle |  |  | PV9_32 |  | Cycle | 0 | Type number : Factime "Growatt_Factime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Factime", formatBeforePublish="Factime%s"] | Number Growatt_Factime "Factime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Factime"} |  | 1,1,Factime,5,75,0,2,0
| 3 | 76 | Vactime | Grid voltage protect time L lim | W |  |  |  |  | ALL |  |  | 0 | Type number : Vactime "Growatt_Vactime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vactime", formatBeforePublish="Vactime%s"] | Number Growatt_Vactime "Vactime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vactime"} |  | 1,1,Vactime,5,76,0,2,0
| 3 | 77 | Vactime | Grid voltage protect time H lim | W |  |  |  | Cycle | ALL |  |  | 0 | Type number : Vactime "Growatt_Vactime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vactime", formatBeforePublish="Vactime%s"] | Number Growatt_Vactime "Vactime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vactime"} |  | 1,1,Vactime,5,77,0,2,0
| 3 | 78 | Factime | Grid frequency limit protect timeL | W |  | Cycle |  |  | PV9_32 |  | Cycle | 0 | Type number : Factime "Growatt_Factime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Factime", formatBeforePublish="Factime%s"] | Number Growatt_Factime "Factime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Factime"} |  | 1,1,Factime,5,78,0,2,0
| 3 | 79 | Factime | Grid frequency limit protect timeH | W |  | Cycle |  |  | PV9_32 |  | Cycle | 0 | Type number : Factime "Growatt_Factime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Factime", formatBeforePublish="Factime%s"] | Number Growatt_Factime "Factime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Factime"} |  | 1,1,Factime,5,79,0,2,0
| 3 | 80 | U10min | Volt protection for 10 min | W |  | 0.1V | 1.1V |  | ALL | 0.1 | V | 1 | Type number : U10min "Growatt_U10min" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.U10min", formatBeforePublish="U10min%s"] | Number:ElectricPotential Growatt_U10min "U10min [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:U10min"} |  | 1,1,U10min,5,80,0,2,0
| 3 | 81 | PVVoltageHighFault | PV Voltage High Fault | W |  | 0.1V |  |  | TL_X-TL_XH | 0.1 | V | 1 | Type number : PVVoltageHighFault "Growatt_PVVoltageHighFault" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PVVoltageHighFault", formatBeforePublish="PVVoltageHighFault%s"] | Number:ElectricPotential Growatt_PVVoltageHighFault "PVVoltageHighFault [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PVVoltageHighFault"} |  | 1,1,PVVoltageHighFault,5,81,0,2,0
| 3 | 82 | FWBuildNo5 | Model letter version number (TJ) | [5 empty] | PV9_32 |  |  | 0 | Type number : FWBuildNo5 "Growatt_FWBuildNo5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FWBuildNo5", formatBeforePublish="FWBuildNo5%s"] | Number Growatt_FWBuildNo5 "FWBuildNo5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FWBuildNo5"} |  | 1,1,FWBuildNo5,5,82,0,2,0
| 3 | 83 | FWBuildNo | Model letter version number (AA) | [5 empty] | PV9_32 |  |  | 0 | Type number : FWBuildNo "Growatt_FWBuildNo" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FWBuildNo", formatBeforePublish="FWBuildNo%s"] | Number Growatt_FWBuildNo "FWBuildNo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FWBuildNo"} |  | 1,1,FWBuildNo,5,83,0,2,0
| 3 | 84 | FWBuildNo4 | DSP1 FW Build No. | [5 empty] | PV9_32 |  |  | 0 | Type number : FWBuildNo4 "Growatt_FWBuildNo4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FWBuildNo4", formatBeforePublish="FWBuildNo4%s"] | Number Growatt_FWBuildNo4 "FWBuildNo4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FWBuildNo4"} |  | 1,1,FWBuildNo4,5,84,0,2,0
| 3 | 85 | FWBuildNo3 | DSP2/M0 FW Build No. | [5 empty] | PV9_32 |  |  | 0 | Type number : FWBuildNo3 "Growatt_FWBuildNo3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FWBuildNo3", formatBeforePublish="FWBuildNo3%s"] | Number Growatt_FWBuildNo3 "FWBuildNo3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FWBuildNo3"} |  | 1,1,FWBuildNo3,5,85,0,2,0
| 3 | 86 | FWBuildNo2 | CPLD/AFCI FW Build No. | [5 empty] | PV9_32 |  |  | 0 | Type number : FWBuildNo2 "Growatt_FWBuildNo2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FWBuildNo2", formatBeforePublish="FWBuildNo2%s"] | Number Growatt_FWBuildNo2 "FWBuildNo2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FWBuildNo2"} |  | 1,1,FWBuildNo2,5,86,0,2,0
| 3 | 87 | FWBuildNo1 | M3 FW Build No. | [5 empty] | PV9_32 |  |  | 0 | Type number : FWBuildNo1 "Growatt_FWBuildNo1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FWBuildNo1", formatBeforePublish="FWBuildNo1%s"] | Number Growatt_FWBuildNo1 "FWBuildNo1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FWBuildNo1"} |  | 1,1,FWBuildNo1,5,87,0,2,0
| 3 | 88 | ModbusVersion | Modbus Version | [5 empty] | ALL |  |  | 0 | Type number : ModbusVersion "Growatt_ModbusVersion" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ModbusVersion", formatBeforePublish="ModbusVersion%s"] | Number Growatt_ModbusVersion "ModbusVersion" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ModbusVersion"} |  | 1,1,ModbusVersion,5,88,0,2,0
| 3 | 89 | PFModel | Set PF function Model | W |  |  |  |  | ALL |  |  | 0 | Type number : PFModel "Growatt_PFModel" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFModel", formatBeforePublish="PFModel%s"] | Number Growatt_PFModel "PFModel" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFModel"} |  | 1,1,PFModel,5,89,0,2,0
| 3 | 90 | GPRSIPFlag | Bit0-3:read:1;Set GPRS | W | Bit0-3:ab |  |  |  | ALL |  |  | 0 | Type number : GPRSIPFlag "Growatt_GPRSIPFlag" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GPRSIPFlag", formatBeforePublish="GPRSIPFlag%s"] | Number Growatt_GPRSIPFlag "GPRSIPFlag" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GPRSIPFlag"} |  | 1,1,GPRSIPFlag,5,90,0,2,0
| 3 | 91 | FreqDerateStart | Frequency derating start point | W |  | 0.01Hz |  |  | PV9_32 | 0.01 | Hz | 2 | Type number : FreqDerateStart "Growatt_FreqDerateStart" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FreqDerateStart", formatBeforePublish="FreqDerateStart%s"] | Number:Frequency Growatt_FreqDerateStart "FreqDerateStart [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FreqDerateStart"} |  | 1,1,FreqDerateStart,5,91,0,2,0
| 3 | 92 | FLrate | Frequency  load limit rate | W | 0-100 |  |  |  | PV9_32 |  |  | 0 | Type number : FLrate "Growatt_FLrate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FLrate", formatBeforePublish="FLrate%s"] | Number Growatt_FLrate "FLrate" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FLrate"} |  | 1,1,FLrate,5,92,0,2,0
| 3 | 93 | V1S | CEI021 V1S Q(v) | W | V1S<V2S | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V1S "Growatt_V1S" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.V1S", formatBeforePublish="V1S%s"] | Number:ElectricPotential Growatt_V1S "V1S [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V1S"} |  | 1,1,V1S,5,93,0,2,0
| 3 | 94 | V2S | CEI021 V2S Q(v) | W |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V2S "Growatt_V2S" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.V2S", formatBeforePublish="V2S%s"] | Number:ElectricPotential Growatt_V2S "V2S [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V2S"} |  | 1,1,V2S,5,94,0,2,0
| 3 | 95 | V1L | CEI021 V1L Q(v) | W | V1L<V1S | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V1L "Growatt_V1L" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.V1L", formatBeforePublish="V1L%s"] | Number:ElectricPotential Growatt_V1L "V1L [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V1L"} |  | 1,1,V1L,5,95,0,2,0
| 3 | 96 | V2L | CEI021 V2L Q(v) | W | V2L<V1L | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : V2L "Growatt_V2L" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.V2L", formatBeforePublish="V2L%s"] | Number:ElectricPotential Growatt_V2L "V2L [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:V2L"} |  | 1,1,V2L,5,96,0,2,0
| 3 | 97 | Qlockinpower | Q(v) lock in active power of CEI021 | W | 0-100 | % |  | CV voltage(acid) can charge when lower than this voltage | TL_X-TL_XH |  | % | 0 | Type number : Qlockinpower "Growatt_Qlockinpower" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Qlockinpower", formatBeforePublish="Qlockinpower%s"] | Number Growatt_Qlockinpower "Qlockinpower" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Qlockinpower"} |  | 1,1,Qlockinpower,5,97,0,2,0
| 3 | 98 | QlockOutpower | Q(v) lock Out active power of CEI021 | W | 0-100 | % |  | Should not discharge when lower than this voltage | TL_X-TL_XH |  | % | 0 | Type number : QlockOutpower "Growatt_QlockOutpower" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.QlockOutpower", formatBeforePublish="QlockOutpower%s"] | Number Growatt_QlockOutpower "QlockOutpower" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:QlockOutpower"} |  | 1,1,QlockOutpower,5,98,0,2,0
| 3 | 99 | LIGridV | Lock in gird volt of | W | nVn | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : LIGridV "Growatt_LIGridV" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LIGridV", formatBeforePublish="LIGridV%s"] | Number:ElectricPotential Growatt_LIGridV "LIGridV [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:LIGridV"} |  | 1,1,LIGridV,5,99,0,2,0
| 3 | 100 | LOGridV | Lock out gird volt of | W | nVn | 0.1V |  | suggestive | ALL | 0.1 | V | 1 | Type number : LOGridV "Growatt_LOGridV" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LOGridV", formatBeforePublish="LOGridV%s"] | Number:ElectricPotential Growatt_LOGridV "LOGridV [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:LOGridV"} |  | 1,1,LOGridV,5,100,0,2,0
| 3 | 101 | PFAdj1 | PF adjust value 1 |  | 4096 is 1 |  |  |  | ALL |  |  | 0 | Type number : PFAdj1 "Growatt_PFAdj1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFAdj1", formatBeforePublish="PFAdj1%s"] | Number Growatt_PFAdj1 "PFAdj1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFAdj1"} |  | 1,1,PFAdj1,5,101,0,2,0
| 3 | 102 | PFAdj2 | PF adjust value 2 |  | 4096 is 1 |  |  |  | ALL |  |  | 0 | Type number : PFAdj2 "Growatt_PFAdj2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFAdj2", formatBeforePublish="PFAdj2%s"] | Number Growatt_PFAdj2 "PFAdj2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFAdj2"} |  | 1,1,PFAdj2,5,102,0,2,0
| 3 | 103 | PFAdj3 | PF adjust value 3 |  | 4096 is 1 |  |  |  | ALL |  |  | 0 | Type number : PFAdj3 "Growatt_PFAdj3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFAdj3", formatBeforePublish="PFAdj3%s"] | Number Growatt_PFAdj3 "PFAdj3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFAdj3"} |  | 1,1,PFAdj3,5,103,0,2,0
| 3 | 104 | PFAdj4 | PF adjust value 4 |  | 4096 is 1 |  |  |  | ALL |  |  | 0 | Type number : PFAdj4 "Growatt_PFAdj4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFAdj4", formatBeforePublish="PFAdj4%s"] | Number Growatt_PFAdj4 "PFAdj4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFAdj4"} |  | 1,1,PFAdj4,5,104,0,2,0
| 3 | 105 | PFAdj5 | PF adjust value 5 |  | 4096 is 1 |  |  |  | ALL |  |  | 0 | Type number : PFAdj5 "Growatt_PFAdj5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFAdj5", formatBeforePublish="PFAdj5%s"] | Number Growatt_PFAdj5 "PFAdj5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFAdj5"} |  | 1,1,PFAdj5,5,105,0,2,0
| 3 | 106 | PFAdj6 | PF adjust value 6 |  | 4096 is 1 |  |  |  | ALL |  |  | 0 | Type number : PFAdj6 "Growatt_PFAdj6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFAdj6", formatBeforePublish="PFAdj6%s"] | Number Growatt_PFAdj6 "PFAdj6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFAdj6"} |  | 1,1,PFAdj6,5,106,0,2,0
| 3 | 107 | QVRPDelayTimeEE | QV Reactive Power | W | 0-30 | 1S | 3S | Should stop discharge when lower than this voltage(only lead-Acid): | TL_X-TL_XH | 1 | S | 0 | Type number : QVRPDelayTimeEE "Growatt_QVRPDelayTimeEE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.QVRPDelayTimeEE", formatBeforePublish="QVRPDelayTimeEE%s"] | Number:Time Growatt_QVRPDelayTimeEE "QVRPDelayTimeEE [%1f S]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:QVRPDelayTimeEE"} |  | 1,1,QVRPDelayTimeEE,5,107,0,2,0
| 3 | 108 | OverFDeratDelayTimeEE | Overfrequency derati ngdelaytime | W | 0-20 | 50ms | 0 |  | ALL | 50 | ms | 1 | Type number : OverFDeratDelayTimeEE "Growatt_OverFDeratDelayTimeEE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.OverFDeratDelayTimeEE", formatBeforePublish="OverFDeratDelayTimeEE%s"] | #N/A |  | 1,1,OverFDeratDelayTimeEE,5,108,0,2,0
| 3 | 109 | QpercentMax | Qmax for Q(V) curve | W | 0-1000 | 0.001 |  | Should stop charge when higher than this voltage | TL_X-TL_XH | 0.001 |  | 3 | Type number : QpercentMax "Growatt_QpercentMax" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.QpercentMax", formatBeforePublish="QpercentMax%s"] | Number Growatt_QpercentMax "QpercentMax [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:QpercentMax"} |  | 1,1,QpercentMax,5,109,0,2,0
| 3 | 110 | PFLineP1_LP | PF limit line point 1 load percent | W | 0-255 | % |  |  | ALL |  | % | 0 | Type number : PFLineP1_LP "Growatt_PFLineP1_LP" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFLineP1_LP", formatBeforePublish="PFLineP1_LP%s"] | Number Growatt_PFLineP1_LP "PFLineP1_LP" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFLineP1_LP"} |  | 1,1,PFLineP1_LP,5,110,0,2,0
| 3 | 111 | PFLineP1_PF | PF limit line point 1 power factor | W | 0-20000 |  |  |  | ALL |  |  | 0 | Type number : PFLineP1_PF "Growatt_PFLineP1_PF" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFLineP1_PF", formatBeforePublish="PFLineP1_PF%s"] | Number Growatt_PFLineP1_PF "PFLineP1_PF" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFLineP1_PF"} |  | 1,1,PFLineP1_PF,5,111,0,2,0
| 3 | 112 | PFLineP2_LP | PF limit line point 2 load percent | W | 0-255 | % |  |  | ALL |  | % | 0 | Type number : PFLineP2_LP "Growatt_PFLineP2_LP" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFLineP2_LP", formatBeforePublish="PFLineP2_LP%s"] | Number Growatt_PFLineP2_LP "PFLineP2_LP" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFLineP2_LP"} |  | 1,1,PFLineP2_LP,5,112,0,2,0
| 3 | 113 | PFLineP2_PF | PF limit line point | W | 0-20000 |  |  |  | ALL |  |  | 0 | Type number : PFLineP2_PF "Growatt_PFLineP2_PF" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFLineP2_PF", formatBeforePublish="PFLineP2_PF%s"] | Number Growatt_PFLineP2_PF "PFLineP2_PF" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFLineP2_PF"} |  | 1,1,PFLineP2_PF,5,113,0,2,0
| 3 | 114 | PFLineP3_LP | PF limit line point 3 load percent | W | 0-255 | % |  |  | ALL |  | % | 0 | Type number : PFLineP3_LP "Growatt_PFLineP3_LP" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFLineP3_LP", formatBeforePublish="PFLineP3_LP%s"] | Number Growatt_PFLineP3_LP "PFLineP3_LP" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFLineP3_LP"} |  | 1,1,PFLineP3_LP,5,114,0,2,0
| 3 | 115 | PFLineP3_PF | PF limit line point 3 power factor | W | 0-20000 |  |  |  | ALL |  |  | 0 | Type number : PFLineP3_PF "Growatt_PFLineP3_PF" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFLineP3_PF", formatBeforePublish="PFLineP3_PF%s"] | Number Growatt_PFLineP3_PF "PFLineP3_PF" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFLineP3_PF"} |  | 1,1,PFLineP3_PF,5,115,0,2,0
| 3 | 116 | PFLineP4_LP | PF limit line point 4 load percent | W | 0-255 | % |  |  | ALL |  | % | 0 | Type number : PFLineP4_LP "Growatt_PFLineP4_LP" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFLineP4_LP", formatBeforePublish="PFLineP4_LP%s"] | Number Growatt_PFLineP4_LP "PFLineP4_LP" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFLineP4_LP"} |  | 1,1,PFLineP4_LP,5,116,0,2,0
| 3 | 117 | PFLineP4_PF | PF limit line point 4 power factor | W | 0-20000 |  |  |  | ALL |  |  | 0 | Type number : PFLineP4_PF "Growatt_PFLineP4_PF" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFLineP4_PF", formatBeforePublish="PFLineP4_PF%s"] | Number Growatt_PFLineP4_PF "PFLineP4_PF" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFLineP4_PF"} |  | 1,1,PFLineP4_PF,5,117,0,2,0
| 3 | 118 | Module4 | Inverter Module (4) |  | &*11 |  |  |  | ALL |  |  | 0 | Type number : Module4 "Growatt_Module4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Module4", formatBeforePublish="Module4%s"] | Number Growatt_Module4 "Module4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Module4"} |  | 1,1,Module4,5,118,0,2,0
| 3 | 119 | Module3 | Inverter Module (3) |  | &*11 |  |  |  | ALL |  |  | 0 | Type number : Module3 "Growatt_Module3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Module3", formatBeforePublish="Module3%s"] | Number Growatt_Module3 "Module3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Module3"} |  | 1,1,Module3,5,119,0,2,0
| 3 | 120 | Module2 | Inverter Module (2) |  | &*11 |  |  |  | ALL |  |  | 0 | Type number : Module2 "Growatt_Module2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Module2", formatBeforePublish="Module2%s"] | Number Growatt_Module2 "Module2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Module2"} |  | 1,1,Module2,5,120,0,2,0
| 3 | 121 | Module1 | Inverter Module (1) |  | &*11 |  |  |  | ALL |  |  | 0 | Type number : Module1 "Growatt_Module1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Module1", formatBeforePublish="Module1%s"] | Number Growatt_Module1 "Module1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Module1"} |  | 1,1,Module1,5,121,0,2,0
| 3 | 122 | ExportLimit_ | ExportLimit_En/dis | R/W | 1/0 |  |  |  | PV9_32 |  |  | 0 | Type number : ExportLimit_ "Growatt_ExportLimit_" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ExportLimit_", formatBeforePublish="ExportLimit_%s"] | Number Growatt_ExportLimit_ "ExportLimit_" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ExportLimit_"} | 65.,ExportLimit_,Modbus RTU,,5,3,122,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,ExportLimit_,5,122,0,2,0
| 3 | 123 | ExportLimitPowerRate | ExportLimitPowerRate | R/W | -1000~+1 | 0.001 |  |  | PV9_32 | 0.001 |  | 3 | Type number : ExportLimitPowerRate "Growatt_ExportLimitPowerRate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ExportLimitPowerRate", formatBeforePublish="ExportLimitPowerRate%s"] | Number Growatt_ExportLimitPowerRate "ExportLimitPowerRate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ExportLimitPowerRate"} | 65.,ExportLimitPowerRate,Modbus RTU,,5,3,123,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,ExportLimitPowerRate,5,123,0,2,0
| 3 | 124 | TrakerModel | Traker Model | W | 0,1,2 |  |  |  | ALL |  |  | 0 | Type number : TrakerModel "Growatt_TrakerModel" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.TrakerModel", formatBeforePublish="TrakerModel%s"] | Number Growatt_TrakerModel "TrakerModel" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TrakerModel"} |  | 1,1,TrakerModel,5,124,0,2,0
| 3 | 125 | INVType-1 | Inverter type-1 | R |  |  |  |  | ALL |  |  | 0 | Type number : INVType-1 "Growatt_INVType-1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.INVType-1", formatBeforePublish="INVType-1%s"] | Number Growatt_INVType-1 "INVType-1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:INVType-1"} |  | 1,1,INVType-1,5,125,0,2,0
| 3 | 126 | INVType-2 | Inverter type-2 | R |  |  |  |  | ALL |  |  | 0 | Type number : INVType-2 "Growatt_INVType-2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.INVType-2", formatBeforePublish="INVType-2%s"] | Number Growatt_INVType-2 "INVType-2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:INVType-2"} |  | 1,1,INVType-2,5,126,0,2,0
| 3 | 127 | INVType-3 | Inverter type-3 | R |  |  |  |  | ALL |  |  | 0 | Type number : INVType-3 "Growatt_INVType-3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.INVType-3", formatBeforePublish="INVType-3%s"] | Number Growatt_INVType-3 "INVType-3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:INVType-3"} |  | 1,1,INVType-3,5,127,0,2,0
| 3 | 128 | INVType-4 | Inverter type-4 | R |  |  |  |  | ALL |  |  | 0 | Type number : INVType-4 "Growatt_INVType-4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.INVType-4", formatBeforePublish="INVType-4%s"] | Number Growatt_INVType-4 "INVType-4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:INVType-4"} |  | 1,1,INVType-4,5,128,0,2,0
| 3 | 129 | INVType-5 | Inverter type-5 | R |  |  |  |  | ALL |  |  | 0 | Type number : INVType-5 "Growatt_INVType-5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.INVType-5", formatBeforePublish="INVType-5%s"] | Number Growatt_INVType-5 "INVType-5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:INVType-5"} |  | 1,1,INVType-5,5,129,0,2,0
| 3 | 130 | INVType-6 | Inverter type-6 | R |  |  |  |  | ALL |  |  | 0 | Type number : INVType-6 "Growatt_INVType-6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.INVType-6", formatBeforePublish="INVType-6%s"] | Number Growatt_INVType-6 "INVType-6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:INVType-6"} |  | 1,1,INVType-6,5,130,0,2,0
| 3 | 131 | INVType-7 | Inverter type-7 | R |  |  |  |  | ALL |  |  | 0 | Type number : INVType-7 "Growatt_INVType-7" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.INVType-7", formatBeforePublish="INVType-7%s"] | Number Growatt_INVType-7 "INVType-7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:INVType-7"} |  | 1,1,INVType-7,5,131,0,2,0
| 3 | 132 | INVType-8 | Inverter type-8 | R |  |  |  |  | ALL |  |  | 0 | Type number : INVType-8 "Growatt_INVType-8" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.INVType-8", formatBeforePublish="INVType-8%s"] | Number Growatt_INVType-8 "INVType-8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:INVType-8"} |  | 1,1,INVType-8,5,132,0,2,0
| 3 | 133 | BLVersion1 | Boot loader version1 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BLVersion1 "Growatt_BLVersion1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BLVersion1", formatBeforePublish="BLVersion1%s"] | Number Growatt_BLVersion1 "BLVersion1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BLVersion1"} |  | 1,1,BLVersion1,5,133,0,2,0
| 3 | 134 | BLVersion2 | Boot loader version2 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BLVersion2 "Growatt_BLVersion2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BLVersion2", formatBeforePublish="BLVersion2%s"] | Number Growatt_BLVersion2 "BLVersion2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BLVersion2"} |  | 1,1,BLVersion2,5,134,0,2,0
| 3 | 135 | BLVersion3 | Boot loader version3 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BLVersion3 "Growatt_BLVersion3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BLVersion3", formatBeforePublish="BLVersion3%s"] | Number Growatt_BLVersion3 "BLVersion3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BLVersion3"} |  | 1,1,BLVersion3,5,135,0,2,0
| 3 | 136 | BLVersion4 | Boot loader version4 | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BLVersion4 "Growatt_BLVersion4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BLVersion4", formatBeforePublish="BLVersion4%s"] | Number Growatt_BLVersion4 "BLVersion4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BLVersion4"} |  | 1,1,BLVersion4,5,136,0,2,0
| 3 | 137 | ReactivePowerH | Reactive PowerH | R/W |  | 0.1O |  |  | TL_X-TL_XH | 0.1 | O | 1 | Type number : ReactivePowerH "Growatt_ReactivePowerH" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ReactivePowerH", formatBeforePublish="ReactivePowerH%s"] | Number:Resistance Growatt_ReactivePowerH "ReactivePowerH [%0.1f O]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ReactivePowerH"} | 65.,ReactivePowerH,Modbus RTU,,5,3,137,1,9410,2,0,Unsigned int,0,1,O,1,100,97,0,0,0,1.000000,0,255 | 1,1,ReactivePowerH,5,137,0,2,0
| 3 | 138 | ReactiveP | Reactive PowerL | R/W |  | 0.1O |  |  | TL_X-TL_XH | 0.1 | O | 1 | Type number : ReactiveP "Growatt_ReactiveP" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ReactiveP", formatBeforePublish="ReactiveP%s"] | Number:Resistance Growatt_ReactiveP "ReactiveP [%0.1f O]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ReactiveP"} | 65.,ReactiveP,Modbus RTU,,5,3,138,1,9410,2,0,Unsigned int,0,1,O,1,100,97,0,0,0,1.000000,0,255 | 1,1,ReactiveP,5,138,0,2,0
| 3 | 139 | ReactiveOutputPriorityenable | ReactiveOutput Priority | R/W |  | 0/1 |  | CC current | TL_X-TL_XH | 0/ | / | 1 | Type number : ReactiveOutputPriorityenable "Growatt_ReactiveOutputPriorityenable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ReactiveOutputPriorityenable", formatBeforePublish="ReactiveOutputPriorityenable%s"] | #N/A | 65.,ReactiveOutputPriorityenable,Modbus RTU,,5,3,139,1,9410,2,0,Unsigned int,0,1,/,1,100,97,0,0,0,1.000000,0,255 | 1,1,ReactiveOutputPriorityenable,5,139,0,2,0
| 3 | 140 | ReactiveP | Reactive Power Ratio | R/W |  | 0.1 |  | MIN2.5~6KTL-XH/ XA Double CT | TL_X-TL_XH | 0.1 |  | 1 | Type number : ReactiveP "Growatt_ReactiveP" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ReactiveP", formatBeforePublish="ReactiveP%s"] | Number Growatt_ReactiveP "ReactiveP [%0.1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ReactiveP"} | 65.,ReactiveP,Modbus RTU,,5,3,140,1,9410,2,0,Unsigned int,0,1,,1,100,97,0,0,0,1.000000,0,255 | 1,1,ReactiveP,5,140,0,2,0
| 3 | 141 | SvgFunction | Svg enable on night | R/W |  | 0/1 |  |  | Storage | 0/ | / | 1 | Type number : SvgFunction "Growatt_SvgFunction" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SvgFunction", formatBeforePublish="SvgFunction%s"] | #N/A | 65.,SvgFunction,Modbus RTU,,5,3,141,1,9410,2,0,Unsigned int,0,1,/,1,100,97,0,0,0,1.000000,0,255 | 1,1,SvgFunction,5,141,0,2,0
| 3 | 142 | uwUnderFUploadPoint | UnderF Upload Point | R/W |  | 0.01H |  |  | ALL | 0.01 | H | 2 | Type number : uwUnderFUploadPoint "Growatt_uwUnderFUploadPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUnderFUploadPoint", formatBeforePublish="uwUnderFUploadPoint%s"] | #N/A | 65.,uwUnderFUploadPoint,Modbus RTU,,5,3,142,1,9410,2,0,Unsigned int,0,2,H,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUnderFUploadPoint,5,142,0,2,0
| 3 | 143 | uwOFDerateRecoverPoin | OFDerate RecoverPoint | R/W |  | 0.01H |  | UL | ALL | 0.01 | H | 2 | Type number : uwOFDerateRecoverPoin "Growatt_uwOFDerateRecoverPoin" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwOFDerateRecoverPoin", formatBeforePublish="uwOFDerateRecoverPoin%s"] | #N/A | 65.,uwOFDerateRecoverPoin,Modbus RTU,,5,3,143,1,9410,2,0,Unsigned int,0,2,H,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwOFDerateRecoverPoin,5,143,0,2,0
| 3 | 144 | uwOFDerateRecoverDelayTime | OFDerate | R/W | 0-30000 | 50ms |  | UL | ALL | 50 | ms | 1 | Type number : uwOFDerateRecoverDelayTime "Growatt_uwOFDerateRecoverDelayTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwOFDerateRecoverDelayTime", formatBeforePublish="uwOFDerateRecoverDelayTime%s"] | #N/A | 65.,uwOFDerateRecoverDelayTime,Modbus RTU,,5,3,144,1,9410,2,0,Unsigned int,0,1,ms,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwOFDerateRecoverDelayTime,5,144,0,2,0
| 3 | 145 | ZeroCurrent | ZeroCurrent Enable | R/W | 0-1 |  |  | The inverter can be switched on and off, and the BDC can be switched on and off for the batt ready function. | ALL |  |  | 0 | Type number : ZeroCurrent "Growatt_ZeroCurrent" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ZeroCurrent", formatBeforePublish="ZeroCurrent%s"] | Number Growatt_ZeroCurrent "ZeroCurrent" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ZeroCurrent"} | 65.,ZeroCurrent,Modbus RTU,,5,3,145,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,ZeroCurrent,5,145,0,2,0
| 3 | 146 | uwZeroCurrentStaticlowV | ZeroCurrent | R/W | 46-230V | 0.1V | 115V | ASCII | ALL | 0.1 | V | 1 | Type number : uwZeroCurrentStaticlowV "Growatt_uwZeroCurrentStaticlowV" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwZeroCurrentStaticlowV", formatBeforePublish="uwZeroCurrentStaticlowV%s"] | Number:ElectricPotential Growatt_uwZeroCurrentStaticlowV "uwZeroCurrentStaticlowV [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwZeroCurrentStaticlowV"} | 65.,uwZeroCurrentStaticlowV,Modbus RTU,,5,3,146,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwZeroCurrentStaticlowV,5,146,0,2,0
| 3 | 147 | uwZeroCurrentStaticHigh | ZeroCurrent | R/W | 230-276V | 0.1V | 276V | ASCII | ALL | 0.1 | V | 1 | Type number : uwZeroCurrentStaticHigh "Growatt_uwZeroCurrentStaticHigh" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwZeroCurrentStaticHigh", formatBeforePublish="uwZeroCurrentStaticHigh%s"] | Number:ElectricPotential Growatt_uwZeroCurrentStaticHigh "uwZeroCurrentStaticHigh [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwZeroCurrentStaticHigh"} | 65.,uwZeroCurrentStaticHigh,Modbus RTU,,5,3,147,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwZeroCurrentStaticHigh,5,147,0,2,0
| 3 | 148 | uwHVoltDer | HVoltDerate HighPoint | R/W | 0-1000V | 0.1V |  | 0:Not support | ALL | 0.1 | V | 1 | Type number : uwHVoltDer "Growatt_uwHVoltDer" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwHVoltDer", formatBeforePublish="uwHVoltDer%s"] | Number:ElectricPotential Growatt_uwHVoltDer "uwHVoltDer [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwHVoltDer"} | 65.,uwHVoltDer,Modbus RTU,,5,3,148,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwHVoltDer,5,148,0,2,0
| 3 | 149 | uwHVoltDerateLowPoint | HVoltDerate LowPoint | R/W | 0-1000V | 0.1V |  | 0x00:Not configured success | ALL | 0.1 | V | 1 | Type number : uwHVoltDerateLowPoint "Growatt_uwHVoltDerateLowPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwHVoltDerateLowPoint", formatBeforePublish="uwHVoltDerateLowPoint%s"] | Number:ElectricPotential Growatt_uwHVoltDerateLowPoint "uwHVoltDerateLowPoint [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwHVoltDerateLowPoint"} | 65.,uwHVoltDerateLowPoint,Modbus RTU,,5,3,149,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwHVoltDerateLowPoint,5,149,0,2,0
| 3 | 150 | uwQVPower | QVPower Stable Time | R/W | 0-60S | 0.1S |  | CEI | ALL | 0.1 | S | 1 | Type number : uwQVPower "Growatt_uwQVPower" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwQVPower", formatBeforePublish="uwQVPower%s"] | Number:Time Growatt_uwQVPower "uwQVPower [%0.1f S]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwQVPower"} | 65.,uwQVPower,Modbus RTU,,5,3,150,1,9410,2,0,Unsigned int,0,1,S,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwQVPower,5,150,0,2,0
| 3 | 151 | uwUnderFUploadStopPo | UnderF Upload | R/W |  | 0.01H |  |  | ALL | 0.01 | H | 2 | Type number : uwUnderFUploadStopPo "Growatt_uwUnderFUploadStopPo" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUnderFUploadStopPo", formatBeforePublish="uwUnderFUploadStopPo%s"] | #N/A | 65.,uwUnderFUploadStopPo,Modbus RTU,,5,3,151,1,9410,2,0,Unsigned int,0,2,H,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUnderFUploadStopPo,5,151,0,2,0
| 3 | 152 | fUnderFreqPoint | Underfrequency load | R/W | 46.00-50. | 0.01Hz | 49,8 |  | PV9_32 | 0.01 | Hz | 2 | Type number : fUnderFreqPoint "Growatt_fUnderFreqPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.fUnderFreqPoint", formatBeforePublish="fUnderFreqPoint%s"] | Number:Frequency Growatt_fUnderFreqPoint "fUnderFreqPoint [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:fUnderFreqPoint"} | 65.,fUnderFreqPoint,Modbus RTU,,5,3,152,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255 | 1,1,fUnderFreqPoint,5,152,0,2,0
| 3 | 153 | fUnderFreqendPoint | Underfrequency down load end point | R/W | 46.00-50. | 0.01Hz | 49,1 |  | PV9_32 | 0.01 | Hz | 2 | Type number : fUnderFreqendPoint "Growatt_fUnderFreqendPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.fUnderFreqendPoint", formatBeforePublish="fUnderFreqendPoint%s"] | Number:Frequency Growatt_fUnderFreqendPoint "fUnderFreqendPoint [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:fUnderFreqendPoint"} | 65.,fUnderFreqendPoint,Modbus RTU,,5,3,153,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255 | 1,1,fUnderFreqendPoint,5,153,0,2,0
| 3 | 154 | fOverFreqPo | Over frequency loading start point | R/W | 50.00-52. | 0.01Hz | 50,2 |  | PV9_32 | 0.01 | Hz | 2 | Type number : fOverFreqPo "Growatt_fOverFreqPo" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.fOverFreqPo", formatBeforePublish="fOverFreqPo%s"] | Number:Frequency Growatt_fOverFreqPo "fOverFreqPo [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:fOverFreqPo"} | 65.,fOverFreqPo,Modbus RTU,,5,3,154,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255 | 1,1,fOverFreqPo,5,154,0,2,0
| 3 | 155 | fOverFreqEndPoint | Over frequency loading end point | R/W | 50.00-52. | 0.01Hz | 51,5 |  | PV9_32 | 0.01 | Hz | 2 | Type number : fOverFreqEndPoint "Growatt_fOverFreqEndPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.fOverFreqEndPoint", formatBeforePublish="fOverFreqEndPoint%s"] | Number:Frequency Growatt_fOverFreqEndPoint "fOverFreqEndPoint [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:fOverFreqEndPoint"} | 65.,fOverFreqEndPoint,Modbus RTU,,5,3,155,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255 | 1,1,fOverFreqEndPoint,5,155,0,2,0
| 3 | 156 | fUnderVoltPoint | Undervoltage load | R/W | 160-300 | 0.1V | 220 |  | PV9_32 | 0.1 | V | 1 | Type number : fUnderVoltPoint "Growatt_fUnderVoltPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.fUnderVoltPoint", formatBeforePublish="fUnderVoltPoint%s"] | Number:ElectricPotential Growatt_fUnderVoltPoint "fUnderVoltPoint [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:fUnderVoltPoint"} | 65.,fUnderVoltPoint,Modbus RTU,,5,3,156,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255 | 1,1,fUnderVoltPoint,5,156,0,2,0
| 3 | 157 | fUnderVoltendPoint | Undervoltage derating end point | R/W | 160-300 | 0.1V | 207 |  | PV9_32 | 0.1 | V | 1 | Type number : fUnderVoltendPoint "Growatt_fUnderVoltendPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.fUnderVoltendPoint", formatBeforePublish="fUnderVoltendPoint%s"] | Number:ElectricPotential Growatt_fUnderVoltendPoint "fUnderVoltendPoint [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:fUnderVoltendPoint"} | 65.,fUnderVoltendPoint,Modbus RTU,,5,3,157,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255 | 1,1,fUnderVoltendPoint,5,157,0,2,0
| 3 | 158 | fOverVoltPoint | Overvoltage loading | R/W | 160-300 | 0.1V | 230 |  | PV9_32 | 0.1 | V | 1 | Type number : fOverVoltPoint "Growatt_fOverVoltPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.fOverVoltPoint", formatBeforePublish="fOverVoltPoint%s"] | Number:ElectricPotential Growatt_fOverVoltPoint "fOverVoltPoint [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:fOverVoltPoint"} | 65.,fOverVoltPoint,Modbus RTU,,5,3,158,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255 | 1,1,fOverVoltPoint,5,158,0,2,0
| 3 | 159 | fOverVoltEndPoint | Overvoltage loading end point | R/W | 160-300 | 0.1V | 245 |  | PV9_32 | 0.1 | V | 1 | Type number : fOverVoltEndPoint "Growatt_fOverVoltEndPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.fOverVoltEndPoint", formatBeforePublish="fOverVoltEndPoint%s"] | Number:ElectricPotential Growatt_fOverVoltEndPoint "fOverVoltEndPoint [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:fOverVoltEndPoint"} | 65.,fOverVoltEndPoint,Modbus RTU,,5,3,159,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255 | 1,1,fOverVoltEndPoint,5,159,0,2,0
| 3 | 160 | uwNominal | NominalGridVolt Select | R/W | 0~3 |  |  | UL | ALL |  |  | 0 | Type number : uwNominal "Growatt_uwNominal" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwNominal", formatBeforePublish="uwNominal%s"] | Number Growatt_uwNominal "uwNominal" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwNominal"} | 65.,uwNominal,Modbus RTU,,5,3,160,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwNominal,5,160,0,2,0
| 3 | 161 | uwGridWatt | GridWatt DelayTime | R/W | 0~3000 | 20ms |  | 0:connection succeeded | ALL | 20 | ms | 1 | Type number : uwGridWatt "Growatt_uwGridWatt" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwGridWatt", formatBeforePublish="uwGridWatt%s"] | #N/A | 65.,uwGridWatt,Modbus RTU,,5,3,161,1,9410,2,0,Unsigned int,0,1,ms,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwGridWatt,5,161,0,2,0
| 3 | 162 | uwReconnec | Reconnect StartSlope | R/W | 1~1000 | 0.1 |  |  | ALL | 0.1 |  | 1 | Type number : uwReconnec "Growatt_uwReconnec" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwReconnec", formatBeforePublish="uwReconnec%s"] | Number Growatt_uwReconnec "uwReconnec [%0.1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwReconnec"} | 65.,uwReconnec,Modbus RTU,,5,3,162,1,9410,2,0,Unsigned int,0,1,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwReconnec,5,162,0,2,0
| 3 | 163 | uwLFRTEE | LFRT1 Freq | R/W | 5500~650 | 0.01Hz |  | 50549 | ALL | 0.01 | Hz | 2 | Type number : uwLFRTEE "Growatt_uwLFRTEE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwLFRTEE", formatBeforePublish="uwLFRTEE%s"] | Number:Frequency Growatt_uwLFRTEE "uwLFRTEE [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwLFRTEE"} | 65.,uwLFRTEE,Modbus RTU,,5,3,163,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwLFRTEE,5,163,0,2,0
| 3 | 164 | uwLFRTTime | LFRT1 Time | R/W |  | 20ms |  | UL | ALL | 20 | ms | 1 | Type number : uwLFRTTime "Growatt_uwLFRTTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwLFRTTime", formatBeforePublish="uwLFRTTime%s"] | #N/A | 65.,uwLFRTTime,Modbus RTU,,5,3,164,1,9410,2,0,Unsigned int,0,1,ms,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwLFRTTime,5,164,0,2,0
| 3 | 165 | uwLFRT2EE | LFRT2 Freq | R/W | 5500~650 | 0.01Hz |  | 50549 | ALL | 0.01 | Hz | 2 | Type number : uwLFRT2EE "Growatt_uwLFRT2EE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwLFRT2EE", formatBeforePublish="uwLFRT2EE%s"] | Number:Frequency Growatt_uwLFRT2EE "uwLFRT2EE [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwLFRT2EE"} | 65.,uwLFRT2EE,Modbus RTU,,5,3,165,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwLFRT2EE,5,165,0,2,0
| 3 | 166 | uwLFRTTime | LFRT2 Time | R/W |  | 20ms |  | 50549 | ALL | 20 | ms | 1 | Type number : uwLFRTTime "Growatt_uwLFRTTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwLFRTTime", formatBeforePublish="uwLFRTTime%s"] | #N/A | 65.,uwLFRTTime,Modbus RTU,,5,3,166,1,9410,2,0,Unsigned int,0,1,ms,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwLFRTTime,5,166,0,2,0
| 3 | 167 | uwHFRTEE | HFRT1 Freq | R/W | 5500~650 | 0.01Hz |  |  | ALL | 0.01 | Hz | 2 | Type number : uwHFRTEE "Growatt_uwHFRTEE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwHFRTEE", formatBeforePublish="uwHFRTEE%s"] | Number:Frequency Growatt_uwHFRTEE "uwHFRTEE [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwHFRTEE"} | 65.,uwHFRTEE,Modbus RTU,,5,3,167,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwHFRTEE,5,167,0,2,0
| 3 | 168 | uwHFRTTimeEE | HFRT1 Time | R/W |  | 20ms |  | The number of BDCs connected to the current machine Default is 0 | ALL | 20 | ms | 1 | Type number : uwHFRTTimeEE "Growatt_uwHFRTTimeEE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwHFRTTimeEE", formatBeforePublish="uwHFRTTimeEE%s"] | #N/A | 65.,uwHFRTTimeEE,Modbus RTU,,5,3,168,1,9410,2,0,Unsigned int,0,1,ms,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwHFRTTimeEE,5,168,0,2,0
| 3 | 169 | uwHFRT2EE | HFRT2 Freq | R/W | 5500~650 | 0.01Hz |  | 0:Disable | ALL | 0.01 | Hz | 2 | Type number : uwHFRT2EE "Growatt_uwHFRT2EE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwHFRT2EE", formatBeforePublish="uwHFRT2EE%s"] | Number:Frequency Growatt_uwHFRT2EE "uwHFRT2EE [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwHFRT2EE"} | 65.,uwHFRT2EE,Modbus RTU,,5,3,169,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwHFRT2EE,5,169,0,2,0
| 3 | 170 | uwHFRTTime2EE | HFRT2 Time | R/W |  | 20ms |  | Total number of battery modules currently associated with all BDCs | ALL | 20 | ms | 1 | Type number : uwHFRTTime2EE "Growatt_uwHFRTTime2EE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwHFRTTime2EE", formatBeforePublish="uwHFRTTime2EE%s"] | #N/A | 65.,uwHFRTTime2EE,Modbus RTU,,5,3,170,1,9410,2,0,Unsigned int,0,1,ms,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwHFRTTime2EE,5,170,0,2,0
| 3 | 171 | uwHVRTEE | HVRT1 Volt | R/W |  | 0.001 |  | 0: Missed, 1: Received | ALL | 0.001 |  | 3 | Type number : uwHVRTEE "Growatt_uwHVRTEE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwHVRTEE", formatBeforePublish="uwHVRTEE%s"] | Number Growatt_uwHVRTEE "uwHVRTEE [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwHVRTEE"} | 65.,uwHVRTEE,Modbus RTU,,5,3,171,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwHVRTEE,5,171,0,2,0
| 3 | 172 | uwHVRTTimeEE | HVRT1 Time | R/W |  | 20ms |  |  | ALL | 20 | ms | 1 | Type number : uwHVRTTimeEE "Growatt_uwHVRTTimeEE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwHVRTTimeEE", formatBeforePublish="uwHVRTTimeEE%s"] | #N/A | 65.,uwHVRTTimeEE,Modbus RTU,,5,3,172,1,9410,2,0,Unsigned int,0,1,ms,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwHVRTTimeEE,5,172,0,2,0
| 3 | 173 | uwHVRT2EE | HVRT2 Volt | R/W |  | 0.001 |  | The total number of optimizers connected to the inverter | ALL | 0.001 |  | 3 | Type number : uwHVRT2EE "Growatt_uwHVRT2EE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwHVRT2EE", formatBeforePublish="uwHVRT2EE%s"] | Number Growatt_uwHVRT2EE "uwHVRT2EE [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwHVRT2EE"} | 65.,uwHVRT2EE,Modbus RTU,,5,3,173,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwHVRT2EE,5,173,0,2,0
| 3 | 174 | uwHVRTTime2EE | HVRT2 Time | R/W |  | 0.001 |  |  | ALL | 0.001 |  | 3 | Type number : uwHVRTTime2EE "Growatt_uwHVRTTime2EE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwHVRTTime2EE", formatBeforePublish="uwHVRTTime2EE%s"] | Number Growatt_uwHVRTTime2EE "uwHVRTTime2EE [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwHVRTTime2EE"} | 65.,uwHVRTTime2EE,Modbus RTU,,5,3,174,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwHVRTTime2EE,5,174,0,2,0
| 3 | 175 | uwUnderFU | UnderF | R/W | 0-2s | 50ms | 0s |  | ALL | 50 | ms | 1 | Type number : uwUnderFU "Growatt_uwUnderFU" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUnderFU", formatBeforePublish="uwUnderFU%s"] | #N/A | 65.,uwUnderFU,Modbus RTU,,5,3,175,1,9410,2,0,Unsigned int,0,1,ms,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUnderFU,5,175,0,2,0
| 3 | 176 | uwUnderFUploadRateEE | UnderF UploadRate | R/W |  |  |  | 0:disable | ALL |  |  | 0 | Type number : uwUnderFUploadRateEE "Growatt_uwUnderFUploadRateEE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUnderFUploadRateEE", formatBeforePublish="uwUnderFUploadRateEE%s"] | Number Growatt_uwUnderFUploadRateEE "uwUnderFUploadRateEE" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwUnderFUploadRateEE"} | 65.,uwUnderFUploadRateEE,Modbus RTU,,5,3,176,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUnderFUploadRateEE,5,176,0,2,0
| 3 | 177 | uwGridRestart_H_Freq | GridRestart HighFreq | R/W |  | 0.01Hz |  |  | ALL | 0.01 | Hz | 2 | Type number : uwGridRestart_H_Freq "Growatt_uwGridRestart_H_Freq" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwGridRestart_H_Freq", formatBeforePublish="uwGridRestart_H_Freq%s"] | Number:Frequency Growatt_uwGridRestart_H_Freq "uwGridRestart_H_Freq [%0.01f Hz]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwGridRestart_H_Freq"} | 65.,uwGridRestart_H_Freq,Modbus RTU,,5,3,177,1,9410,2,0,Unsigned int,0,2,Hz,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwGridRestart_H_Freq,5,177,0,2,0
| 3 | 178 | OverFDeratResponseTime | OverFDerat | R/W | 0-500 |  |  |  | ALL |  |  | 0 | Type number : OverFDeratResponseTime "Growatt_OverFDeratResponseTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.OverFDeratResponseTime", formatBeforePublish="OverFDeratResponseTime%s"] | Number Growatt_OverFDeratResponseTime "OverFDeratResponseTime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OverFDeratResponseTime"} | 65.,OverFDeratResponseTime,Modbus RTU,,5,3,178,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,OverFDeratResponseTime,5,178,0,2,0
| 3 | 179 | UnderFUploadResponse | UnderFUpload | R/W | 0-500 |  |  | 1-1000,(Percent ratio) | ALL |  |  | 0 | Type number : UnderFUploadResponse "Growatt_UnderFUploadResponse" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.UnderFUploadResponse", formatBeforePublish="UnderFUploadResponse%s"] | Number Growatt_UnderFUploadResponse "UnderFUploadResponse" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:UnderFUploadResponse"} | 65.,UnderFUploadResponse,Modbus RTU,,5,3,179,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,UnderFUploadResponse,5,179,0,2,0
| 3 | 180 | MeterLink | Whether to elect the meter | R/W |  |  |  |  | ALL |  |  | 0 | Type number : MeterLink "Growatt_MeterLink" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.MeterLink", formatBeforePublish="MeterLink%s"] | Number Growatt_MeterLink "MeterLink" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:MeterLink"} | 65.,MeterLink,Modbus RTU,,5,3,180,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,MeterLink,5,180,0,2,0
| 3 | 181 | OPTNumber | Number of connection optimizers | R/W | 0-64 |  |  |  | ALL |  |  | 0 | Type number : OPTNumber "Growatt_OPTNumber" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.OPTNumber", formatBeforePublish="OPTNumber%s"] | Number Growatt_OPTNumber "OPTNumber" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OPTNumber"} | 65.,OPTNumber,Modbus RTU,,5,3,181,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,OPTNumber,5,181,0,2,0
| 3 | 182 | OPT | Optimizer configuration completion flag | R/W |  |  |  |  | ALL |  |  | 0 | Type number : OPT "Growatt_OPT" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.OPT", formatBeforePublish="OPT%s"] | Number Growatt_OPT "OPT" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OPT"} | 65.,OPT,Modbus RTU,,5,3,182,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,OPT,5,182,0,2,0
| 3 | 183 | PvStrScan | String Num | R/W | 0?8?16? |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : PvStrScan "Growatt_PvStrScan" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PvStrScan", formatBeforePublish="PvStrScan%s"] | Number Growatt_PvStrScan "PvStrScan" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PvStrScan"} | 65.,PvStrScan,Modbus RTU,,5,3,183,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,PvStrScan,5,183,0,2,0
| 3 | 184 | BDCLinkNum | BDC parallel Num | R/W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BDCLinkNum "Growatt_BDCLinkNum" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BDCLinkNum", formatBeforePublish="BDCLinkNum%s"] | Number Growatt_BDCLinkNum "BDCLinkNum" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BDCLinkNum"} | 65.,BDCLinkNum,Modbus RTU,,5,3,184,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,BDCLinkNum,5,184,0,2,0
| 3 | 185 | PackNum | Number of battery modules | R |  |  |  |  | ALL |  |  | 0 | Type number : PackNum "Growatt_PackNum" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PackNum", formatBeforePublish="PackNum%s"] | Number Growatt_PackNum "PackNum" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PackNum"} |  | 1,1,PackNum,5,185,0,2,0
| 3 | 186 | Reserved | [5 empty] | SPA/ reserve | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 1,1,Reserved,5,186,0,2,0
| 3 | 187 | VPPfunctionenablestatus | VPP function enable status | R |  |  |  |  | ALL |  |  | 0 | Type number : VPPfunctionenablestatus "Growatt_VPPfunctionenablestatus" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.VPPfunctionenablestatus", formatBeforePublish="VPPfunctionenablestatus%s"] | Number Growatt_VPPfunctionenablestatus "VPPfunctionenablestatus" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:VPPfunctionenablestatus"} |  | 1,1,VPPfunctionenablestatus,5,187,0,2,0
| 3 | 188 | dataLogConnectServerstatus | dataLog Connect |  |  |  |  | Storage | SPA |  |  | 0 | Type number : dataLogConnectServerstatus "Growatt_dataLogConnectServerstatus" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.dataLogConnectServerstatus", formatBeforePublish="dataLogConnectServerstatus%s"] | Number Growatt_dataLogConnectServerstatus "dataLogConnectServerstatus" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:dataLogConnectServerstatus"} |  | 1,1,dataLogConnectServerstatus,5,188,0,2,0
| 3 | 201 | PIDWorkingModel | PID Operating mode | W | 0 |  |  | Same as Time 1 | USTimeSet |  |  | 0 | Type number : PIDWorkingModel "Growatt_PIDWorkingModel" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PIDWorkingModel", formatBeforePublish="PIDWorkingModel%s"] | Number Growatt_PIDWorkingModel "PIDWorkingModel" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDWorkingModel"} |  | 1,1,PIDWorkingModel,5,201,0,2,0
| 3 | 202 | PIDOn_OffCtrl | PID Break control | W | 0:On 1:Off |  |  |  | ALL |  |  | 0 | Type number : PIDOn_OffCtrl "Growatt_PIDOn_OffCtrl" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PIDOn_OffCtrl", formatBeforePublish="PIDOn_OffCtrl%s"] | Number Growatt_PIDOn_OffCtrl "PIDOn_OffCtrl" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDOn_OffCtrl"} |  | 1,1,PIDOn_OffCtrl,5,202,0,2,0
| 3 | 203 | PIDOption | PID Output voltage | W | 300~1000 | V |  |  | ALL |  | V | 0 | Type number : PIDOption "Growatt_PIDOption" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PIDOption", formatBeforePublish="PIDOption%s"] | Number:ElectricPotential Growatt_PIDOption "PIDOption" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PIDOption"} |  | 1,1,PIDOption,5,203,0,2,0
| 3 | 209 | NewSerialNO | Serial number 1-2 | [5 empty] | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,209,0,2,0
| 3 | 210 | NewSerialNO | Serial number 3-4 | [5 empty] | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,210,0,2,0
| 3 | 211 | NewSerialNO | Serial number 5-6 | [5 empty] | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,211,0,2,0
| 3 | 212 | NewSerialNO | Serial number 7-8 | [5 empty] | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,212,0,2,0
| 3 | 213 | NewSerialNO | Serial number 9-10 | [5 empty] | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,213,0,2,0
| 3 | 214 | NewSerialNO | Serial number 11-12 | [5 empty] | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,214,0,2,0
| 3 | 215 | NewSerialNO | Serial number 13-14 |  |  |  |  | StoragePow er (SPA) | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,215,0,2,0
| 3 | 216 | NewSerialNO | Serial number 15-16 |  |  |  |  | StoragePow er (SPA) | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,216,0,2,0
| 3 | 217 | NewSerialNO | Serial number 17-18 | [5 empty] | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,217,0,2,0
| 3 | 218 | NewSerialNO | Serial number 19-20 | [5 empty] | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,218,0,2,0
| 3 | 219 | Time9 | [5 empty] | ISO detection command | ALL |  |  | 0 | Type number : Time9 "Growatt_Time9" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time9", formatBeforePublish="Time9%s"] | Number Growatt_Time9 "Time9" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time9"} |  | 1,1,Time9,5,219,0,2,0
| 3 | 219 | NewSerialNO | Serial number 21-22 | [5 empty] | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,219,0,2,0
| 3 | 220 | NewSerialNO | Serial number 23-24 |  |  |  |  | MAX | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,220,0,2,0
| 3 | 221 | NewSerialNO | Serial number 25-26 | [5 empty] | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,221,0,2,0
| 3 | 222 | NewSerialNO | Serial number 27-28 | [5 empty] | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,222,0,2,0
| 3 | 223 | NewSerialNO | Serial number 29-30 |  |  |  |  | Storage | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 1,1,NewSerialNO,5,223,0,2,0
| 3 | 229 | EnergyAdjust | Power generation incremental calibration coefficient | R/W |  | 0.001 |  |  | BMS | 0.001 |  | 3 | Type number : EnergyAdjust "Growatt_EnergyAdjust" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.EnergyAdjust", formatBeforePublish="EnergyAdjust%s"] | Number Growatt_EnergyAdjust "EnergyAdjust [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EnergyAdjust"} | 65.,EnergyAdjust,Modbus RTU,,5,3,229,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,EnergyAdjust,5,229,0,2,0
| 3 | 230 | IslandDisable | Island Disable or not. | W | 0,1 |  | 0 |  | ALL |  |  | 0 | Type number : IslandDisable "Growatt_IslandDisable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.IslandDisable", formatBeforePublish="IslandDisable%s"] | Number Growatt_IslandDisable "IslandDisable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:IslandDisable"} |  | 1,1,IslandDisable,5,230,0,2,0
| 3 | 231 | FanCheck | Start Fan Check | W | 1 |  |  |  | PV9_32 |  |  | 0 | Type number : FanCheck "Growatt_FanCheck" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FanCheck", formatBeforePublish="FanCheck%s"] | Number Growatt_FanCheck "FanCheck" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FanCheck"} |  | 1,1,FanCheck,5,231,0,2,0
| 3 | 232 | EnableNLine | Enable N Line of grid | W | 1 |  | 0 |  | BMS |  |  | 0 | Type number : EnableNLine "Growatt_EnableNLine" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.EnableNLine", formatBeforePublish="EnableNLine%s"] | Number Growatt_EnableNLine "EnableNLine" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EnableNLine"} |  | 1,1,EnableNLine,5,232,0,2,0
| 3 | 233 | wCheckHardware | wCheckHardware | [5 empty] | ALL |  |  | 0 | Type number : wCheckHardware "Growatt_wCheckHardware" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.wCheckHardware", formatBeforePublish="wCheckHardware%s"] | Number Growatt_wCheckHardware "wCheckHardware" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:wCheckHardware"} |  | 1,1,wCheckHardware,5,233,0,2,0
| 3 | 234 | wCheckHardware2 | [6 empty] | ALL |  |  | 0 | Type number : wCheckHardware2 "Growatt_wCheckHardware2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.wCheckHardware2", formatBeforePublish="wCheckHardware2%s"] | Number Growatt_wCheckHardware2 "wCheckHardware2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:wCheckHardware2"} |  | 1,1,wCheckHardware2,5,234,0,2,0
| 3 | 235 | ubNToGNDDetect | Dis/enable N to GND | W | 1:enable |  | 1 |  | ALL |  |  | 0 | Type number : ubNToGNDDetect "Growatt_ubNToGNDDetect" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ubNToGNDDetect", formatBeforePublish="ubNToGNDDetect%s"] | Number Growatt_ubNToGNDDetect "ubNToGNDDetect" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ubNToGNDDetect"} |  | 1,1,ubNToGNDDetect,5,235,0,2,0
| 3 | 236 | NonStdVacenable | Enable/Disable | W | 0-2 |  | 0 |  | ALL |  |  | 0 | Type number : NonStdVacenable "Growatt_NonStdVacenable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NonStdVacenable", formatBeforePublish="NonStdVacenable%s"] | Number Growatt_NonStdVacenable "NonStdVacenable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NonStdVacenable"} |  | 1,1,NonStdVacenable,5,236,0,2,0
| 3 | 237 | uwEnableSpecSet | Disablse/enable appointed spec setting | W | 1:enable | Binary | 0x000 | ASCII | ALL |  | Binary | 0 | Type number : uwEnableSpecSet "Growatt_uwEnableSpecSet" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwEnableSpecSet", formatBeforePublish="uwEnableSpecSet%s"] | #N/A |  | 1,1,uwEnableSpecSet,5,237,0,2,0
| 3 | 238 | FastMPPTenable | About Fast mppt |  | 0,1,2 |  | 0 |  | PV9_32 |  |  | 0 | Type number : FastMPPTenable "Growatt_FastMPPTenable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FastMPPTenable", formatBeforePublish="FastMPPTenable%s"] | Number Growatt_FastMPPTenable "FastMPPTenable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FastMPPTenable"} |  | 1,1,FastMPPTenable,5,238,0,2,0
| 3 | 240 | CheckStep |  | W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : CheckStep "Growatt_CheckStep" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.CheckStep", formatBeforePublish="CheckStep%s"] | Number Growatt_CheckStep "CheckStep" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CheckStep"} |  | 1,1,CheckStep,5,240,0,2,0
| 3 | 241 | INV-Lng | Inverter Longitude | W |  |  |  |  | ALL |  |  | 0 | Type number : INV-Lng "Growatt_INV-Lng" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.INV-Lng", formatBeforePublish="INV-Lng%s"] | Number Growatt_INV-Lng "INV-Lng" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:INV-Lng"} |  | 1,1,INV-Lng,5,241,0,2,0
| 3 | 242 | INV-Lat | Inverter Latitude | W |  |  |  |  | ALL |  |  | 0 | Type number : INV-Lat "Growatt_INV-Lat" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.INV-Lat", formatBeforePublish="INV-Lat%s"] | Number Growatt_INV-Lat "INV-Lat" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:INV-Lat"} |  | 1,1,INV-Lat,5,242,0,2,0
| 3 | 304 | uwAntiBackflowFailPowerLimitEE | Anti-backflow failure power percentage | R/W | 0-1000 | 0.001 |  | ASCII | ALL | 0.001 |  | 3 | Type number : uwAntiBackflowFailPowerLimitEE "Growatt_uwAntiBackflowFailPowerLimitEE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwAntiBackflowFailPowerLimitEE", formatBeforePublish="uwAntiBackflowFailPowerLimitEE%s"] | Number Growatt_uwAntiBackflowFailPowerLimitEE "uwAntiBackflowFailPowerLimitEE [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwAntiBackflowFailPowerLimitEE"} | 65.,uwAntiBackflowFailPowerLimitEE,Modbus RTU,,5,3,304,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwAntiBackflowFailPowerLimitEE,5,304,0,2,0
| 3 | 305 | Qloadspeed | Reactive loading speed | R/W | 0-100 | 0.01 |  | 0-200:0-20? | TL_X-TL_XH | 0.01 |  | 2 | Type number : Qloadspeed "Growatt_Qloadspeed" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Qloadspeed", formatBeforePublish="Qloadspeed%s"] | Number Growatt_Qloadspeed "Qloadspeed [%0.01f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Qloadspeed"} | 65.,Qloadspeed,Modbus RTU,,5,3,305,1,9410,2,0,Unsigned int,0,2,,1,100,97,0,0,0,1.000000,0,255 | 1,1,Qloadspeed,5,305,0,2,0
| 3 | 306 | bParallelAntiBackflowEnable | ParallelAnti-Backflow | R/W | 0-1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bParallelAntiBackflowEnable "Growatt_bParallelAntiBackflowEnable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bParallelAntiBackflowEnable", formatBeforePublish="bParallelAntiBackflowEnable%s"] | Number Growatt_bParallelAntiBackflowEnable "bParallelAntiBackflowEnable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bParallelAntiBackflowEnable"} | 65.,bParallelAntiBackflowEnable,Modbus RTU,,5,3,306,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,bParallelAntiBackflowEnable,5,306,0,2,0
| 3 | 307 | uwAntiBackflowFailureResponseTime | AntiBackflowFailure | R/W | 1132254 | 1s |  | ASCII | ALL | 1 | s | 0 | Type number : uwAntiBackflowFailureResponseTime "Growatt_uwAntiBackflowFailureResponseTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwAntiBackflowFailureResponseTime", formatBeforePublish="uwAntiBackflowFailureResponseTime%s"] | Number:Time Growatt_uwAntiBackflowFailureResponseTime "uwAntiBackflowFailureResponseTime [%1f s]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwAntiBackflowFailureResponseTime"} | 65.,uwAntiBackflowFailureResponseTime,Modbus RTU,,5,3,307,1,9410,2,0,Unsigned int,0,0,s,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwAntiBackflowFailureResponseTime,5,307,0,2,0
| 3 | 308 | uwParallelAntiBackflowPowerLimitEE | ParallelAntiBackflowPo wer | R/W | 0-1000 | 0.001 |  | UL | ALL | 0.001 |  | 3 | Type number : uwParallelAntiBackflowPowerLimitEE "Growatt_uwParallelAntiBackflowPowerLimitEE" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwParallelAntiBackflowPowerLimitEE", formatBeforePublish="uwParallelAntiBackflowPowerLimitEE%s"] | Number Growatt_uwParallelAntiBackflowPowerLimitEE "uwParallelAntiBackflowPowerLimitEE [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwParallelAntiBackflowPowerLimitEE"} | 65.,uwParallelAntiBackflowPowerLimitEE,Modbus RTU,,5,3,308,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwParallelAntiBackflowPowerLimitEE,5,308,0,2,0
| 3 | 309 | bISOCheckCmd | ISO detection | R/W | 0-1 | 1 |  |  | TL_X-TL_XH | 1 |  | 0 | Type number : bISOCheckCmd "Growatt_bISOCheckCmd" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bISOCheckCmd", formatBeforePublish="bISOCheckCmd%s"] | Number Growatt_bISOCheckCmd "bISOCheckCmd [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bISOCheckCmd"} | 65.,bISOCheckCmd,Modbus RTU,,5,3,309,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,bISOCheckCmd,5,309,0,2,0
| 3 | 310 | bGPRSStatus | GPRS Status | R/W | 0-255 | 1 |  |  | TL_X-TL_XH | 1 |  | 0 | Type number : bGPRSStatus "Growatt_bGPRSStatus" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bGPRSStatus", formatBeforePublish="bGPRSStatus%s"] | Number Growatt_bGPRSStatus "bGPRSStatus [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bGPRSStatus"} | 65.,bGPRSStatus,Modbus RTU,,5,3,310,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,bGPRSStatus,5,310,0,2,0
| 3 | 311 | uwQmax_Inductive | The inductive Qmax of the Q(V) curve | R/W | 0-1000 | 0.001 |  | CEI | ALL | 0.001 |  | 3 | Type number : uwQmax_Inductive "Growatt_uwQmax_Inductive" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwQmax_Inductive", formatBeforePublish="uwQmax_Inductive%s"] | Number Growatt_uwQmax_Inductive "uwQmax_Inductive [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwQmax_Inductive"} | 65.,uwQmax_Inductive,Modbus RTU,,5,3,311,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwQmax_Inductive,5,311,0,2,0
| 3 | 312 | uwQmax_Capactive | The Capactive Qmax of | R/W | 0-1000 | 0.001 |  | CEI | ALL | 0.001 |  | 3 | Type number : uwQmax_Capactive "Growatt_uwQmax_Capactive" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwQmax_Capactive", formatBeforePublish="uwQmax_Capactive%s"] | Number Growatt_uwQmax_Capactive "uwQmax_Capactive [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwQmax_Capactive"} | 65.,uwQmax_Capactive,Modbus RTU,,5,3,312,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwQmax_Capactive,5,312,0,2,0
| 3 | 313 | uwReactivePowerAdjustFailureResponseTime | ReactivePowerAdjust | R/W | 0-5000 | S |  |  | ALL |  | S | 0 | Type number : uwReactivePowerAdjustFailureResponseTime "Growatt_uwReactivePowerAdjustFailureResponseTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwReactivePowerAdjustFailureResponseTime", formatBeforePublish="uwReactivePowerAdjustFailureResponseTime%s"] | Number:Time Growatt_uwReactivePowerAdjustFailureResponseTime "uwReactivePowerAdjustFailureResponseTime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwReactivePowerAdjustFailureResponseTime"} | 65.,uwReactivePowerAdjustFailureResponseTime,Modbus RTU,,5,3,313,1,9410,2,0,Unsigned int,0,0,S,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwReactivePowerAdjustFailureResponseTime,5,313,0,2,0
| 3 | 314 | bSuperAntiBackflowEnable | SuperAntiBackflow | R/W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bSuperAntiBackflowEnable "Growatt_bSuperAntiBackflowEnable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bSuperAntiBackflowEnable", formatBeforePublish="bSuperAntiBackflowEnable%s"] | Number Growatt_bSuperAntiBackflowEnable "bSuperAntiBackflowEnable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bSuperAntiBackflowEnable"} | 65.,bSuperAntiBackflowEnable,Modbus RTU,,5,3,314,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,bSuperAntiBackflowEnable,5,314,0,2,0
| 3 | 315 | uwReactivePowerStableTime | ReactivePowerStableTi | R/W | 0-200 | S |  |  | ALL |  | S | 0 | Type number : uwReactivePowerStableTime "Growatt_uwReactivePowerStableTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwReactivePowerStableTime", formatBeforePublish="uwReactivePowerStableTime%s"] | Number:Time Growatt_uwReactivePowerStableTime "uwReactivePowerStableTime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwReactivePowerStableTime"} | 65.,uwReactivePowerStableTime,Modbus RTU,,5,3,315,1,9410,2,0,Unsigned int,0,0,S,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwReactivePowerStableTime,5,315,0,2,0
| 3 | 316 | uwQpStableTime | QpStableTime | R/W | 0-200 | S |  | CEI | ALL |  | S | 0 | Type number : uwQpStableTime "Growatt_uwQpStableTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwQpStableTime", formatBeforePublish="uwQpStableTime%s"] | Number:Time Growatt_uwQpStableTime "uwQpStableTime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwQpStableTime"} | 65.,uwQpStableTime,Modbus RTU,,5,3,316,1,9410,2,0,Unsigned int,0,0,S,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwQpStableTime,5,316,0,2,0
| 3 | 317 | uwPuDerateTime | PuDerateTime | R/W | 0-200 | S |  | CEI | ALL |  | S | 0 | Type number : uwPuDerateTime "Growatt_uwPuDerateTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwPuDerateTime", formatBeforePublish="uwPuDerateTime%s"] | Number:Time Growatt_uwPuDerateTime "uwPuDerateTime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwPuDerateTime"} | 65.,uwPuDerateTime,Modbus RTU,,5,3,317,1,9410,2,0,Unsigned int,0,0,S,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwPuDerateTime,5,317,0,2,0
| 3 | 318 | uwQVModelQ2Point | QV mode Q2 set point reactive power | R/W | 0-2000 | 0.001 |  | CEI | ALL | 0.001 |  | 3 | Type number : uwQVModelQ2Point "Growatt_uwQVModelQ2Point" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwQVModelQ2Point", formatBeforePublish="uwQVModelQ2Point%s"] | Number Growatt_uwQVModelQ2Point "uwQVModelQ2Point [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwQVModelQ2Point"} | 65.,uwQVModelQ2Point,Modbus RTU,,5,3,318,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwQVModelQ2Point,5,318,0,2,0
| 3 | 319 | uwQVModelQ3Point | QV mode Q3 set point reactive power | R/W | 0-2000 | 0.001 |  | CEI | ALL | 0.001 |  | 3 | Type number : uwQVModelQ3Point "Growatt_uwQVModelQ3Point" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwQVModelQ3Point", formatBeforePublish="uwQVModelQ3Point%s"] | Number Growatt_uwQVModelQ3Point "uwQVModelQ3Point [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwQVModelQ3Point"} | 65.,uwQVModelQ3Point,Modbus RTU,,5,3,319,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwQVModelQ3Point,5,319,0,2,0
| 3 | 320 | bVrefModelEnable | VrefModelEnable | R/W | 0 : Vref mode for QV curve is not active |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bVrefModelEnable "Growatt_bVrefModelEnable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bVrefModelEnable", formatBeforePublish="bVrefModelEnable%s"] | Number Growatt_bVrefModelEnable "bVrefModelEnable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bVrefModelEnable"} | 65.,bVrefModelEnable,Modbus RTU,,5,3,320,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,bVrefModelEnable,5,320,0,2,0
| 3 | 321 | uwVrefModelFilterTime | VrefModelFilterTime | R/W | 0-5000 | S |  | ASCII | ALL |  | S | 0 | Type number : uwVrefModelFilterTime "Growatt_uwVrefModelFilterTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwVrefModelFilterTime", formatBeforePublish="uwVrefModelFilterTime%s"] | Number:Time Growatt_uwVrefModelFilterTime "uwVrefModelFilterTime" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwVrefModelFilterTime"} | 65.,uwVrefModelFilterTime,Modbus RTU,,5,3,321,1,9410,2,0,Unsigned int,0,0,S,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwVrefModelFilterTime,5,321,0,2,0
| 3 | 322 | uwUserQPModeP1Krate | Active power P1 set point percentage for | R/W | 0-1000 | 0.001 |  |  | ALL | 0.001 |  | 3 | Type number : uwUserQPModeP1Krate "Growatt_uwUserQPModeP1Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUserQPModeP1Krate", formatBeforePublish="uwUserQPModeP1Krate%s"] | Number Growatt_uwUserQPModeP1Krate "uwUserQPModeP1Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwUserQPModeP1Krate"} | 65.,uwUserQPModeP1Krate,Modbus RTU,,5,3,322,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUserQPModeP1Krate,5,322,0,2,0
| 3 | 323 | uwUserQPModeP2Krate | Active power P2 point percentage | R/W | 0-1000 | 0.001 |  |  | ALL | 0.001 |  | 3 | Type number : uwUserQPModeP2Krate "Growatt_uwUserQPModeP2Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUserQPModeP2Krate", formatBeforePublish="uwUserQPModeP2Krate%s"] | Number Growatt_uwUserQPModeP2Krate "uwUserQPModeP2Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwUserQPModeP2Krate"} | 65.,uwUserQPModeP2Krate,Modbus RTU,,5,3,323,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUserQPModeP2Krate,5,323,0,2,0
| 3 | 324 | uwUserQPModeP3Krate | Active power P3 point percentage | R/W | 0-1000 | 0.001 |  |  | ALL | 0.001 |  | 3 | Type number : uwUserQPModeP3Krate "Growatt_uwUserQPModeP3Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUserQPModeP3Krate", formatBeforePublish="uwUserQPModeP3Krate%s"] | Number Growatt_uwUserQPModeP3Krate "uwUserQPModeP3Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwUserQPModeP3Krate"} | 65.,uwUserQPModeP3Krate,Modbus RTU,,5,3,324,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUserQPModeP3Krate,5,324,0,2,0
| 3 | 325 | uwUserQPModeQ1Krate | Reactive power Q1 set point percentage for | R/W | -1010 | 0.001 |  | ASCII | ALL | 0.001 |  | 3 | Type number : uwUserQPModeQ1Krate "Growatt_uwUserQPModeQ1Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUserQPModeQ1Krate", formatBeforePublish="uwUserQPModeQ1Krate%s"] | Number Growatt_uwUserQPModeQ1Krate "uwUserQPModeQ1Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwUserQPModeQ1Krate"} | 65.,uwUserQPModeQ1Krate,Modbus RTU,,5,3,325,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUserQPModeQ1Krate,5,325,0,2,0
| 3 | 326 | uwUserQPModeQ2Krate | Reactive power Q2 set point percentage for | R/W | -1010 | 0.001 |  | ASCII | ALL | 0.001 |  | 3 | Type number : uwUserQPModeQ2Krate "Growatt_uwUserQPModeQ2Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUserQPModeQ2Krate", formatBeforePublish="uwUserQPModeQ2Krate%s"] | Number Growatt_uwUserQPModeQ2Krate "uwUserQPModeQ2Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwUserQPModeQ2Krate"} | 65.,uwUserQPModeQ2Krate,Modbus RTU,,5,3,326,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUserQPModeQ2Krate,5,326,0,2,0
| 3 | 327 | uwUserQPModeQ3Krate | Reactive power Q3 set point percentage for | R/W | -1010 | 0.001 |  | ASCII | ALL | 0.001 |  | 3 | Type number : uwUserQPModeQ3Krate "Growatt_uwUserQPModeQ3Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUserQPModeQ3Krate", formatBeforePublish="uwUserQPModeQ3Krate%s"] | Number Growatt_uwUserQPModeQ3Krate "uwUserQPModeQ3Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwUserQPModeQ3Krate"} | 65.,uwUserQPModeQ3Krate,Modbus RTU,,5,3,327,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUserQPModeQ3Krate,5,327,0,2,0
| 3 | 328 | uwAcVoltHighDeratPowerLimit | AcVoltHighDeratPower | R/W | 0-1000 | 0.001 |  | SpecialDay1_Time | ALL | 0.001 |  | 3 | Type number : uwAcVoltHighDeratPowerLimit "Growatt_uwAcVoltHighDeratPowerLimit" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwAcVoltHighDeratPowerLimit", formatBeforePublish="uwAcVoltHighDeratPowerLimit%s"] | Number Growatt_uwAcVoltHighDeratPowerLimit "uwAcVoltHighDeratPowerLimit [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwAcVoltHighDeratPowerLimit"} | 65.,uwAcVoltHighDeratPowerLimit,Modbus RTU,,5,3,328,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwAcVoltHighDeratPowerLimit,5,328,0,2,0
| 3 | 329 | BackflowSingleCtrl | BackflowSingleCtrl | R/W | 0: disable |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BackflowSingleCtrl "Growatt_BackflowSingleCtrl" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BackflowSingleCtrl", formatBeforePublish="BackflowSingleCtrl%s"] | Number Growatt_BackflowSingleCtrl "BackflowSingleCtrl" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BackflowSingleCtrl"} | 65.,BackflowSingleCtrl,Modbus RTU,,5,3,329,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,BackflowSingleCtrl,5,329,0,2,0
| 3 | 330 | bAntiBackflowProtectMode | AntiBackflowProtectM ode | R/W | 0-3 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bAntiBackflowProtectMode "Growatt_bAntiBackflowProtectMode" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bAntiBackflowProtectMode", formatBeforePublish="bAntiBackflowProtectMode%s"] | Number Growatt_bAntiBackflowProtectMode "bAntiBackflowProtectMode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bAntiBackflowProtectMode"} | 65.,bAntiBackflowProtectMode,Modbus RTU,,5,3,330,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,bAntiBackflowProtectMode,5,330,0,2,0
| 3 | 331 | uwUnderFUploadZeroPowerPoint | UnderfreqUploadZeroP owerPoint | W |  | 0.01H |  | 0:disable | ALL | 0.01 | H | 2 | Type number : uwUnderFUploadZeroPowerPoint "Growatt_uwUnderFUploadZeroPowerPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUnderFUploadZeroPowerPoint", formatBeforePublish="uwUnderFUploadZeroPowerPoint%s"] | #N/A |  | 1,1,uwUnderFUploadZeroPowerPoint,5,331,0,2,0
| 3 | 332 | FreqDerateZeroPowerPoint | FreqDerateZeroPowerP oint | W |  | 0.01H |  |  | PV9_32 | 0.01 | H | 2 | Type number : FreqDerateZeroPowerPoint "Growatt_FreqDerateZeroPowerPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FreqDerateZeroPowerPoint", formatBeforePublish="FreqDerateZeroPowerPoint%s"] | #N/A |  | 1,1,FreqDerateZeroPowerPoint,5,332,0,2,0
| 3 | 333 | bFreqDeratingStopModeEnable | FreqDeratingStopMode | R/W | 0-1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bFreqDeratingStopModeEnable "Growatt_bFreqDeratingStopModeEnable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bFreqDeratingStopModeEnable", formatBeforePublish="bFreqDeratingStopModeEnable%s"] | Number Growatt_bFreqDeratingStopModeEnable "bFreqDeratingStopModeEnable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bFreqDeratingStopModeEnable"} | 65.,bFreqDeratingStopModeEnable,Modbus RTU,,5,3,333,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,bFreqDeratingStopModeEnable,5,333,0,2,0
| 3 | 334 | bFreqIncreasingEnable | FreqIncreasingEnable | R/W | 0-1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bFreqIncreasingEnable "Growatt_bFreqIncreasingEnable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bFreqIncreasingEnable", formatBeforePublish="bFreqIncreasingEnable%s"] | Number Growatt_bFreqIncreasingEnable "bFreqIncreasingEnable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bFreqIncreasingEnable"} | 65.,bFreqIncreasingEnable,Modbus RTU,,5,3,334,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,bFreqIncreasingEnable,5,334,0,2,0
| 3 | 335 | uwFreqIncreasingRecoverTime | FreqIncreasingRecover | R/W |  | 50ms |  |  | ALL | 50 | ms | 1 | Type number : uwFreqIncreasingRecoverTime "Growatt_uwFreqIncreasingRecoverTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwFreqIncreasingRecoverTime", formatBeforePublish="uwFreqIncreasingRecoverTime%s"] | #N/A | 65.,uwFreqIncreasingRecoverTime,Modbus RTU,,5,3,335,1,9410,2,0,Unsigned int,0,1,ms,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwFreqIncreasingRecoverTime,5,335,0,2,0
| 3 | 336 | uwFreqIncreasingEndLowPoint | FreqIncreasingEndLow | R/W |  | 0.01H |  | ASCII | ALL | 0.01 | H | 2 | Type number : uwFreqIncreasingEndLowPoint "Growatt_uwFreqIncreasingEndLowPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwFreqIncreasingEndLowPoint", formatBeforePublish="uwFreqIncreasingEndLowPoint%s"] | #N/A | 65.,uwFreqIncreasingEndLowPoint,Modbus RTU,,5,3,336,1,9410,2,0,Unsigned int,0,2,H,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwFreqIncreasingEndLowPoint,5,336,0,2,0
| 3 | 337 | bFreqIncreasingStopModeEnable | FreqIncreasingStopMo deEnable | R/W | 0-1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bFreqIncreasingStopModeEnable "Growatt_bFreqIncreasingStopModeEnable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bFreqIncreasingStopModeEnable", formatBeforePublish="bFreqIncreasingStopModeEnable%s"] | Number Growatt_bFreqIncreasingStopModeEnable "bFreqIncreasingStopModeEnable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bFreqIncreasingStopModeEnable"} | 65.,bFreqIncreasingStopModeEnable,Modbus RTU,,5,3,337,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,bFreqIncreasingStopModeEnable,5,337,0,2,0
| 3 | 338 | uwUserQpChrP1Krate | User QP charge P1 percentage | R/W | 0-1000 | 0.001 |  |  | ALL | 0.001 |  | 3 | Type number : uwUserQpChrP1Krate "Growatt_uwUserQpChrP1Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUserQpChrP1Krate", formatBeforePublish="uwUserQpChrP1Krate%s"] | Number Growatt_uwUserQpChrP1Krate "uwUserQpChrP1Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwUserQpChrP1Krate"} | 65.,uwUserQpChrP1Krate,Modbus RTU,,5,3,338,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUserQpChrP1Krate,5,338,0,2,0
| 3 | 339 | uwUserQpChrP2Krate | User QP charge P2 percentage | R/W | 0-1000 | 0.001 |  |  | ALL | 0.001 |  | 3 | Type number : uwUserQpChrP2Krate "Growatt_uwUserQpChrP2Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUserQpChrP2Krate", formatBeforePublish="uwUserQpChrP2Krate%s"] | Number Growatt_uwUserQpChrP2Krate "uwUserQpChrP2Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwUserQpChrP2Krate"} | 65.,uwUserQpChrP2Krate,Modbus RTU,,5,3,339,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUserQpChrP2Krate,5,339,0,2,0
| 3 | 340 | uwUserQpChrP3Krate | User QP charge P3 percentage | R/W | 0-1000 | 0.001 |  |  | ALL | 0.001 |  | 3 | Type number : uwUserQpChrP3Krate "Growatt_uwUserQpChrP3Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUserQpChrP3Krate", formatBeforePublish="uwUserQpChrP3Krate%s"] | Number Growatt_uwUserQpChrP3Krate "uwUserQpChrP3Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwUserQpChrP3Krate"} | 65.,uwUserQpChrP3Krate,Modbus RTU,,5,3,340,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwUserQpChrP3Krate,5,340,0,2,0
| 3 | 341 | wUserQpChrQ1Krate | User QP | R/W | -1010 | 0.001 |  | 255: power is not be limited | ALL | 0.001 |  | 3 | Type number : wUserQpChrQ1Krate "Growatt_wUserQpChrQ1Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.wUserQpChrQ1Krate", formatBeforePublish="wUserQpChrQ1Krate%s"] | Number Growatt_wUserQpChrQ1Krate "wUserQpChrQ1Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:wUserQpChrQ1Krate"} | 65.,wUserQpChrQ1Krate,Modbus RTU,,5,3,341,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,wUserQpChrQ1Krate,5,341,0,2,0
| 3 | 342 | wUserQpChrQ2Krate | User QP | R/W | -1010 | 0.001 |  | Means these settings will be acting or not when next power on | ALL | 0.001 |  | 3 | Type number : wUserQpChrQ2Krate "Growatt_wUserQpChrQ2Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.wUserQpChrQ2Krate", formatBeforePublish="wUserQpChrQ2Krate%s"] | Number Growatt_wUserQpChrQ2Krate "wUserQpChrQ2Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:wUserQpChrQ2Krate"} | 65.,wUserQpChrQ2Krate,Modbus RTU,,5,3,342,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,wUserQpChrQ2Krate,5,342,0,2,0
| 3 | 343 | wUserQpChrQ3Krate | User QP | R/W | -1010 | 0.001 |  | SPI: system protection interface Bit0~3:for CEI0-21 Bit4~6:for SAA | ALL | 0.001 |  | 3 | Type number : wUserQpChrQ3Krate "Growatt_wUserQpChrQ3Krate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.wUserQpChrQ3Krate", formatBeforePublish="wUserQpChrQ3Krate%s"] | Number Growatt_wUserQpChrQ3Krate "wUserQpChrQ3Krate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:wUserQpChrQ3Krate"} | 65.,wUserQpChrQ3Krate,Modbus RTU,,5,3,343,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,wUserQpChrQ3Krate,5,343,0,2,0
| 3 | 344 | uwFreqDeratingRecoverLowPoint | FreqDeratingRecoverLo wPoint | R/W |  | 0.01H |  | ASCII | ALL | 0.01 | H | 2 | Type number : uwFreqDeratingRecoverLowPoint "Growatt_uwFreqDeratingRecoverLowPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwFreqDeratingRecoverLowPoint", formatBeforePublish="uwFreqDeratingRecoverLowPoint%s"] | #N/A | 65.,uwFreqDeratingRecoverLowPoint,Modbus RTU,,5,3,344,1,9410,2,0,Unsigned int,0,2,H,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwFreqDeratingRecoverLowPoint,5,344,0,2,0
| 3 | 345 | uwFreqIncreasingRecoverHighPoint | FreqIncreasingRecover | R/W |  | 0.01H |  |  | ALL | 0.01 | H | 2 | Type number : uwFreqIncreasingRecoverHighPoint "Growatt_uwFreqIncreasingRecoverHighPoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwFreqIncreasingRecoverHighPoint", formatBeforePublish="uwFreqIncreasingRecoverHighPoint%s"] | #N/A | 65.,uwFreqIncreasingRecoverHighPoint,Modbus RTU,,5,3,345,1,9410,2,0,Unsigned int,0,2,H,1,100,97,0,0,0,1.000000,0,255 | 1,1,uwFreqIncreasingRecoverHighPoint,5,345,0,2,0
| 3 | 532 | TurnOffUnloadSpeed | TurnOffUnloadSpeed | R/W | 0-1000 | 0.001 | 0,001 |  | ALL | 0.001 |  | 3 | Type number : TurnOffUnloadSpeed "Growatt_TurnOffUnloadSpeed" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.TurnOffUnloadSpeed", formatBeforePublish="TurnOffUnloadSpeed%s"] | Number Growatt_TurnOffUnloadSpeed "TurnOffUnloadSpeed [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TurnOffUnloadSpeed"} | 65.,TurnOffUnloadSpeed,Modbus RTU,,5,3,532,1,9410,2,0,Unsigned int,0,3,,1,100,97,0,0,0,1.000000,0,255 | 1,1,TurnOffUnloadSpeed,5,532,0,2,0
| 3 | 533 | LimitDevice | Anti-backflow equipment selection | R/W | 0-3 |  |  |  | ALL |  |  | 0 | Type number : LimitDevice "Growatt_LimitDevice" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LimitDevice", formatBeforePublish="LimitDevice%s"] | Number Growatt_LimitDevice "LimitDevice" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:LimitDevice"} | 65.,LimitDevice,Modbus RTU,,5,3,533,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,LimitDevice,5,533,0,2,0
| 3 | 534 | PowerSetOndCSourceMode | Power settings in dc source mode | R/W | 0-90000 |  |  | Same as Time 1 | USTimeSet |  |  | 0 | Type number : PowerSetOndCSourceMode "Growatt_PowerSetOndCSourceMode" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PowerSetOndCSourceMode", formatBeforePublish="PowerSetOndCSourceMode%s"] | Number Growatt_PowerSetOndCSourceMode "PowerSetOndCSourceMode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PowerSetOndCSourceMode"} | 65.,PowerSetOndCSourceMode,Modbus RTU,,5,3,534,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,PowerSetOndCSourceMode,5,534,0,2,0
| 3 | 535 | OUFreqGrade1En | Over-under-frequency | R/W | 0-1 |  |  |  | ALL |  |  | 0 | Type number : OUFreqGrade1En "Growatt_OUFreqGrade1En" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.OUFreqGrade1En", formatBeforePublish="OUFreqGrade1En%s"] | Number Growatt_OUFreqGrade1En "OUFreqGrade1En" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OUFreqGrade1En"} | 65.,OUFreqGrade1En,Modbus RTU,,5,3,535,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,OUFreqGrade1En,5,535,0,2,0
| 3 | 536 | CountrySet | Country settings under the same safety regulations | R/W | 0-200 |  |  | Three phase grid output power | TL_X-TL_XH |  |  | 0 | Type number : CountrySet "Growatt_CountrySet" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.CountrySet", formatBeforePublish="CountrySet%s"] | Number Growatt_CountrySet "CountrySet" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CountrySet"} | 65.,CountrySet,Modbus RTU,,5,3,536,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,CountrySet,5,536,0,2,0
| 3 | 538 | InterlockEnable | Three-machine communication | R/W | 0-2 |  |  |  | ALL |  |  | 0 | Type number : InterlockEnable "Growatt_InterlockEnable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.InterlockEnable", formatBeforePublish="InterlockEnable%s"] | Number Growatt_InterlockEnable "InterlockEnable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:InterlockEnable"} | 65.,InterlockEnable,Modbus RTU,,5,3,538,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,InterlockEnable,5,538,0,2,0
| 3 | 539 | OvTemperDeratePoint | Over temperature derate point | R/W |  |  |  |  | ALL |  |  | 0 | Type number : OvTemperDeratePoint "Growatt_OvTemperDeratePoint" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.OvTemperDeratePoint", formatBeforePublish="OvTemperDeratePoint%s"] | Number Growatt_OvTemperDeratePoint "OvTemperDeratePoint" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OvTemperDeratePoint"} | 65.,OvTemperDeratePoint,Modbus RTU,,5,3,539,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,OvTemperDeratePoint,5,539,0,2,0
| 3 | 540 | SafetySetPassword | Switch between different safety regulations to set the | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SafetySetPassword "Growatt_SafetySetPassword" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SafetySetPassword", formatBeforePublish="SafetySetPassword%s"] | Number Growatt_SafetySetPassword "SafetySetPassword" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SafetySetPassword"} | 65.,SafetySetPassword,Modbus RTU,,5,3,540,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,SafetySetPassword,5,540,0,2,0
| 3 | 541 | AFCIOnoff | AFCI Onoff | R/W | 0xA0/0xA |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : AFCIOnoff "Growatt_AFCIOnoff" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.AFCIOnoff", formatBeforePublish="AFCIOnoff%s"] | Number Growatt_AFCIOnoff "AFCIOnoff" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AFCIOnoff"} | 65.,AFCIOnoff,Modbus RTU,,5,3,541,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,AFCIOnoff,5,541,0,2,0
| 3 | 542 | AfciSelfCheck | AfciSelfCheck | R/W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : AfciSelfCheck "Growatt_AfciSelfCheck" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.AfciSelfCheck", formatBeforePublish="AfciSelfCheck%s"] | Number Growatt_AfciSelfCheck "AfciSelfCheck" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AfciSelfCheck"} | 65.,AfciSelfCheck,Modbus RTU,,5,3,542,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,AfciSelfCheck,5,542,0,2,0
| 3 | 543 | AfciReset | AfciReset | R/W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : AfciReset "Growatt_AfciReset" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.AfciReset", formatBeforePublish="AfciReset%s"] | Number Growatt_AfciReset "AfciReset" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AfciReset"} | 65.,AfciReset,Modbus RTU,,5,3,543,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,AfciReset,5,543,0,2,0
| 3 | 544 | AFCIValue1 | AFCIThresholdValue | R/W | 0-65000 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : AFCIValue1 "Growatt_AFCIValue1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.AFCIValue1", formatBeforePublish="AFCIValue1%s"] | Number Growatt_AFCIValue1 "AFCIValue1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AFCIValue1"} | 65.,AFCIValue1,Modbus RTU,,5,3,544,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,AFCIValue1,5,544,0,2,0
| 3 | 545 | AFCIValue2 | AFCIThresholdValue | R/W | 0-65000 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : AFCIValue2 "Growatt_AFCIValue2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.AFCIValue2", formatBeforePublish="AFCIValue2%s"] | Number Growatt_AFCIValue2 "AFCIValue2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AFCIValue2"} | 65.,AFCIValue2,Modbus RTU,,5,3,545,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,AFCIValue2,5,545,0,2,0
| 3 | 546 | AFCIValue3 | AFCIThresholdValue | R/W | 0-65000 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : AFCIValue3 "Growatt_AFCIValue3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.AFCIValue3", formatBeforePublish="AFCIValue3%s"] | Number Growatt_AFCIValue3 "AFCIValue3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AFCIValue3"} | 65.,AFCIValue3,Modbus RTU,,5,3,546,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,AFCIValue3,5,546,0,2,0
| 3 | 547 | OverThresholdValueMaxCnt | OverThresholdValueMa xCnt | R/W | 0-255 |  |  |  | ALL |  |  | 0 | Type number : OverThresholdValueMaxCnt "Growatt_OverThresholdValueMaxCnt" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.OverThresholdValueMaxCnt", formatBeforePublish="OverThresholdValueMaxCnt%s"] | Number Growatt_OverThresholdValueMaxCnt "OverThresholdValueMaxCnt" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OverThresholdValueMaxCnt"} | 65.,OverThresholdValueMaxCnt,Modbus RTU,,5,3,547,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,OverThresholdValueMaxCnt,5,547,0,2,0
| 3 | 548 | AFCIScanTypeEnable | AFCI curve scan type | R/W | 1~4 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : AFCIScanTypeEnable "Growatt_AFCIScanTypeEnable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.AFCIScanTypeEnable", formatBeforePublish="AFCIScanTypeEnable%s"] | Number Growatt_AFCIScanTypeEnable "AFCIScanTypeEnable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AFCIScanTypeEnable"} | 65.,AFCIScanTypeEnable,Modbus RTU,,5,3,548,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,AFCIScanTypeEnable,5,548,0,2,0
| 3 | 549 | PowerVoltStopModeEn | PowerVoltStopModeEn | R/W | 0?1 |  |  | Same as Time 1 | USTimeSet |  |  | 0 | Type number : PowerVoltStopModeEn "Growatt_PowerVoltStopModeEn" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PowerVoltStopModeEn", formatBeforePublish="PowerVoltStopModeEn%s"] | Number Growatt_PowerVoltStopModeEn "PowerVoltStopModeEn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PowerVoltStopModeEn"} | 65.,PowerVoltStopModeEn,Modbus RTU,,5,3,549,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,PowerVoltStopModeEn,5,549,0,2,0
| 3 | 550 | VoltWattRecoverTime | Voltage active power recovery time | R/W | 0-15000 | 20ms |  |  | ALL | 20 | ms | 1 | Type number : VoltWattRecoverTime "Growatt_VoltWattRecoverTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.VoltWattRecoverTime", formatBeforePublish="VoltWattRecoverTime%s"] | #N/A | 65.,VoltWattRecoverTime,Modbus RTU,,5,3,550,1,9410,2,0,Unsigned int,0,1,ms,1,100,97,0,0,0,1.000000,0,255 | 1,1,VoltWattRecoverTime,5,550,0,2,0
| 3 | 551 | HVoltDerate | Voltage active cut-off | R/W | -5011 |  |  |  | ALL |  |  | 0 | Type number : HVoltDerate "Growatt_HVoltDerate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.HVoltDerate", formatBeforePublish="HVoltDerate%s"] | Number Growatt_HVoltDerate "HVoltDerate" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:HVoltDerate"} | 65.,HVoltDerate,Modbus RTU,,5,3,551,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,HVoltDerate,5,551,0,2,0
| 3 | 552 | QVTimeExponent | QVTimeExponent | R/W | 1-255 |  |  | Clear battery low voltage error voltage point | TL_X-TL_XH |  |  | 0 | Type number : QVTimeExponent "Growatt_QVTimeExponent" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.QVTimeExponent", formatBeforePublish="QVTimeExponent%s"] | Number Growatt_QVTimeExponent "QVTimeExponent" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:QVTimeExponent"} | 65.,QVTimeExponent,Modbus RTU,,5,3,552,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,QVTimeExponent,5,552,0,2,0
| 3 | 553 | Volt-Watt1 | Voltage active V1 point, corresponding active power | R/W | 0-11400 |  |  |  | ALL |  |  | 0 | Type number : Volt-Watt1 "Growatt_Volt-Watt1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Volt-Watt1", formatBeforePublish="Volt-Watt1%s"] | Number Growatt_Volt-Watt1 "Volt-Watt1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Volt-Watt1"} | 65.,Volt-Watt1,Modbus RTU,,5,3,553,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,Volt-Watt1,5,553,0,2,0
| 3 | 554 | Volt-Watt2 | Voltage active V2 point, corresponding active power | R/W | 0-11400 |  |  |  | ALL |  |  | 0 | Type number : Volt-Watt2 "Growatt_Volt-Watt2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Volt-Watt2", formatBeforePublish="Volt-Watt2%s"] | Number Growatt_Volt-Watt2 "Volt-Watt2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Volt-Watt2"} | 65.,Volt-Watt2,Modbus RTU,,5,3,554,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,Volt-Watt2,5,554,0,2,0
| 3 | 600 | Volt-Var1 | Voltage reactive V1 | R/W | 0-1000 |  |  | Local time | ALL |  |  | 0 | Type number : Volt-Var1 "Growatt_Volt-Var1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Volt-Var1", formatBeforePublish="Volt-Var1%s"] | Number Growatt_Volt-Var1 "Volt-Var1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Volt-Var1"} | 65.,Volt-Var1,Modbus RTU,,5,3,600,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,Volt-Var1,5,600,0,2,0
| 3 | 601 | Volt-Var2 | Voltage reactive point,V2 | R/W | 0-1000 |  |  | Eg:0x020 | ALL |  |  | 0 | Type number : Volt-Var2 "Growatt_Volt-Var2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Volt-Var2", formatBeforePublish="Volt-Var2%s"] | Number Growatt_Volt-Var2 "Volt-Var2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Volt-Var2"} | 65.,Volt-Var2,Modbus RTU,,5,3,601,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,Volt-Var2,5,601,0,2,0
| 3 | 602 | Volt-Var3 | Voltage reactive point,V3 | R/W | 0-1000 |  |  |  | ALL |  |  | 0 | Type number : Volt-Var3 "Growatt_Volt-Var3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Volt-Var3", formatBeforePublish="Volt-Var3%s"] | Number Growatt_Volt-Var3 "Volt-Var3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Volt-Var3"} | 65.,Volt-Var3,Modbus RTU,,5,3,602,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,Volt-Var3,5,602,0,2,0
| 3 | 603 | Volt-Var4 | Voltage reactive point,V4 | R/W | 0-1000 |  |  | English G100 fail safe set | ALL |  |  | 0 | Type number : Volt-Var4 "Growatt_Volt-Var4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Volt-Var4", formatBeforePublish="Volt-Var4%s"] | Number Growatt_Volt-Var4 "Volt-Var4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Volt-Var4"} | 65.,Volt-Var4,Modbus RTU,,5,3,603,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,Volt-Var4,5,603,0,2,0
| 3 | 605 | OPModEner | Allowed inverter output power | R/W | 0/1 |  |  |  | ALL |  |  | 0 | Type number : OPModEner "Growatt_OPModEner" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.OPModEner", formatBeforePublish="OPModEner%s"] | Number Growatt_OPModEner "OPModEner" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OPModEner"} | 65.,OPModEner,Modbus RTU,,5,3,605,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,OPModEner,5,605,0,2,0
| 3 | 608 | OneKeySetB | One key to set battery mode function | R/W |  |  |  |  | ALL |  |  | 0 | Type number : OneKeySetB "Growatt_OneKeySetB" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.OneKeySetB", formatBeforePublish="OneKeySetB%s"] | Number Growatt_OneKeySetB "OneKeySetB" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:OneKeySetB"} | 65.,OneKeySetB,Modbus RTU,,5,3,608,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 1,1,OneKeySetB,5,608,0,2,0
X | 3 | 608 | LoadFirstSOCmin |  | W | 0-100 |  |  |  | ALL |  |  | 0 | Type number : LoadFirstSOCmin "Growatt_LoadFirstSOCmin" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LoadFirstSOCmin", formatBeforePublish="LoadFirstSOCmin%s"] | Number Growatt_LoadFirstSOCmin "LoadFirstSOCmin" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:LoadFirstSOCmin"} |  | 2,1,LoadFirstSOCmin,5,608,0,2,0
| 3 | 609 | PowerOutputEnable | Zero Power Output |  |  |  |  | Same as Time 1 | USTimeSet |  |  | 0 | Type number : PowerOutputEnable "Growatt_PowerOutputEnable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PowerOutputEnable", formatBeforePublish="PowerOutputEnable%s"] | Number Growatt_PowerOutputEnable "PowerOutputEnable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PowerOutputEnable"} |  | 2,1,PowerOutputEnable,5,609,0,2,0
| 3 | 610 | DealDebugParaFlag | Flag bit for clearing debug variables |  |  |  |  | SPA used | SPA |  |  | 0 | Type number : DealDebugParaFlag "Growatt_DealDebugParaFlag" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.DealDebugParaFlag", formatBeforePublish="DealDebugParaFlag%s"] | Number Growatt_DealDebugParaFlag "DealDebugParaFlag" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DealDebugParaFlag"} |  | 2,1,DealDebugParaFlag,5,610,0,2,0
| 3 | 612 | bAcCoupleen | AcCoupleEn | R/W | 0-1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bAcCoupleen "Growatt_bAcCoupleen" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bAcCoupleen", formatBeforePublish="bAcCoupleen%s"] | Number Growatt_bAcCoupleen "bAcCoupleen" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bAcCoupleen"} | 66.,bAcCoupleen,Modbus RTU,,5,3,612,1,9410,2,0,Unsigned int,0,0,,1,100,97,0,0,0,1.000000,0,255 | 2,1,bAcCoupleen,5,612,0,2,0
| 3 | 660 | ReloadCmd | M3 remote command |  |  |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : ReloadCmd "Growatt_ReloadCmd" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ReloadCmd", formatBeforePublish="ReloadCmd%s"] | Number Growatt_ReloadCmd "ReloadCmd" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ReloadCmd"} |  | 2,1,ReloadCmd,5,660,0,2,0
| 3 | 1000 | Floatchargecurrentlimit | When charge current battery need is lower than this value, enter into float charge | W |  | 0.1A | 600 |  | PV9_32 | 0.1 | A | 1 | Type number : Floatchargecurrentlimit "Growatt_Floatchargecurrentlimit" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Floatchargecurrentlimit", formatBeforePublish="Floatchargecurrentlimit%s"] | Number:ElectricCurrent Growatt_Floatchargecurrentlimit "Floatchargecurrentlimit [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Floatchargecurrentlimit"} |  | 2,1,Floatchargecurrentlimit,5,1000,0,2,0
| 3 | 1001 | PFCMD | Set the following 19-22 | W | 0or1, |  | 0 |  | ALL |  |  | 0 | Type number : PFCMD "Growatt_PFCMD" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.PFCMD", formatBeforePublish="PFCMD%s"] | Number Growatt_PFCMD "PFCMD" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:PFCMD"} |  | 2,1,PFCMD,5,1001,0,2,0
| 3 | 1002 | VbatStartForDischarge | LV Vbat | R/W |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : VbatStartForDischarge "Growatt_VbatStartForDischarge" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.VbatStartForDischarge", formatBeforePublish="VbatStartForDischarge%s"] | Number:ElectricPotential Growatt_VbatStartForDischarge "VbatStartForDischarge [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:VbatStartForDischarge"} | 66.,VbatStartForDischarge,Modbus RTU,,5,3,1002,1,9410,2,0,Unsigned int,0,1,V,1,100,97,0,0,0,1.000000,0,255 | 2,1,VbatStartForDischarge,5,1002,0,2,0
| 3 | 1003 | VbatlowWa | LoadPercent(only lead-Acid): | W |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : VbatlowWa "Growatt_VbatlowWa" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.VbatlowWa", formatBeforePublish="VbatlowWa%s"] | Number:ElectricPotential Growatt_VbatlowWa "VbatlowWa [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:VbatlowWa"} |  | 2,1,VbatlowWa,5,1003,0,2,0
| 3 | 1004 | Vbatstopfordischarge | Should stop discharge when lower than this | W |  | 0.01V |  |  | ALL | 0.01 | V | 2 | Type number : Vbatstopfordischarge "Growatt_Vbatstopfordischarge" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vbatstopfordischarge", formatBeforePublish="Vbatstopfordischarge%s"] | Number:ElectricPotential Growatt_Vbatstopfordischarge "Vbatstopfordischarge [%0.01f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbatstopfordischarge"} |  | 2,1,Vbatstopfordischarge,5,1004,0,2,0
| 3 | 1005 | Vbatstop | Should stop charge when higher than this voltage | W |  | 0.01V | 5800 |  | ALL | 0.01 | V | 2 | Type number : Vbatstop "Growatt_Vbatstop" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vbatstop", formatBeforePublish="Vbatstop%s"] | Number:ElectricPotential Growatt_Vbatstop "Vbatstop [%0.01f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbatstop"} |  | 2,1,Vbatstop,5,1005,0,2,0
| 3 | 1006 | Vbatstart | Should not discharge when lower than this | W |  | 0.01V | 4800 |  | ALL | 0.01 | V | 2 | Type number : Vbatstart "Growatt_Vbatstart" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vbatstart", formatBeforePublish="Vbatstart%s"] | Number:ElectricPotential Growatt_Vbatstart "Vbatstart [%0.01f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbatstart"} |  | 2,1,Vbatstart,5,1006,0,2,0
| 3 | 1007 | Vbatconstantcharge | can charge when lower than this voltage | W |  | 0.01V | 5800 |  | ALL | 0.01 | V | 2 | Type number : Vbatconstantcharge "Growatt_Vbatconstantcharge" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vbatconstantcharge", formatBeforePublish="Vbatconstantcharge%s"] | Number:ElectricPotential Growatt_Vbatconstantcharge "Vbatconstantcharge [%0.01f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbatconstantcharge"} |  | 2,1,Vbatconstantcharge,5,1007,0,2,0
| 3 | 1008 | EESysInfoSysSetEn | Bit0:Resved; | W |  |  |  |  | BMS |  |  | 0 | Type number : EESysInfoSysSetEn "Growatt_EESysInfoSysSetEn" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.EESysInfoSysSetEn", formatBeforePublish="EESysInfoSysSetEn%s"] | Number Growatt_EESysInfoSysSetEn "EESysInfoSysSetEn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:EESysInfoSysSetEn"} |  | 2,1,EESysInfoSysSetEn,5,1008,0,2,0
| 3 | 1009 | Battemplowerlimitd | Battery temperature lower limit for discharge | W | 0-200:0-2 | 0.1? | 1170 |  | TL_X-TL_XH | 0.1 | ? | 1 | Type number : Battemplowerlimitd "Growatt_Battemplowerlimitd" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Battemplowerlimitd", formatBeforePublish="Battemplowerlimitd%s"] | Number:Length Growatt_Battemplowerlimitd "Battemplowerlimitd [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Battemplowerlimitd"} |  | 2,1,Battemplowerlimitd,5,1009,0,2,0
| 3 | 1010 | Battempupperlimitd | Battery temperature upper limit for discharge | W | 200-1000 | 0.1? | 420 |  | TL_X-TL_XH | 0.1 | ? | 1 | Type number : Battempupperlimitd "Growatt_Battempupperlimitd" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Battempupperlimitd", formatBeforePublish="Battempupperlimitd%s"] | Number:Length Growatt_Battempupperlimitd "Battempupperlimitd [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Battempupperlimitd"} |  | 2,1,Battempupperlimitd,5,1010,0,2,0
| 3 | 1011 | Battemplowerlimitc | Battery temperature lower limit for charge | W | 0-200:0-2 | 0.1? | 30 |  | TL_X-TL_XH | 0.1 | ? | 1 | Type number : Battemplowerlimitc "Growatt_Battemplowerlimitc" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Battemplowerlimitc", formatBeforePublish="Battemplowerlimitc%s"] | Number:Length Growatt_Battemplowerlimitc "Battemplowerlimitc [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Battemplowerlimitc"} |  | 2,1,Battemplowerlimitc,5,1011,0,2,0
| 3 | 1012 | Battempupperlimitc | Battery temperature upper limit for charge | W | 200-1000 | 0.1? | 370 |  | TL_X-TL_XH | 0.1 | ? | 1 | Type number : Battempupperlimitc "Growatt_Battempupperlimitc" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Battempupperlimitc", formatBeforePublish="Battempupperlimitc%s"] | Number:Length Growatt_Battempupperlimitc "Battempupperlimitc [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Battempupperlimitc"} |  | 2,1,Battempupperlimitc,5,1012,0,2,0
| 3 | 1013 | uwUnderFreDischargeDelyTime | Under Fre Delay Time |  | 0-20 | 50ms |  |  | ALL | 50 | ms | 1 | Type number : uwUnderFreDischargeDelyTime "Growatt_uwUnderFreDischargeDelyTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUnderFreDischargeDelyTime", formatBeforePublish="uwUnderFreDischargeDelyTime%s"] | #N/A |  | 2,1,uwUnderFreDischargeDelyTime,5,1013,0,2,0
| 3 | 1014 | BatMdlSerialNum | Battery serial number | W | 0 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatMdlSerialNum "Growatt_BatMdlSerialNum" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatMdlSerialNum", formatBeforePublish="BatMdlSerialNum%s"] | Number Growatt_BatMdlSerialNum "BatMdlSerialNum" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatMdlSerialNum"} |  | 2,1,BatMdlSerialNum,5,1014,0,2,0
| 3 | 1015 | BatMdlParallNum | Battery parallel section | W | 0 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatMdlParallNum "Growatt_BatMdlParallNum" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatMdlParallNum", formatBeforePublish="BatMdlParallNum%s"] | Number Growatt_BatMdlParallNum "BatMdlParallNum" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatMdlParallNum"} |  | 2,1,BatMdlParallNum,5,1015,0,2,0
| 3 | 1016 | DRMS_EN | [5 empty] | SPA | SPA |  |  | 0 | Type number : DRMS_EN "Growatt_DRMS_EN" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.DRMS_EN", formatBeforePublish="DRMS_EN%s"] | Number Growatt_DRMS_EN "DRMS_EN" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DRMS_EN"} |  | 2,1,DRMS_EN,5,1016,0,2,0
| 3 | 1017 | BatFirstStartTime4 | High eight:hours | W | 0-23 | h |  |  | TL_X-TL_XH |  | h | 0 | Type number : BatFirstStartTime4 "Growatt_BatFirstStartTime4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStartTime4", formatBeforePublish="BatFirstStartTime4%s"] | #N/A |  | 2,1,BatFirstStartTime4,5,1017,0,2,0
| 3 | 1018 | BatFirstStopTime4 | High eight:hours | W | 0-23 | h |  |  | TL_X-TL_XH |  | h | 0 | Type number : BatFirstStopTime4 "Growatt_BatFirstStopTime4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStopTime4", formatBeforePublish="BatFirstStopTime4%s"] | #N/A |  | 2,1,BatFirstStopTime4,5,1018,0,2,0
| 3 | 1019 | BatFirston_offSwitch4 | Enable:1 | W | 0 or 1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatFirston_offSwitch4 "Growatt_BatFirston_offSwitch4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirston_offSwitch4", formatBeforePublish="BatFirston_offSwitch4%s"] | Number Growatt_BatFirston_offSwitch4 "BatFirston_offSwitch4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatFirston_offSwitch4"} |  | 2,1,BatFirston_offSwitch4,5,1019,0,2,0
| 3 | 1020 | BatFirstStartTime5 | High eight:hours | W | 0-23 | h |  |  | TL_X-TL_XH |  | h | 0 | Type number : BatFirstStartTime5 "Growatt_BatFirstStartTime5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStartTime5", formatBeforePublish="BatFirstStartTime5%s"] | #N/A |  | 2,1,BatFirstStartTime5,5,1020,0,2,0
| 3 | 1021 | BatFirstStopTime5 | High eight:hours | W | 0-23 | h |  |  | TL_X-TL_XH |  | h | 0 | Type number : BatFirstStopTime5 "Growatt_BatFirstStopTime5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStopTime5", formatBeforePublish="BatFirstStopTime5%s"] | #N/A |  | 2,1,BatFirstStopTime5,5,1021,0,2,0
| 3 | 1022 | BatFirston_offSwitch5 | Enable:1 | W | 0 or 1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatFirston_offSwitch5 "Growatt_BatFirston_offSwitch5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirston_offSwitch5", formatBeforePublish="BatFirston_offSwitch5%s"] | Number Growatt_BatFirston_offSwitch5 "BatFirston_offSwitch5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatFirston_offSwitch5"} |  | 2,1,BatFirston_offSwitch5,5,1022,0,2,0
| 3 | 1023 | BatFirstStartTime6 | High eight:hours | W | 0-23 | h |  |  | TL_X-TL_XH |  | h | 0 | Type number : BatFirstStartTime6 "Growatt_BatFirstStartTime6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStartTime6", formatBeforePublish="BatFirstStartTime6%s"] | #N/A |  | 2,1,BatFirstStartTime6,5,1023,0,2,0
| 3 | 1024 | BatFirstStopTime6 | High eight:hours | W | 0-23 | h |  |  | TL_X-TL_XH |  | h | 0 | Type number : BatFirstStopTime6 "Growatt_BatFirstStopTime6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStopTime6", formatBeforePublish="BatFirstStopTime6%s"] | #N/A |  | 2,1,BatFirstStopTime6,5,1024,0,2,0
| 3 | 1025 | BatFirston_offSwitch6 | Enable:1 | W | 0 or 1 |  |  | [0,650.00] | TL_X-TL_XH |  |  | 0 | Type number : BatFirston_offSwitch6 "Growatt_BatFirston_offSwitch6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirston_offSwitch6", formatBeforePublish="BatFirston_offSwitch6%s"] | Number Growatt_BatFirston_offSwitch6 "BatFirston_offSwitch6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatFirston_offSwitch6"} |  | 2,1,BatFirston_offSwitch6,5,1025,0,2,0
| 3 | 1026 | GridFirstStartTime4 | High eight:hours | W | 0-23 | h |  |  | ALL |  | h | 0 | Type number : GridFirstStartTime4 "Growatt_GridFirstStartTime4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStartTime4", formatBeforePublish="GridFirstStartTime4%s"] | #N/A |  | 2,1,GridFirstStartTime4,5,1026,0,2,0
| 3 | 1027 | GridFirstStopTime4 | High eight:hours | W | 0-23 | h |  |  | ALL |  | h | 0 | Type number : GridFirstStopTime4 "Growatt_GridFirstStopTime4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopTime4", formatBeforePublish="GridFirstStopTime4%s"] | #N/A |  | 2,1,GridFirstStopTime4,5,1027,0,2,0
| 3 | 1028 | GridFirstStopSwitch4 | Enable:1 | W | 0 or 1 |  |  |  | ALL |  |  | 0 | Type number : GridFirstStopSwitch4 "Growatt_GridFirstStopSwitch4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopSwitch4", formatBeforePublish="GridFirstStopSwitch4%s"] | Number Growatt_GridFirstStopSwitch4 "GridFirstStopSwitch4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstStopSwitch4"} |  | 2,1,GridFirstStopSwitch4,5,1028,0,2,0
| 3 | 1029 | GridFirstStartTime5 | High eight:hours | W | 0-23 | h |  |  | ALL |  | h | 0 | Type number : GridFirstStartTime5 "Growatt_GridFirstStartTime5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStartTime5", formatBeforePublish="GridFirstStartTime5%s"] | #N/A |  | 2,1,GridFirstStartTime5,5,1029,0,2,0
| 3 | 1030 | GridFirstStopTime5 | High eight:hours | W | 0-23 | h |  |  | ALL |  | h | 0 | Type number : GridFirstStopTime5 "Growatt_GridFirstStopTime5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopTime5", formatBeforePublish="GridFirstStopTime5%s"] | #N/A |  | 2,1,GridFirstStopTime5,5,1030,0,2,0
| 3 | 1031 | GridFirstStopSwitch5 | Enable:1 | W | 0 or 1 |  |  |  | ALL |  |  | 0 | Type number : GridFirstStopSwitch5 "Growatt_GridFirstStopSwitch5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopSwitch5", formatBeforePublish="GridFirstStopSwitch5%s"] | Number Growatt_GridFirstStopSwitch5 "GridFirstStopSwitch5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstStopSwitch5"} |  | 2,1,GridFirstStopSwitch5,5,1031,0,2,0
| 3 | 1032 | GridFirstStartTime6 | High eight:hours | W | 0-23 | h |  |  | ALL |  | h | 0 | Type number : GridFirstStartTime6 "Growatt_GridFirstStartTime6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStartTime6", formatBeforePublish="GridFirstStartTime6%s"] | #N/A |  | 2,1,GridFirstStartTime6,5,1032,0,2,0
| 3 | 1033 | GridFirstStopTime6 | High eight:hours | W | 0-23 | h |  |  | ALL |  | h | 0 | Type number : GridFirstStopTime6 "Growatt_GridFirstStopTime6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopTime6", formatBeforePublish="GridFirstStopTime6%s"] | #N/A |  | 2,1,GridFirstStopTime6,5,1033,0,2,0
| 3 | 1034 | GridFirstStopSwitch6 | Enable:1 | W | 0 or 1 |  |  |  | ALL |  |  | 0 | Type number : GridFirstStopSwitch6 "Growatt_GridFirstStopSwitch6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopSwitch6", formatBeforePublish="GridFirstStopSwitch6%s"] | Number Growatt_GridFirstStopSwitch6 "GridFirstStopSwitch6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstStopSwitch6"} |  | 2,1,GridFirstStopSwitch6,5,1034,0,2,0
| 3 | 1035 | BatFirstStartTime | High eight:hours | W | 0-23 | h |  |  | TL_X-TL_XH |  | h | 0 | Type number : BatFirstStartTime "Growatt_BatFirstStartTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStartTime", formatBeforePublish="BatFirstStartTime%s"] | #N/A |  | 2,1,BatFirstStartTime,5,1035,0,2,0
| 3 | 1037 | bCTMode | Use the CTMode to | W | 2:METER 1:cWirele ssCT |  | 0 |  | TL_X-TL_XH |  |  | 0 | Type number : bCTMode "Growatt_bCTMode" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bCTMode", formatBeforePublish="bCTMode%s"] | Number Growatt_bCTMode "bCTMode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bCTMode"} |  | 2,1,bCTMode,5,1037,0,2,0
| 3 | 1038 | CTAdjust | CTAdjust enable | W | 0:disable |  | 0 | Three/single | TL_X-TL_XH |  |  | 0 | Type number : CTAdjust "Growatt_CTAdjust" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.CTAdjust", formatBeforePublish="CTAdjust%s"] | Number Growatt_CTAdjust "CTAdjust" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:CTAdjust"} |  | 2,1,CTAdjust,5,1038,0,2,0
| 3 | 1044 | Priority | ForceChrEn/ForceDischr | R |  |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : Priority "Growatt_Priority" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Priority", formatBeforePublish="Priority%s"] | Number Growatt_Priority "Priority" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Priority"} |  | 2,1,Priority,5,1044,0,2,0
| 3 | 1047 | AgingTestStepCmd | Command for aging test |  |  |  | 0: default |  | TL_X-TL_XH |  |  | 0 | Type number : AgingTestStepCmd "Growatt_AgingTestStepCmd" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.AgingTestStepCmd", formatBeforePublish="AgingTestStepCmd%s"] | Number Growatt_AgingTestStepCmd "AgingTestStepCmd" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AgingTestStepCmd"} |  | 2,1,AgingTestStepCmd,5,1047,0,2,0
| 3 | 1048 | BatteryType | Battery type choose of buck-boost input |  |  |  | 0:Lithium 1:Lead-aci d |  | TL_X-TL_XH |  |  | 0 | Type number : BatteryType "Growatt_BatteryType" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatteryType", formatBeforePublish="BatteryType%s"] | Number Growatt_BatteryType "BatteryType" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatteryType"} |  | 2,1,BatteryType,5,1048,0,2,0
| 3 | 1060 | BuckUpsFunen | Ups function enable |  | 0:disable |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BuckUpsFunen "Growatt_BuckUpsFunen" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BuckUpsFunen", formatBeforePublish="BuckUpsFunen%s"] | Number Growatt_BuckUpsFunen "BuckUpsFunen" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BuckUpsFunen"} |  | 2,1,BuckUpsFunen,5,1060,0,2,0
| 3 | 1061 | BuckUPSVoltSet | UPS output voltage |  | 0,159722222222222 |  | 230V |  | TL_X-TL_XH |  |  | 0 | Type number : BuckUPSVoltSet "Growatt_BuckUPSVoltSet" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BuckUPSVoltSet", formatBeforePublish="BuckUPSVoltSet%s"] | Number Growatt_BuckUPSVoltSet "BuckUPSVoltSet" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BuckUPSVoltSet"} |  | 2,1,BuckUPSVoltSet,5,1061,0,2,0
| 3 | 1062 | UPSFreqSet | UPS output frequency |  | 0:50Hz |  | 50Hz | ASCII | ALL |  |  | 0 | Type number : UPSFreqSet "Growatt_UPSFreqSet" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.UPSFreqSet", formatBeforePublish="UPSFreqSet%s"] | Number Growatt_UPSFreqSet "UPSFreqSet" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:UPSFreqSet"} |  | 2,1,UPSFreqSet,5,1062,0,2,0
X | 3 | 1070 | GridFirstDischargePowerRate | Discharge Power Rate | W | 0-100 |  |  |  | ALL |  |  | 0 | Type number : GridFirstDischargePowerRate "Growatt_GridFirstDischargePowerRate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstDischargePowerRate", formatBeforePublish="GridFirstDischargePowerRate%s"] | Number Growatt_GridFirstDischargePowerRate "GridFirstDischargePowerRate" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstDischargePowerRate"} |  | 3,1,GridFirstDischargePowerRate,5,1070,0,2,0
X | 3 | 1071 | GridFirstStopSOC | Stop Discharge soc when | W | 0-100 |  |  |  | ALL |  |  | 0 | Type number : GridFirstStopSOC "Growatt_GridFirstStopSOC" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopSOC", formatBeforePublish="GridFirstStopSOC%s"] | Number Growatt_GridFirstStopSOC "GridFirstStopSOC" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstStopSOC"} |  | 4,1,GridFirstStopSOC,5,1071,0,2,0
X | 3 | 1080 | GridFirstStartTime1 | High eight bit:hour | W | 0-23 |  |  |  | ALL |  |  | 0 | Type number : GridFirstStartTime1 "Growatt_GridFirstStartTime1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStartTime1", formatBeforePublish="GridFirstStartTime1%s"] | Number Growatt_GridFirstStartTime1 "GridFirstStartTime1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstStartTime1"} |  | 5,1,GridFirstStartTime1,5,1080,0,2,0
X | 3 | 1081 | GridFirstStopTime1 | High eight bit:hour | W | 0-23 |  |  |  | ALL |  |  | 0 | Type number : GridFirstStopTime1 "Growatt_GridFirstStopTime1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopTime1", formatBeforePublish="GridFirstStopTime1%s"] | Number Growatt_GridFirstStopTime1 "GridFirstStopTime1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstStopTime1"} |  | 6,1,GridFirstStopTime1,5,1081,0,2,0
X | 3 | 1082 | GridFirstStopSwitch1 | Enable :1 | W | 0 or 1 |  |  |  | ALL |  |  | 0 | Type number : GridFirstStopSwitch1 "Growatt_GridFirstStopSwitch1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopSwitch1", formatBeforePublish="GridFirstStopSwitch1%s"] | Number Growatt_GridFirstStopSwitch1 "GridFirstStopSwitch1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstStopSwitch1"} |  | 7,1,GridFirstStopSwitch1,5,1082,0,2,0
| 3 | 1083 | GridFirstStartTime2 | High eight bit:hour |  | 0-23 | h |  |  | ALL |  | h | 0 | Type number : GridFirstStartTime2 "Growatt_GridFirstStartTime2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStartTime2", formatBeforePublish="GridFirstStartTime2%s"] | #N/A |  | 7,1,GridFirstStartTime2,5,1083,0,2,0
| 3 | 1084 | GridFirstStopTime2 | High eight bit:hour |  | 0-23 | h |  |  | ALL |  | h | 0 | Type number : GridFirstStopTime2 "Growatt_GridFirstStopTime2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopTime2", formatBeforePublish="GridFirstStopTime2%s"] | #N/A |  | 7,1,GridFirstStopTime2,5,1084,0,2,0
| 3 | 1085 | GridFirstStopSwitch2 | ForceDischarge.bSwitch&L |  | 0 or 1 |  |  |  | ALL |  |  | 0 | Type number : GridFirstStopSwitch2 "Growatt_GridFirstStopSwitch2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopSwitch2", formatBeforePublish="GridFirstStopSwitch2%s"] | Number Growatt_GridFirstStopSwitch2 "GridFirstStopSwitch2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstStopSwitch2"} |  | 7,1,GridFirstStopSwitch2,5,1085,0,2,0
| 3 | 1086 | GridFirstStartTime3 | High eight bit:hour |  | 0-23 | h |  |  | ALL |  | h | 0 | Type number : GridFirstStartTime3 "Growatt_GridFirstStartTime3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStartTime3", formatBeforePublish="GridFirstStartTime3%s"] | #N/A |  | 7,1,GridFirstStartTime3,5,1086,0,2,0
| 3 | 1087 | GridFirstStopTime3 | High eight bit:hour |  | 0-23 | h |  |  | ALL |  | h | 0 | Type number : GridFirstStopTime3 "Growatt_GridFirstStopTime3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopTime3", formatBeforePublish="GridFirstStopTime3%s"] | #N/A |  | 7,1,GridFirstStopTime3,5,1087,0,2,0
| 3 | 1088 | GridFirstStopSwitch3 | Enable :1 |  | 0 or 1 |  |  |  | ALL |  |  | 0 | Type number : GridFirstStopSwitch3 "Growatt_GridFirstStopSwitch3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopSwitch3", formatBeforePublish="GridFirstStopSwitch3%s"] | Number Growatt_GridFirstStopSwitch3 "GridFirstStopSwitch3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstStopSwitch3"} |  | 7,1,GridFirstStopSwitch3,5,1088,0,2,0
X | 3 | 1090 | BatFirstPowerRate | Charge Power Rate when | W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatFirstPowerRate "Growatt_BatFirstPowerRate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstPowerRate", formatBeforePublish="BatFirstPowerRate%s"] | Number Growatt_BatFirstPowerRate "BatFirstPowerRate" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatFirstPowerRate"} |  | 8,1,BatFirstPowerRate,5,1090,0,2,0
X | 3 | 1091 | wBatFirststopSOC | Stop Charge soc when Bat | W | 0-100 |  |  | ASCII | ALL |  |  | 0 | Type number : wBatFirststopSOC "Growatt_wBatFirststopSOC" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.wBatFirststopSOC", formatBeforePublish="wBatFirststopSOC%s"] | Number Growatt_wBatFirststopSOC "wBatFirststopSOC" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:wBatFirststopSOC"} |  | 9,1,wBatFirststopSOC,5,1091,0,2,0
X | 3 | 1092 | ACchargeSwitch | When Bat First | W | Enable:1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : ACchargeSwitch "Growatt_ACchargeSwitch" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ACchargeSwitch", formatBeforePublish="ACchargeSwitch%s"] | Number Growatt_ACchargeSwitch "ACchargeSwitch" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ACchargeSwitch"} |  | 10,1,ACchargeSwitch,5,1092,0,2,0
X | 3 | 1100 | BatFirstStartTime1 | High eight bit:hour | W | 0-23 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatFirstStartTime1 "Growatt_BatFirstStartTime1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStartTime1", formatBeforePublish="BatFirstStartTime1%s"] | Number Growatt_BatFirstStartTime1 "BatFirstStartTime1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatFirstStartTime1"} |  | 11,1,BatFirstStartTime1,5,1100,0,2,0
X | 3 | 1101 | BatFirstStopTime1 | High eight bit:hour | W | 0-23 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatFirstStopTime1 "Growatt_BatFirstStopTime1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStopTime1", formatBeforePublish="BatFirstStopTime1%s"] | Number Growatt_BatFirstStopTime1 "BatFirstStopTime1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatFirstStopTime1"} |  | 12,1,BatFirstStopTime1,5,1101,0,2,0
X | 3 | 1102 | BatFirston_offSwitch1 | Enable :1 | W | 0 or 1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatFirston_offSwitch1 "Growatt_BatFirston_offSwitch1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirston_offSwitch1", formatBeforePublish="BatFirston_offSwitch1%s"] | Number Growatt_BatFirston_offSwitch1 "BatFirston_offSwitch1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatFirston_offSwitch1"} |  | 13,1,BatFirston_offSwitch1,5,1102,0,2,0
| 3 | 1103 | BatFirstStartTime2 | High eight bit:hour |  | 0-23 | h |  |  | TL_X-TL_XH |  | h | 0 | Type number : BatFirstStartTime2 "Growatt_BatFirstStartTime2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStartTime2", formatBeforePublish="BatFirstStartTime2%s"] | #N/A |  | 13,1,BatFirstStartTime2,5,1103,0,2,0
| 3 | 1104 | BatFirstStopTime2 | High eight bit:hour |  | 0-23 | h |  |  | TL_X-TL_XH |  | h | 0 | Type number : BatFirstStopTime2 "Growatt_BatFirstStopTime2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStopTime2", formatBeforePublish="BatFirstStopTime2%s"] | #N/A |  | 13,1,BatFirstStopTime2,5,1104,0,2,0
| 3 | 1105 | BatFirston_offSwitch2 | Enable :1 |  | 0 or 1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatFirston_offSwitch2 "Growatt_BatFirston_offSwitch2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirston_offSwitch2", formatBeforePublish="BatFirston_offSwitch2%s"] | Number Growatt_BatFirston_offSwitch2 "BatFirston_offSwitch2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatFirston_offSwitch2"} |  | 13,1,BatFirston_offSwitch2,5,1105,0,2,0
| 3 | 1106 | BatFirstStartTime3 | High eight bit:hour |  | 0-23 | h |  |  | TL_X-TL_XH |  | h | 0 | Type number : BatFirstStartTime3 "Growatt_BatFirstStartTime3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStartTime3", formatBeforePublish="BatFirstStartTime3%s"] | #N/A |  | 13,1,BatFirstStartTime3,5,1106,0,2,0
| 3 | 1107 | BatFirstStopTime3 | High eight bit:hour |  | 0-23 | h |  |  | TL_X-TL_XH |  | h | 0 | Type number : BatFirstStopTime3 "Growatt_BatFirstStopTime3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstStopTime3", formatBeforePublish="BatFirstStopTime3%s"] | #N/A |  | 13,1,BatFirstStopTime3,5,1107,0,2,0
| 3 | 1108 | BatFirston_offSwitch3 | Enable :1 |  | 0 or 1 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatFirston_offSwitch3 "Growatt_BatFirston_offSwitch3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirston_offSwitch3", formatBeforePublish="BatFirston_offSwitch3%s"] | Number Growatt_BatFirston_offSwitch3 "BatFirston_offSwitch3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatFirston_offSwitch3"} |  | 13,1,BatFirston_offSwitch3,5,1108,0,2,0
X | 3 | 1110 | LoadFirstStartTime1 | High eight bit:hour | W | 0-23 |  |  |  | ALL |  |  | 0 | Type number : LoadFirstStartTime1 "Growatt_LoadFirstStartTime1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LoadFirstStartTime1", formatBeforePublish="LoadFirstStartTime1%s"] | Number Growatt_LoadFirstStartTime1 "LoadFirstStartTime1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:LoadFirstStartTime1"} |  | 14,1,LoadFirstStartTime1,5,1110,0,2,0
X | 3 | 1111 | LoadFirstStopTime1 | High eight bit:hour | W | 0-23 |  |  |  | ALL |  |  | 0 | Type number : LoadFirstStopTime1 "Growatt_LoadFirstStopTime1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LoadFirstStopTime1", formatBeforePublish="LoadFirstStopTime1%s"] | Number Growatt_LoadFirstStopTime1 "LoadFirstStopTime1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:LoadFirstStopTime1"} |  | 15,1,LoadFirstStopTime1,5,1111,0,2,0
X | 3 | 1112 | LoadFirstSwitch1 | Enable :1 | W | 0 or 1 |  |  |  | ALL |  |  | 0 | Type number : LoadFirstSwitch1 "Growatt_LoadFirstSwitch1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LoadFirstSwitch1", formatBeforePublish="LoadFirstSwitch1%s"] | Number Growatt_LoadFirstSwitch1 "LoadFirstSwitch1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:LoadFirstSwitch1"} |  | 16,1,LoadFirstSwitch1,5,1112,0,2,0
| 3 | 1113 | LoadFirstStartTime2 | High eight bit:hour |  | 0-23 | h |  |  | ALL |  | h | 0 | Type number : LoadFirstStartTime2 "Growatt_LoadFirstStartTime2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LoadFirstStartTime2", formatBeforePublish="LoadFirstStartTime2%s"] | #N/A |  | 16,1,LoadFirstStartTime2,5,1113,0,2,0
| 3 | 1114 | LoadFirstStopTime2 | High eight bit:hour |  | 0-23 | h |  |  | ALL |  | h | 0 | Type number : LoadFirstStopTime2 "Growatt_LoadFirstStopTime2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LoadFirstStopTime2", formatBeforePublish="LoadFirstStopTime2%s"] | #N/A |  | 16,1,LoadFirstStopTime2,5,1114,0,2,0
| 3 | 1115 | LoadFirstSwitch2 | Enable :1 |  | 0 or 1 |  |  |  | ALL |  |  | 0 | Type number : LoadFirstSwitch2 "Growatt_LoadFirstSwitch2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LoadFirstSwitch2", formatBeforePublish="LoadFirstSwitch2%s"] | Number Growatt_LoadFirstSwitch2 "LoadFirstSwitch2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:LoadFirstSwitch2"} |  | 16,1,LoadFirstSwitch2,5,1115,0,2,0
| 3 | 1116 | LoadFirstStartTime3 | High eight bit:hour |  | 0-23 | h |  |  | ALL |  | h | 0 | Type number : LoadFirstStartTime3 "Growatt_LoadFirstStartTime3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LoadFirstStartTime3", formatBeforePublish="LoadFirstStartTime3%s"] | #N/A |  | 16,1,LoadFirstStartTime3,5,1116,0,2,0
| 3 | 1117 | LoadFirstStopTime3 | High eight bit:hour |  | 0-23 | h |  |  | ALL |  | h | 0 | Type number : LoadFirstStopTime3 "Growatt_LoadFirstStopTime3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LoadFirstStopTime3", formatBeforePublish="LoadFirstStopTime3%s"] | #N/A |  | 16,1,LoadFirstStopTime3,5,1117,0,2,0
| 3 | 1118 | LoadFirstSwitch3 | Enable :1 |  | 0 or 1 |  |  |  | ALL |  |  | 0 | Type number : LoadFirstSwitch3 "Growatt_LoadFirstSwitch3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.LoadFirstSwitch3", formatBeforePublish="LoadFirstSwitch3%s"] | Number Growatt_LoadFirstSwitch3 "LoadFirstSwitch3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:LoadFirstSwitch3"} |  | 16,1,LoadFirstSwitch3,5,1118,0,2,0
| 3 | 1119 | NewEPowerCalcFlag | [6 empty] | ALL |  |  | 0 | Type number : NewEPowerCalcFlag "Growatt_NewEPowerCalcFlag" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewEPowerCalcFlag", formatBeforePublish="NewEPowerCalcFlag%s"] | Number Growatt_NewEPowerCalcFlag "NewEPowerCalcFlag" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewEPowerCalcFlag"} |  | 16,1,NewEPowerCalcFlag,5,1119,0,2,0
| 3 | 1120 | BackUpEn | BackUp Enable | R/W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BackUpEn "Growatt_BackUpEn" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BackUpEn", formatBeforePublish="BackUpEn%s"] | Number Growatt_BackUpEn "BackUpEn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BackUpEn"} |  | 16,1,BackUpEn,5,1120,0,2,0
| 3 | 1121 | SGIPEn | SGIP Enable | [5 empty] | Storage |  |  | 0 | Type number : SGIPEn "Growatt_SGIPEn" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SGIPEn", formatBeforePublish="SGIPEn%s"] | Number Growatt_SGIPEn "SGIPEn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SGIPEn"} |  | 16,1,SGIPEn,5,1121,0,2,0
| 3 | 1125 | BatSerialNO | Product serial number of the first PACK of energy | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNO "Growatt_BatSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatSerialNO", formatBeforePublish="BatSerialNO%s"] | Number Growatt_BatSerialNO "BatSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNO"} |  | 16,1,BatSerialNO,5,1125,0,2,0
| 3 | 1126 | BatSerialNO7 | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNO7 "Growatt_BatSerialNO7" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatSerialNO7", formatBeforePublish="BatSerialNO7%s"] | Number Growatt_BatSerialNO7 "BatSerialNO7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNO7"} |  | 16,1,BatSerialNO7,5,1126,0,2,0
| 3 | 1127 | BatSerialNO6 | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNO6 "Growatt_BatSerialNO6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatSerialNO6", formatBeforePublish="BatSerialNO6%s"] | Number Growatt_BatSerialNO6 "BatSerialNO6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNO6"} |  | 16,1,BatSerialNO6,5,1127,0,2,0
| 3 | 1128 | BatSerialNO5 | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNO5 "Growatt_BatSerialNO5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatSerialNO5", formatBeforePublish="BatSerialNO5%s"] | Number Growatt_BatSerialNO5 "BatSerialNO5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNO5"} |  | 16,1,BatSerialNO5,5,1128,0,2,0
| 3 | 1129 | BatSerialNO4 | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNO4 "Growatt_BatSerialNO4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatSerialNO4", formatBeforePublish="BatSerialNO4%s"] | Number Growatt_BatSerialNO4 "BatSerialNO4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNO4"} |  | 16,1,BatSerialNO4,5,1129,0,2,0
| 3 | 1130 | BatSerialNO3 | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNO3 "Growatt_BatSerialNO3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatSerialNO3", formatBeforePublish="BatSerialNO3%s"] | Number Growatt_BatSerialNO3 "BatSerialNO3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNO3"} |  | 16,1,BatSerialNO3,5,1130,0,2,0
| 3 | 1131 | BatSerialNO2 | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNO2 "Growatt_BatSerialNO2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatSerialNO2", formatBeforePublish="BatSerialNO2%s"] | Number Growatt_BatSerialNO2 "BatSerialNO2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNO2"} |  | 16,1,BatSerialNO2,5,1131,0,2,0
| 3 | 1132 | BatSerialNO1 | [6 empty] | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNO1 "Growatt_BatSerialNO1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatSerialNO1", formatBeforePublish="BatSerialNO1%s"] | Number Growatt_BatSerialNO1 "BatSerialNO1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNO1"} |  | 16,1,BatSerialNO1,5,1132,0,2,0
| 3 | 1132 | BatSerialNO | The serial number of the second to tenth packs of the energy storage battery consists of nine packs, and | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BatSerialNO "Growatt_BatSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatSerialNO", formatBeforePublish="BatSerialNO%s"] | Number Growatt_BatSerialNO "BatSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatSerialNO"} |  | 16,1,BatSerialNO,5,1132,0,2,0
| 3 | 1244 | ComversionNameH | Name of the battery main control firmware version | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : ComversionNameH "Growatt_ComversionNameH" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ComversionNameH", formatBeforePublish="ComversionNameH%s"] | Number Growatt_ComversionNameH "ComversionNameH" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ComversionNameH"} |  | 16,1,ComversionNameH,5,1244,0,2,0
| 3 | 1245 | ComversionNameL | Name of the battery main control firmware version | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : ComversionNameL "Growatt_ComversionNameL" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ComversionNameL", formatBeforePublish="ComversionNameL%s"] | Number Growatt_ComversionNameL "ComversionNameL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ComversionNameL"} |  | 16,1,ComversionNameL,5,1245,0,2,0
| 3 | 1246 | ComversionNo | Version of the battery main control firmware | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : ComversionNo "Growatt_ComversionNo" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ComversionNo", formatBeforePublish="ComversionNo%s"] | Number Growatt_ComversionNo "ComversionNo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ComversionNo"} |  | 16,1,ComversionNo,5,1246,0,2,0
| 3 | 1247 | ComversionNameH | Name of battery monitoring firmware |  |  |  |  | Total reverse power | TL_X-TL_XH |  |  | 0 | Type number : ComversionNameH "Growatt_ComversionNameH" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ComversionNameH", formatBeforePublish="ComversionNameH%s"] | Number Growatt_ComversionNameH "ComversionNameH" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ComversionNameH"} |  | 16,1,ComversionNameH,5,1247,0,2,0
| 3 | 1248 | ComversionNameL | Name of battery monitoring firmware |  |  |  |  | Total forward power | TL_X-TL_XH |  |  | 0 | Type number : ComversionNameL "Growatt_ComversionNameL" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ComversionNameL", formatBeforePublish="ComversionNameL%s"] | Number Growatt_ComversionNameL "ComversionNameL" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ComversionNameL"} |  | 16,1,ComversionNameL,5,1248,0,2,0
| 3 | 1249 | ComversionNo | Battery monitoring | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : ComversionNo "Growatt_ComversionNo" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ComversionNo", formatBeforePublish="ComversionNo%s"] | Number Growatt_ComversionNo "ComversionNo" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ComversionNo"} |  | 16,1,ComversionNo,5,1249,0,2,0
| 3 | 3000 | ExportLimitFailedPowerRate | The power rate when | R/W |  | 0.001 |  |  | PV9_32 | 0.001 |  | 3 | Type number : ExportLimitFailedPowerRate "Growatt_ExportLimitFailedPowerRate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ExportLimitFailedPowerRate", formatBeforePublish="ExportLimitFailedPowerRate%s"] | Number Growatt_ExportLimitFailedPowerRate "ExportLimitFailedPowerRate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ExportLimitFailedPowerRate"} |  | 16,1,ExportLimitFailedPowerRate,5,3000,0,2,0
| 3 | 3001 | NewSerialNO | Serial number 1-2 | R/W |  |  |  | Storage | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3001,0,2,0
| 3 | 3002 | NewSerialNO | Serial number 3-4 | R/W |  |  |  | Storage | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3002,0,2,0
| 3 | 3003 | NewSerialNO | Serial number 5-6 | R/W |  |  |  | Storage | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3003,0,2,0
| 3 | 3004 | NewSerialNO | Serial number 7-8 | R/W |  |  |  | Storage | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3004,0,2,0
| 3 | 3005 | NewSerialNO | Serial number 9-10 | R/W |  |  |  | off | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3005,0,2,0
| 3 | 3006 | NewSerialNO | Serial number 11-12 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3006,0,2,0
| 3 | 3007 | NewSerialNO | Serial number 13-14 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3007,0,2,0
| 3 | 3008 | NewSerialNO | Serial number 15-16 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3008,0,2,0
| 3 | 3009 | NewSerialNO | Serial number 17-18 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3009,0,2,0
| 3 | 3010 | NewSerialNO | Serial number 19-20 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3010,0,2,0
| 3 | 3011 | NewSerialNO | Serial number 21-22 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3011,0,2,0
| 3 | 3012 | NewSerialNO | Serial number 23-24 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3012,0,2,0
| 3 | 3013 | NewSerialNO | Serial number 25-26 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3013,0,2,0
| 3 | 3014 | NewSerialNO | Serial number 27-28 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3014,0,2,0
| 3 | 3015 | NewSerialNO | Serial number 29-30 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : NewSerialNO "Growatt_NewSerialNO" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.NewSerialNO", formatBeforePublish="NewSerialNO%s"] | Number Growatt_NewSerialNO "NewSerialNO" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:NewSerialNO"} |  | 16,1,NewSerialNO,5,3015,0,2,0
| 3 | 3016 | DryContactFuncEn | DryContact function enable | R/W | 0:Disable |  |  | SPA | SPA |  |  | 0 | Type number : DryContactFuncEn "Growatt_DryContactFuncEn" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.DryContactFuncEn", formatBeforePublish="DryContactFuncEn%s"] | Number Growatt_DryContactFuncEn "DryContactFuncEn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DryContactFuncEn"} |  | 16,1,DryContactFuncEn,5,3016,0,2,0
| 3 | 3017 | DryContactOn | The power rate of | R/W | 0~1000 | 0.001 |  | SPA | SPA | 0.001 |  | 3 | Type number : DryContactOn "Growatt_DryContactOn" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.DryContactOn", formatBeforePublish="DryContactOn%s"] | Number Growatt_DryContactOn "DryContactOn [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DryContactOn"} |  | 16,1,DryContactOn,5,3017,0,2,0
| 3 | 3018 | bWorkMode | WorkMode----0:default,1: | R/W | 0?1?2 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bWorkMode "Growatt_bWorkMode" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bWorkMode", formatBeforePublish="bWorkMode%s"] | Number Growatt_bWorkMode "bWorkMode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bWorkMode"} |  | 16,1,bWorkMode,5,3018,0,2,0
| 3 | 3019 | DryContactOffRate | Dry contact closure power | R/W | 0~100 | 0.001 |  | SPA | SPA | 0.001 |  | 3 | Type number : DryContactOffRate "Growatt_DryContactOffRate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.DryContactOffRate", formatBeforePublish="DryContactOffRate%s"] | Number Growatt_DryContactOffRate "DryContactOffRate [%0.001f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DryContactOffRate"} |  | 16,1,DryContactOffRate,5,3019,0,2,0
| 3 | 3020 | BoxCtrlInvOrder | BoxCtrlInvOrderOff-net box control instruct ion | R/W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BoxCtrlInvOrder "Growatt_BoxCtrlInvOrder" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BoxCtrlInvOrder", formatBeforePublish="BoxCtrlInvOrder%s"] | Number Growatt_BoxCtrlInvOrder "BoxCtrlInvOrder" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BoxCtrlInvOrder"} |  | 16,1,BoxCtrlInvOrder,5,3020,0,2,0
| 3 | 3021 | ExterCommOffGridEn | External communication setting manual off-network enable | R/W |  |  |  |  | PV9_32 |  |  | 0 | Type number : ExterCommOffGridEn "Growatt_ExterCommOffGridEn" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ExterCommOffGridEn", formatBeforePublish="ExterCommOffGridEn%s"] | Number Growatt_ExterCommOffGridEn "ExterCommOffGridEn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ExterCommOffGridEn"} |  | 16,1,ExterCommOffGridEn,5,3021,0,2,0
| 3 | 3022 | uwBdcStopWorkOfBusVolt | BdcStopWorkOfBusVolt | R |  |  |  | ASCII | ALL |  |  | 0 | Type number : uwBdcStopWorkOfBusVolt "Growatt_uwBdcStopWorkOfBusVolt" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwBdcStopWorkOfBusVolt", formatBeforePublish="uwBdcStopWorkOfBusVolt%s"] | Number Growatt_uwBdcStopWorkOfBusVolt "uwBdcStopWorkOfBusVolt" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwBdcStopWorkOfBusVolt"} |  | 16,1,uwBdcStopWorkOfBusVolt,5,3022,0,2,0
| 3 | 3023 | bGridType | GridType---0:SinglePhase | R/W | 0?1?2 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bGridType "Growatt_bGridType" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bGridType", formatBeforePublish="bGridType%s"] | Number Growatt_bGridType "bGridType" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bGridType"} |  | 16,1,bGridType,5,3023,0,2,0
| 3 | 3024 | Floatchargecurrentlimit | When charge current battery need is lower than | R/W |  | 0.1A | 600 |  | PV9_32 | 0.1 | A | 1 | Type number : Floatchargecurrentlimit "Growatt_Floatchargecurrentlimit" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Floatchargecurrentlimit", formatBeforePublish="Floatchargecurrentlimit%s"] | Number:ElectricCurrent Growatt_Floatchargecurrentlimit "Floatchargecurrentlimit [%0.1f A]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Floatchargecurrentlimit"} |  | 16,1,Floatchargecurrentlimit,5,3024,0,2,0
| 3 | 3025 | VbatWarning | "Battery-low" warning setup voltage | R/W |  | 0.1V | 4800 |  | ALL | 0.1 | V | 1 | Type number : VbatWarning "Growatt_VbatWarning" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.VbatWarning", formatBeforePublish="VbatWarning%s"] | Number:ElectricPotential Growatt_VbatWarning "VbatWarning [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:VbatWarning"} |  | 16,1,VbatWarning,5,3025,0,2,0
| 3 | 3026 | VbatlowWarn | "Battery-low" warning clear voltage | R/W |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : VbatlowWarn "Growatt_VbatlowWarn" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.VbatlowWarn", formatBeforePublish="VbatlowWarn%s"] | Number:ElectricPotential Growatt_VbatlowWarn "VbatlowWarn [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:VbatlowWarn"} |  | 16,1,VbatlowWarn,5,3026,0,2,0
| 3 | 3027 | Vbatstopfordischarge | Battery cut off voltage | R/W |  | 0.1V |  |  | ALL | 0.1 | V | 1 | Type number : Vbatstopfordischarge "Growatt_Vbatstopfordischarge" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vbatstopfordischarge", formatBeforePublish="Vbatstopfordischarge%s"] | Number:ElectricPotential Growatt_Vbatstopfordischarge "Vbatstopfordischarge [%0.1f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbatstopfordischarge"} |  | 16,1,Vbatstopfordischarge,5,3027,0,2,0
| 3 | 3028 | Vbatstopforcharge | Battery over charge voltage | R/W |  | 0.01V | 5800 |  | ALL | 0.01 | V | 2 | Type number : Vbatstopforcharge "Growatt_Vbatstopforcharge" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vbatstopforcharge", formatBeforePublish="Vbatstopforcharge%s"] | Number:ElectricPotential Growatt_Vbatstopforcharge "Vbatstopforcharge [%0.01f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbatstopforcharge"} |  | 16,1,Vbatstopforcharge,5,3028,0,2,0
| 3 | 3029 | Vbatstartfordischarge | Battery start discharge voltage | R/W |  | 0.01V | 4800 |  | ALL | 0.01 | V | 2 | Type number : Vbatstartfordischarge "Growatt_Vbatstartfordischarge" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vbatstartfordischarge", formatBeforePublish="Vbatstartfordischarge%s"] | Number:ElectricPotential Growatt_Vbatstartfordischarge "Vbatstartfordischarge [%0.01f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbatstartfordischarge"} |  | 16,1,Vbatstartfordischarge,5,3029,0,2,0
| 3 | 3030 | Vbatconstantcharge | Battery constant charge voltage | R/W |  | 0.01V | 5800 |  | ALL | 0.01 | V | 2 | Type number : Vbatconstantcharge "Growatt_Vbatconstantcharge" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Vbatconstantcharge", formatBeforePublish="Vbatconstantcharge%s"] | Number:ElectricPotential Growatt_Vbatconstantcharge "Vbatconstantcharge [%0.01f V]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Vbatconstantcharge"} |  | 16,1,Vbatconstantcharge,5,3030,0,2,0
| 3 | 3031 | Battemplowerlimitd | Battery temperature lower limit for discharge | R/W |  | 0.1? | 1170 |  | TL_X-TL_XH | 0.1 | ? | 1 | Type number : Battemplowerlimitd "Growatt_Battemplowerlimitd" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Battemplowerlimitd", formatBeforePublish="Battemplowerlimitd%s"] | Number:Length Growatt_Battemplowerlimitd "Battemplowerlimitd [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Battemplowerlimitd"} |  | 16,1,Battemplowerlimitd,5,3031,0,2,0
| 3 | 3032 | Battempupperlimitd | Battery temperature upper limit for discharge | R/W |  | 0.1? | 420 |  | TL_X-TL_XH | 0.1 | ? | 1 | Type number : Battempupperlimitd "Growatt_Battempupperlimitd" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Battempupperlimitd", formatBeforePublish="Battempupperlimitd%s"] | Number:Length Growatt_Battempupperlimitd "Battempupperlimitd [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Battempupperlimitd"} |  | 16,1,Battempupperlimitd,5,3032,0,2,0
| 3 | 3033 | Battemplowerlimitc | Battery temperature lower limit for charge | R/W |  | 0.1? | 30 |  | TL_X-TL_XH | 0.1 | ? | 1 | Type number : Battemplowerlimitc "Growatt_Battemplowerlimitc" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Battemplowerlimitc", formatBeforePublish="Battemplowerlimitc%s"] | Number:Length Growatt_Battemplowerlimitc "Battemplowerlimitc [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Battemplowerlimitc"} |  | 16,1,Battemplowerlimitc,5,3033,0,2,0
| 3 | 3034 | Battempupperlimitc | Battery temperature upper limit for charge | R/W |  | 0.1? | 370 |  | TL_X-TL_XH | 0.1 | ? | 1 | Type number : Battempupperlimitc "Growatt_Battempupperlimitc" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Battempupperlimitc", formatBeforePublish="Battempupperlimitc%s"] | Number:Length Growatt_Battempupperlimitc "Battempupperlimitc [%0.1f ?]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Battempupperlimitc"} |  | 16,1,Battempupperlimitc,5,3034,0,2,0
| 3 | 3035 | uwUnderFreDischargeDelyTime | Under Fre Delay Time | R/W |  | 50ms |  |  | ALL | 50 | ms | 1 | Type number : uwUnderFreDischargeDelyTime "Growatt_uwUnderFreDischargeDelyTime" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwUnderFreDischargeDelyTime", formatBeforePublish="uwUnderFreDischargeDelyTime%s"] | #N/A |  | 16,1,uwUnderFreDischargeDelyTime,5,3035,0,2,0
| 3 | 3036 | GridFirstDischargePowerRate | Discharge Power Rate when Grid First |  |  |  | 1-255 |  | ALL |  |  | 0 | Type number : GridFirstDischargePowerRate "Growatt_GridFirstDischargePowerRate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstDischargePowerRate", formatBeforePublish="GridFirstDischargePowerRate%s"] | Number Growatt_GridFirstDischargePowerRate "GridFirstDischargePowerRate" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstDischargePowerRate"} |  | 16,1,GridFirstDischargePowerRate,5,3036,0,2,0
| 3 | 3037 | GridFirstStopS | Stop Discharge soc when |  |  |  | 1-100 |  | ALL |  |  | 0 | Type number : GridFirstStopS "Growatt_GridFirstStopS" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.GridFirstStopS", formatBeforePublish="GridFirstStopS%s"] | Number Growatt_GridFirstStopS "GridFirstStopS" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:GridFirstStopS"} |  | 16,1,GridFirstStopS,5,3037,0,2,0
| 3 | 3038 | Time1 | Period 1: [Start Time ~ End | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time1 "Growatt_Time1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time1", formatBeforePublish="Time1%s"] | Number Growatt_Time1 "Time1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time1"} |  | 16,1,Time1,5,3038,0,2,0
| 3 | 3040 | Time2 | Time period 2: [start time ~ end time], [charge / | R/W |  |  |  | -1000~1000:Inductive(100% | ALL |  |  | 0 | Type number : Time2 "Growatt_Time2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time2", formatBeforePublish="Time2%s"] | Number Growatt_Time2 "Time2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time2"} |  | 16,1,Time2,5,3040,0,2,0
| 3 | 3042 | Time3 | With Time1 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time3 "Growatt_Time3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time3", formatBeforePublish="Time3%s"] | Number Growatt_Time3 "Time3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time3"} |  | 16,1,Time3,5,3042,0,2,0
| 3 | 3044 | Time4 | With Time1 | R/W |  |  |  | When the Vref mode is not activated, the V1~V4 and Q1~Q4 upper computer of the QV curve can be adjusted; | ALL |  |  | 0 | Type number : Time4 "Growatt_Time4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time4", formatBeforePublish="Time4%s"] | Number Growatt_Time4 "Time4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time4"} |  | 16,1,Time4,5,3044,0,2,0
| 3 | 3047 | BatFirstPower | Charge Power Rate when |  |  |  | 1-100 |  | TL_X-TL_XH |  |  | 0 | Type number : BatFirstPower "Growatt_BatFirstPower" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatFirstPower", formatBeforePublish="BatFirstPower%s"] | Number Growatt_BatFirstPower "BatFirstPower" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatFirstPower"} |  | 16,1,BatFirstPower,5,3047,0,2,0
| 3 | 3048 | wBatFirststop | Stop Charge soc when Bat |  |  |  | 1-100 |  | ALL |  |  | 0 | Type number : wBatFirststop "Growatt_wBatFirststop" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.wBatFirststop", formatBeforePublish="wBatFirststop%s"] | Number Growatt_wBatFirststop "wBatFirststop" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:wBatFirststop"} |  | 16,1,wBatFirststop,5,3048,0,2,0
| 3 | 3049 | AcChargeEnable | AcChargeEnable | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : AcChargeEnable "Growatt_AcChargeEnable" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.AcChargeEnable", formatBeforePublish="AcChargeEnable%s"] | Number Growatt_AcChargeEnable "AcChargeEnable" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:AcChargeEnable"} |  | 16,1,AcChargeEnable,5,3049,0,2,0
| 3 | 3050 | Time5 | With Time1 | R/W |  |  |  | Capacitive 30% | ALL |  |  | 0 | Type number : Time5 "Growatt_Time5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time5", formatBeforePublish="Time5%s"] | Number Growatt_Time5 "Time5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time5"} |  | 16,1,Time5,5,3050,0,2,0
| 3 | 3052 | Time6 | With Time1 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time6 "Growatt_Time6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time6", formatBeforePublish="Time6%s"] | Number Growatt_Time6 "Time6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time6"} |  | 16,1,Time6,5,3052,0,2,0
| 3 | 3054 | Time7 | With Time1 | R/W |  |  |  | 0:disable,1:enable | ALL |  |  | 0 | Type number : Time7 "Growatt_Time7" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time7", formatBeforePublish="Time7%s"] | Number Growatt_Time7 "Time7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time7"} |  | 16,1,Time7,5,3054,0,2,0
| 3 | 3056 | Time8 | With Time1 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time8 "Growatt_Time8" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time8", formatBeforePublish="Time8%s"] | Number Growatt_Time8 "Time8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time8"} |  | 16,1,Time8,5,3056,0,2,0
| 3 | 3058 | Time9 | With Time1 | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time9 "Growatt_Time9" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time9", formatBeforePublish="Time9%s"] | Number Growatt_Time9 "Time9" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time9"} |  | 16,1,Time9,5,3058,0,2,0
| 3 | 3070 | BatteryType | Battery type choose of buck-boost input | R/W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatteryType "Growatt_BatteryType" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatteryType", formatBeforePublish="BatteryType%s"] | Number Growatt_BatteryType "BatteryType" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatteryType"} |  | 16,1,BatteryType,5,3070,0,2,0
| 3 | 3071 | BatMdlSeria_ | BatMdlSeria/ParalNum | R/W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BatMdlSeria_ "Growatt_BatMdlSeria_" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BatMdlSeria_", formatBeforePublish="BatMdlSeria_%s"] | Number Growatt_BatMdlSeria_ "BatMdlSeria_" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BatMdlSeria_"} |  | 16,1,BatMdlSeria_,5,3071,0,2,0
| 3 | 3072 | Reserved | [5 empty] | SPA/ reserve | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 16,1,Reserved,5,3072,0,2,0
| 3 | 3073 | Reserved | [5 empty] | SPA/ reserve | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 16,1,Reserved,5,3073,0,2,0
| 3 | 3074 | Reserved | [5 empty] | SPA/ reserve | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 16,1,Reserved,5,3074,0,2,0
| 3 | 3075 | Reserved | [5 empty] | SPA/ reserve | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 16,1,Reserved,5,3075,0,2,0
| 3 | 3076 | Reserved | [5 empty] | SPA/ reserve | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 16,1,Reserved,5,3076,0,2,0
| 3 | 3077 | Reserved | [5 empty] | SPA/ reserve | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 16,1,Reserved,5,3077,0,2,0
| 3 | 3078 | Reserved | [5 empty] | 0:The old formula | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 16,1,Reserved,5,3078,0,2,0
| 3 | 3079 | UpsFunEn | Ups function enable or disable | R/W |  |  | 0 | ASCII | ALL |  |  | 0 | Type number : UpsFunEn "Growatt_UpsFunEn" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.UpsFunEn", formatBeforePublish="UpsFunEn%s"] | Number Growatt_UpsFunEn "UpsFunEn" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:UpsFunEn"} |  | 16,1,UpsFunEn,5,3079,0,2,0
| 3 | 3080 | UPSVoltSet | UPS output voltage | R/W |  |  | 0 | ASCII | ALL |  |  | 0 | Type number : UPSVoltSet "Growatt_UPSVoltSet" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.UPSVoltSet", formatBeforePublish="UPSVoltSet%s"] | Number Growatt_UPSVoltSet "UPSVoltSet" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:UPSVoltSet"} |  | 16,1,UPSVoltSet,5,3080,0,2,0
| 3 | 3081 | UPSFreqSet | UPS output frequency | R/W |  |  | 0 | ASCII | ALL |  |  | 0 | Type number : UPSFreqSet "Growatt_UPSFreqSet" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.UPSFreqSet", formatBeforePublish="UPSFreqSet%s"] | Number Growatt_UPSFreqSet "UPSFreqSet" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:UPSFreqSet"} |  | 16,1,UPSFreqSet,5,3081,0,2,0
X | 3 | 3082 | bLoadFirstStopSocSet | StopSoc When LoadFirst | W | 13-100 |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : bLoadFirstStopSocSet "Growatt_bLoadFirstStopSocSet" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.bLoadFirstStopSocSet", formatBeforePublish="bLoadFirstStopSocSet%s"] | Number Growatt_bLoadFirstStopSocSet "bLoadFirstStopSocSet" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:bLoadFirstStopSocSet"} |  | 17,1,bLoadFirstStopSocSet,5,3082,0,2,0
| 3 | 3083 | Reserved | [5 empty] | MIX US | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 17,1,Reserved,5,3083,0,2,0
| 3 | 3084 | Reserved | [5 empty] | MIX US | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 17,1,Reserved,5,3084,0,2,0
| 3 | 3085 | ComAddress | Communication addr | R/W |  |  | 1 | PV energy | TL_X-TL_XH |  |  | 0 | Type number : ComAddress "Growatt_ComAddress" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ComAddress", formatBeforePublish="ComAddress%s"] | Number Growatt_ComAddress "ComAddress" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ComAddress"} |  | 17,1,ComAddress,5,3085,0,2,0
| 3 | 3086 | BaudRate | Communication BaudRate | R/W |  |  | 0 |  | TL_X-TL_XH |  |  | 0 | Type number : BaudRate "Growatt_BaudRate" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BaudRate", formatBeforePublish="BaudRate%s"] | Number Growatt_BaudRate "BaudRate" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BaudRate"} |  | 17,1,BaudRate,5,3086,0,2,0
| 3 | 3087 | SerialNO1 | Serial Number 1-2 | R/W |  |  |  | Grid First enable | Storage |  |  | 0 | Type number : SerialNO1 "Growatt_SerialNO1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNO1", formatBeforePublish="SerialNO1%s"] | Number Growatt_SerialNO1 "SerialNO1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNO1"} |  | 17,1,SerialNO1,5,3087,0,2,0
| 3 | 3088 | SerialNO2 | Serial Number 3-4 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SerialNO2 "Growatt_SerialNO2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNO2", formatBeforePublish="SerialNO2%s"] | Number Growatt_SerialNO2 "SerialNO2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNO2"} |  | 17,1,SerialNO2,5,3088,0,2,0
| 3 | 3089 | SerialNO3 | Serial Number 5-6 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SerialNO3 "Growatt_SerialNO3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNO3", formatBeforePublish="SerialNO3%s"] | Number Growatt_SerialNO3 "SerialNO3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNO3"} |  | 17,1,SerialNO3,5,3089,0,2,0
| 3 | 3090 | SerialNO4 | Serial Number 7-8 | R/W |  |  |  | Grid First enable | Storage |  |  | 0 | Type number : SerialNO4 "Growatt_SerialNO4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNO4", formatBeforePublish="SerialNO4%s"] | Number Growatt_SerialNO4 "SerialNO4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNO4"} |  | 17,1,SerialNO4,5,3090,0,2,0
| 3 | 3091 | SerialNo5 | Serial Number 9-10 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SerialNo5 "Growatt_SerialNo5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNo5", formatBeforePublish="SerialNo5%s"] | Number Growatt_SerialNo5 "SerialNo5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNo5"} |  | 17,1,SerialNo5,5,3091,0,2,0
| 3 | 3092 | SerialNo6 | Serial Number 11-12 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SerialNo6 "Growatt_SerialNo6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNo6", formatBeforePublish="SerialNo6%s"] | Number Growatt_SerialNo6 "SerialNo6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNo6"} |  | 17,1,SerialNo6,5,3092,0,2,0
| 3 | 3093 | SerialNo7 | Serial Number 13-14 | R/W |  |  |  | Grid First enable | Storage |  |  | 0 | Type number : SerialNo7 "Growatt_SerialNo7" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNo7", formatBeforePublish="SerialNo7%s"] | Number Growatt_SerialNo7 "SerialNo7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNo7"} |  | 17,1,SerialNo7,5,3093,0,2,0
| 3 | 3094 | SerialNo8 | Serial Number 15-16 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SerialNo8 "Growatt_SerialNo8" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SerialNo8", formatBeforePublish="SerialNo8%s"] | Number Growatt_SerialNo8 "SerialNo8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SerialNo8"} |  | 17,1,SerialNo8,5,3094,0,2,0
| 3 | 3095 | BdcResetCmd | BDC Reset command | R/W |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BdcResetCmd "Growatt_BdcResetCmd" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BdcResetCmd", formatBeforePublish="BdcResetCmd%s"] | Number Growatt_BdcResetCmd "BdcResetCmd" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BdcResetCmd"} |  | 17,1,BdcResetCmd,5,3095,0,2,0
| 3 | 3096 | ARKM3Code | BDCMonitoring software code | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : ARKM3Code "Growatt_ARKM3Code" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ARKM3Code", formatBeforePublish="ARKM3Code%s"] | Number Growatt_ARKM3Code "ARKM3Code" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ARKM3Code"} |  | 17,1,ARKM3Code,5,3096,0,2,0
| 3 | 3098 | DTC | DTC | R |  |  |  |  | BMS |  |  | 0 | Type number : DTC "Growatt_DTC" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.DTC", formatBeforePublish="DTC%s"] | Number Growatt_DTC "DTC" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:DTC"} |  | 17,1,DTC,5,3098,0,2,0
| 3 | 3099 | FWCode | DSP software code | R |  |  |  |  | PV9_32 |  |  | 0 | Type number : FWCode "Growatt_FWCode" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.FWCode", formatBeforePublish="FWCode%s"] | Number Growatt_FWCode "FWCode" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:FWCode"} |  | 17,1,FWCode,5,3099,0,2,0
| 3 | 3101 | Processor1 | DSP Software Version | R |  |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : Processor1 "Growatt_Processor1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Processor1", formatBeforePublish="Processor1%s"] | Number Growatt_Processor1 "Processor1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Processor1"} |  | 17,1,Processor1,5,3101,0,2,0
| 3 | 3102 | BusVoltRef | Minimum BUS voltage for charging and discharging batteries | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : BusVoltRef "Growatt_BusVoltRef" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BusVoltRef", formatBeforePublish="BusVoltRef%s"] | Number Growatt_BusVoltRef "BusVoltRef" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BusVoltRef"} |  | 17,1,BusVoltRef,5,3102,0,2,0
| 3 | 3103 | ARKM3Ver | BDC monitoring software version | R |  |  |  |  | TL_X-TL_XH |  |  | 0 | Type number : ARKM3Ver "Growatt_ARKM3Ver" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.ARKM3Ver", formatBeforePublish="ARKM3Ver%s"] | Number Growatt_ARKM3Ver "ARKM3Ver" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:ARKM3Ver"} |  | 17,1,ARKM3Ver,5,3103,0,2,0
| 3 | 3104 | BMS_MCUVersion | BMS hardware version | R |  | 1 |  |  | TL_X-TL_XH | 1 |  | 0 | Type number : BMS_MCUVersion "Growatt_BMS_MCUVersion" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BMS_MCUVersion", formatBeforePublish="BMS_MCUVersion%s"] | Number Growatt_BMS_MCUVersion "BMS_MCUVersion [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_MCUVersion"} |  | 17,1,BMS_MCUVersion,5,3104,0,2,0
| 3 | 3105 | BMS_FW | BMS software version information | R |  | 1 |  | Current | TL_X-TL_XH | 1 |  | 0 | Type number : BMS_FW "Growatt_BMS_FW" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BMS_FW", formatBeforePublish="BMS_FW%s"] | Number Growatt_BMS_FW "BMS_FW [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_FW"} |  | 17,1,BMS_FW,5,3105,0,2,0
| 3 | 3106 | BMS_Info | BMS ManufacturerName | R |  | 1 |  | 0 : waiting | TL_X-TL_XH | 1 |  | 0 | Type number : BMS_Info "Growatt_BMS_Info" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BMS_Info", formatBeforePublish="BMS_Info%s"] | Number Growatt_BMS_Info "BMS_Info [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMS_Info"} |  | 17,1,BMS_Info,5,3106,0,2,0
| 3 | 3107 | BMSCommType | BMSCommType | R |  | 1 |  | 0:cNOTDerate 1:cPVHighDer ate | TL_X-TL_XH | 1 |  | 0 | Type number : BMSCommType "Growatt_BMSCommType" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BMSCommType", formatBeforePublish="BMSCommType%s"] | Number Growatt_BMSCommType "BMSCommType [%1f ]" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BMSCommType"} |  | 17,1,BMSCommType,5,3107,0,2,0
| 3 | 3108 | Module4 | BDCmodel (4) | R/W | &*11 |  |  |  | ALL |  |  | 0 | Type number : Module4 "Growatt_Module4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Module4", formatBeforePublish="Module4%s"] | Number Growatt_Module4 "Module4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Module4"} |  | 17,1,Module4,5,3108,0,2,0
| 3 | 3109 | Module3 | BDCmodel (3) | R/W | &*11 |  |  |  | ALL |  |  | 0 | Type number : Module3 "Growatt_Module3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Module3", formatBeforePublish="Module3%s"] | Number Growatt_Module3 "Module3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Module3"} |  | 17,1,Module3,5,3109,0,2,0
| 3 | 3110 | Module2 | BDCmodel (2) | R/W | &*11 |  |  |  | ALL |  |  | 0 | Type number : Module2 "Growatt_Module2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Module2", formatBeforePublish="Module2%s"] | Number Growatt_Module2 "Module2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Module2"} |  | 17,1,Module2,5,3110,0,2,0
| 3 | 3111 | Module1 | BDCmodel (1) | R/W | &*11 |  |  |  | ALL |  |  | 0 | Type number : Module1 "Growatt_Module1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Module1", formatBeforePublish="Module1%s"] | Number Growatt_Module1 "Module1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Module1"} |  | 17,1,Module1,5,3111,0,2,0
| 3 | 3112 | Reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 17,1,Reserved,5,3112,0,2,0
| 3 | 3113 | unProtocolVe | BDCProtocolVer | R | 1 |  |  | ASCII | ALL |  |  | 0 | Type number : unProtocolVe "Growatt_unProtocolVe" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.unProtocolVe", formatBeforePublish="unProtocolVe%s"] | Number Growatt_unProtocolVe "unProtocolVe" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:unProtocolVe"} |  | 17,1,unProtocolVe,5,3113,0,2,0
| 3 | 3114 | uwCertificationVer | BDC CertificationVer | R | 1 |  |  | ASCII | ALL |  |  | 0 | Type number : uwCertificationVer "Growatt_uwCertificationVer" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.uwCertificationVer", formatBeforePublish="uwCertificationVer%s"] | Number Growatt_uwCertificationVer "uwCertificationVer" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:uwCertificationVer"} |  | 17,1,uwCertificationVer,5,3114,0,2,0
| 3 | 3125 | TimeMonth1 | Use with Time1-9(us) | R/W |  |  |  | Parallel AntiBackflow Power | ALL |  |  | 0 | Type number : TimeMonth1 "Growatt_TimeMonth1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.TimeMonth1", formatBeforePublish="TimeMonth1%s"] | Number Growatt_TimeMonth1 "TimeMonth1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TimeMonth1"} |  | 17,1,TimeMonth1,5,3125,0,2,0
| 3 | 3126 | TimeMonth2 | Use with Time10-18(us) | R/W |  |  |  | AntiBackflow Failure | ALL |  |  | 0 | Type number : TimeMonth2 "Growatt_TimeMonth2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.TimeMonth2", formatBeforePublish="TimeMonth2%s"] | Number Growatt_TimeMonth2 "TimeMonth2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TimeMonth2"} |  | 17,1,TimeMonth2,5,3126,0,2,0
| 3 | 3127 | TimeMonth3 | Use with Time19-27(us) | R/W |  |  |  | Parallel anti-Backflow open enable bit | ALL |  |  | 0 | Type number : TimeMonth3 "Growatt_TimeMonth3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.TimeMonth3", formatBeforePublish="TimeMonth3%s"] | Number Growatt_TimeMonth3 "TimeMonth3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TimeMonth3"} |  | 17,1,TimeMonth3,5,3127,0,2,0
| 3 | 3128 | TimeMonth4 | Use with Time28-36(us) | R/W |  |  |  | Reactive power adjustment speed setting item, n%Pn/s, 0 means that the loading speed is not enabled, that is, it is directly loaded to the set value | ALL |  |  | 0 | Type number : TimeMonth4 "Growatt_TimeMonth4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.TimeMonth4", formatBeforePublish="TimeMonth4%s"] | Number Growatt_TimeMonth4 "TimeMonth4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:TimeMonth4"} |  | 17,1,TimeMonth4,5,3128,0,2,0
| 3 | 3129 | Time1 | time1:[starttime~endtime] | R/W |  |  |  | 0xA0:AFCI off | ALL |  |  | 0 | Type number : Time1 "Growatt_Time1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time1", formatBeforePublish="Time1%s"] | Number Growatt_Time1 "Time1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time1"} |  | 17,1,Time1,5,3129,0,2,0
| 3 | 3201 | SpecialDay1MD | SpecialDay1(month,Day) | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay1MD "Growatt_SpecialDay1MD" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay1MD", formatBeforePublish="SpecialDay1MD%s"] | Number Growatt_SpecialDay1MD "SpecialDay1MD" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay1MD"} |  | 17,1,SpecialDay1MD,5,3201,0,2,0
| 3 | 3202 | SpecialDay1_Time1 | Start time | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay1_Time1 "Growatt_SpecialDay1_Time1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay1_Time1", formatBeforePublish="SpecialDay1_Time1%s"] | Number Growatt_SpecialDay1_Time1 "SpecialDay1_Time1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay1_Time1"} |  | 17,1,SpecialDay1_Time1,5,3202,0,2,0
| 3 | 3220 | SpecialDay2MD | SpecialDay2(month,Day) | R/W |  |  |  | Battery priority enable 1 | Storage |  |  | 0 | Type number : SpecialDay2MD "Growatt_SpecialDay2MD" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay2MD", formatBeforePublish="SpecialDay2MD%s"] | Number Growatt_SpecialDay2MD "SpecialDay2MD" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay2MD"} |  | 17,1,SpecialDay2MD,5,3220,0,2,0
| 3 | 3221 | SpecialDay2_Time1 | Start time | R/W |  |  |  | Grid priority enable | Storage |  |  | 0 | Type number : SpecialDay2_Time1 "Growatt_SpecialDay2_Time1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay2_Time1", formatBeforePublish="SpecialDay2_Time1%s"] | Number Growatt_SpecialDay2_Time1 "SpecialDay2_Time1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay2_Time1"} |  | 17,1,SpecialDay2_Time1,5,3221,0,2,0
| 3 | 3060~ | Reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 17,1,Reserved,5,3060~,0,2,0
| 3 | 3115 ~ | Reserved | [5 empty] | ASCII | Storage |  |  | 0 | Type number : Reserved "Growatt_Reserved" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserved", formatBeforePublish="Reserved%s"] | Number Growatt_Reserved "Reserved" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserved"} |  | 17,1,Reserved,5,3115 ~,0,2,0
| 3 | 3131-3132 | Time2 | Time 2(us) | R/W |  |  |  | -1000~1000:Inductive(100% | ALL |  |  | 0 | Type number : Time2 "Growatt_Time2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time2", formatBeforePublish="Time2%s"] | Number Growatt_Time2 "Time2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time2"} |  | 17,1,Time2,5,3131-3132,0,2,0
| 3 | 3133-3134 | Time3 | Time 3(us) | R/W |  |  |  | Used for Australian | ALL |  |  | 0 | Type number : Time3 "Growatt_Time3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time3", formatBeforePublish="Time3%s"] | Number Growatt_Time3 "Time3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time3"} |  | 17,1,Time3,5,3133-3134,0,2,0
| 3 | 3135-3136 | Time4 | Time 4(us) | R/W |  |  |  | Activate Vref mode, the output filter value is equal to | ALL |  |  | 0 | Type number : Time4 "Growatt_Time4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time4", formatBeforePublish="Time4%s"] | Number Growatt_Time4 "Time4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time4"} |  | 17,1,Time4,5,3135-3136,0,2,0
| 3 | 3137-3138 | Time5 | Time 5(us) | R/W |  |  |  | 1300); used for IEE1547 | ALL |  |  | 0 | Type number : Time5 "Growatt_Time5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time5", formatBeforePublish="Time5%s"] | Number Growatt_Time5 "Time5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time5"} |  | 17,1,Time5,5,3137-3138,0,2,0
| 3 | 3139-3140 | Time6 | Time 6(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time6 "Growatt_Time6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time6", formatBeforePublish="Time6%s"] | Number Growatt_Time6 "Time6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time6"} |  | 17,1,Time6,5,3139-3140,0,2,0
| 3 | 3141-3142 | Time7 | Time 7(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time7 "Growatt_Time7" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time7", formatBeforePublish="Time7%s"] | Number Growatt_Time7 "Time7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time7"} |  | 17,1,Time7,5,3141-3142,0,2,0
| 3 | 3143-3144 | Time8 | Time 8(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time8 "Growatt_Time8" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time8", formatBeforePublish="Time8%s"] | Number Growatt_Time8 "Time8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time8"} |  | 17,1,Time8,5,3143-3144,0,2,0
| 3 | 3145-3146 | Time9 | Time9(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time9 "Growatt_Time9" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time9", formatBeforePublish="Time9%s"] | Number Growatt_Time9 "Time9" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time9"} |  | 17,1,Time9,5,3145-3146,0,2,0
| 3 | 3147-3148 | Time10 | Time 10(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time10 "Growatt_Time10" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time10", formatBeforePublish="Time10%s"] | Number Growatt_Time10 "Time10" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time10"} |  | 17,1,Time10,5,3147-3148,0,2,0
| 3 | 3149-3150 | Time11 | Time 11(us) | R/W |  |  |  | 0:disable | ALL |  |  | 0 | Type number : Time11 "Growatt_Time11" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time11", formatBeforePublish="Time11%s"] | Number Growatt_Time11 "Time11" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time11"} |  | 17,1,Time11,5,3149-3150,0,2,0
| 3 | 3151-3152 | Time12 | Time 12(us) | R/W |  |  |  | For mobile APP use only | ALL |  |  | 0 | Type number : Time12 "Growatt_Time12" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time12", formatBeforePublish="Time12%s"] | Number Growatt_Time12 "Time12" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time12"} |  | 17,1,Time12,5,3151-3152,0,2,0
| 3 | 3153-3154 | Time13 | Time 13(us) | R/W |  |  |  | 0:disable | ALL |  |  | 0 | Type number : Time13 "Growatt_Time13" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time13", formatBeforePublish="Time13%s"] | Number Growatt_Time13 "Time13" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time13"} |  | 17,1,Time13,5,3153-3154,0,2,0
| 3 | 3155-3156 | Time14 | Time 14(us) | R/W |  |  |  | The unit is W | ALL |  |  | 0 | Type number : Time14 "Growatt_Time14" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time14", formatBeforePublish="Time14%s"] | Number Growatt_Time14 "Time14" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time14"} |  | 17,1,Time14,5,3155-3156,0,2,0
| 3 | 3157-3158 | Time15 | Time15(us) | R/W |  |  |  | 1:Meter | ALL |  |  | 0 | Type number : Time15 "Growatt_Time15" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time15", formatBeforePublish="Time15%s"] | Number Growatt_Time15 "Time15" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time15"} |  | 17,1,Time15,5,3157-3158,0,2,0
| 3 | 3159-3160 | Time16 | Time 16(us) | R/W |  |  |  | 0 means not enabled, that is, the function is not enabled; 1-1000 means n%Pn/min | ALL |  |  | 0 | Type number : Time16 "Growatt_Time16" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time16", formatBeforePublish="Time16%s"] | Number Growatt_Time16 "Time16" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time16"} |  | 17,1,Time16,5,3159-3160,0,2,0
| 3 | 3161-3162 | Time17 | Time 17(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time17 "Growatt_Time17" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time17", formatBeforePublish="Time17%s"] | Number Growatt_Time17 "Time17" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time17"} |  | 17,1,Time17,5,3161-3162,0,2,0
| 3 | 3163-3164 | Time18 | Time 18(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time18 "Growatt_Time18" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time18", formatBeforePublish="Time18%s"] | Number Growatt_Time18 "Time18" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time18"} |  | 17,1,Time18,5,3163-3164,0,2,0
| 3 | 3165-3166 | Time19 | Time 19(us) | R/W |  |  |  | -1000~1000:Inductive(100% | ALL |  |  | 0 | Type number : Time19 "Growatt_Time19" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time19", formatBeforePublish="Time19%s"] | Number Growatt_Time19 "Time19" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time19"} |  | 17,1,Time19,5,3165-3166,0,2,0
| 3 | 3167-3168 | Time20 | Time 20(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time20 "Growatt_Time20" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time20", formatBeforePublish="Time20%s"] | Number Growatt_Time20 "Time20" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time20"} |  | 17,1,Time20,5,3167-3168,0,2,0
| 3 | 3169-3170 | Time21 | Time 21(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time21 "Growatt_Time21" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time21", formatBeforePublish="Time21%s"] | Number Growatt_Time21 "Time21" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time21"} |  | 17,1,Time21,5,3169-3170,0,2,0
| 3 | 3171-3172 | Time22 | Time 22(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time22 "Growatt_Time22" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time22", formatBeforePublish="Time22%s"] | Number Growatt_Time22 "Time22" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time22"} |  | 17,1,Time22,5,3171-3172,0,2,0
| 3 | 3173-3174 | Time23 | Time 23(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time23 "Growatt_Time23" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time23", formatBeforePublish="Time23%s"] | Number Growatt_Time23 "Time23" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time23"} |  | 17,1,Time23,5,3173-3174,0,2,0
| 3 | 3175-3176 | Time24 | Time 24(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time24 "Growatt_Time24" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time24", formatBeforePublish="Time24%s"] | Number Growatt_Time24 "Time24" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time24"} |  | 17,1,Time24,5,3175-3176,0,2,0
| 3 | 3177-3178 | Time25 | Time 25(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time25 "Growatt_Time25" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time25", formatBeforePublish="Time25%s"] | Number Growatt_Time25 "Time25" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time25"} |  | 17,1,Time25,5,3177-3178,0,2,0
| 3 | 3179-3180 | Time26 | Time 26(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time26 "Growatt_Time26" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time26", formatBeforePublish="Time26%s"] | Number Growatt_Time26 "Time26" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time26"} |  | 17,1,Time26,5,3179-3180,0,2,0
| 3 | 3181-3182 | Time27 | Time 27(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time27 "Growatt_Time27" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time27", formatBeforePublish="Time27%s"] | Number Growatt_Time27 "Time27" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time27"} |  | 17,1,Time27,5,3181-3182,0,2,0
| 3 | 3183-3184 | Time28 | Time 28(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time28 "Growatt_Time28" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time28", formatBeforePublish="Time28%s"] | Number Growatt_Time28 "Time28" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time28"} |  | 17,1,Time28,5,3183-3184,0,2,0
| 3 | 3185-3186 | Time29 | Time 29(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time29 "Growatt_Time29" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time29", formatBeforePublish="Time29%s"] | Number Growatt_Time29 "Time29" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time29"} |  | 17,1,Time29,5,3185-3186,0,2,0
| 3 | 3187-3188 | Time30 | Time 30(us) | R/W |  |  |  |  | ALL |  |  | 0 | Type number : Time30 "Growatt_Time30" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time30", formatBeforePublish="Time30%s"] | Number Growatt_Time30 "Time30" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time30"} |  | 17,1,Time30,5,3187-3188,0,2,0
| 3 | 3189-3190 | Time31 | Time 31(us) | R/W |  |  |  | -1000~1000:Inductive(100% | ALL |  |  | 0 | Type number : Time31 "Growatt_Time31" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time31", formatBeforePublish="Time31%s"] | Number Growatt_Time31 "Time31" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time31"} |  | 17,1,Time31,5,3189-3190,0,2,0
| 3 | 3191-3192 | Time32 | Time 32(us) | R/W |  |  |  | -1000~1000:Inductive(100% | ALL |  |  | 0 | Type number : Time32 "Growatt_Time32" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time32", formatBeforePublish="Time32%s"] | Number Growatt_Time32 "Time32" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time32"} |  | 17,1,Time32,5,3191-3192,0,2,0
| 3 | 3193-3194 | Time33 | Time 33(us) | R/W |  |  |  | -1000~1000:Inductive(100% | ALL |  |  | 0 | Type number : Time33 "Growatt_Time33" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time33", formatBeforePublish="Time33%s"] | Number Growatt_Time33 "Time33" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time33"} |  | 17,1,Time33,5,3193-3194,0,2,0
| 3 | 3195-3196 | Time34 | Time 34(us) | R/W |  |  |  | used for IEE1547 | ALL |  |  | 0 | Type number : Time34 "Growatt_Time34" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time34", formatBeforePublish="Time34%s"] | Number Growatt_Time34 "Time34" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time34"} |  | 17,1,Time34,5,3195-3196,0,2,0
| 3 | 3197-3198 | Time35 | Time 35(us) | R/W |  |  |  | used for IEE1547 | ALL |  |  | 0 | Type number : Time35 "Growatt_Time35" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time35", formatBeforePublish="Time35%s"] | Number Growatt_Time35 "Time35" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time35"} |  | 17,1,Time35,5,3197-3198,0,2,0
| 3 | 3199-3200 | Time36 | Time 36(us) | R/W |  |  |  | used for IEE1547 | ALL |  |  | 0 | Type number : Time36 "Growatt_Time36" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Time36", formatBeforePublish="Time36%s"] | Number Growatt_Time36 "Time36" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Time36"} |  | 17,1,Time36,5,3199-3200,0,2,0
| 3 | 3204-3205 | SpecialDay1_Time2 | SpecialDay1_Time2 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay1_Time2 "Growatt_SpecialDay1_Time2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay1_Time2", formatBeforePublish="SpecialDay1_Time2%s"] | Number Growatt_SpecialDay1_Time2 "SpecialDay1_Time2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay1_Time2"} |  | 17,1,SpecialDay1_Time2,5,3204-3205,0,2,0
| 3 | 3206-3207 | SpecialDay1_Time3 | SpecialDay1_Time3 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay1_Time3 "Growatt_SpecialDay1_Time3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay1_Time3", formatBeforePublish="SpecialDay1_Time3%s"] | Number Growatt_SpecialDay1_Time3 "SpecialDay1_Time3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay1_Time3"} |  | 17,1,SpecialDay1_Time3,5,3206-3207,0,2,0
| 3 | 3208-3209 | SpecialDay1_Time4 | SpecialDay1_Time4 | R/W |  |  |  | 0.Load(de fault)/1.B attery/2.G rid | Storage |  |  | 0 | Type number : SpecialDay1_Time4 "Growatt_SpecialDay1_Time4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay1_Time4", formatBeforePublish="SpecialDay1_Time4%s"] | Number Growatt_SpecialDay1_Time4 "SpecialDay1_Time4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay1_Time4"} |  | 17,1,SpecialDay1_Time4,5,3208-3209,0,2,0
| 3 | 3210-3211 | SpecialDay1_Time5 | SpecialDay1_Time5 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay1_Time5 "Growatt_SpecialDay1_Time5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay1_Time5", formatBeforePublish="SpecialDay1_Time5%s"] | Number Growatt_SpecialDay1_Time5 "SpecialDay1_Time5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay1_Time5"} |  | 17,1,SpecialDay1_Time5,5,3210-3211,0,2,0
| 3 | 3212-3213 | SpecialDay1_Time6 | SpecialDay1_Time6 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay1_Time6 "Growatt_SpecialDay1_Time6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay1_Time6", formatBeforePublish="SpecialDay1_Time6%s"] | Number Growatt_SpecialDay1_Time6 "SpecialDay1_Time6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay1_Time6"} |  | 17,1,SpecialDay1_Time6,5,3212-3213,0,2,0
| 3 | 3214-3215 | SpecialDay1_Time7 | SpecialDay1_Time7 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay1_Time7 "Growatt_SpecialDay1_Time7" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay1_Time7", formatBeforePublish="SpecialDay1_Time7%s"] | Number Growatt_SpecialDay1_Time7 "SpecialDay1_Time7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay1_Time7"} |  | 17,1,SpecialDay1_Time7,5,3214-3215,0,2,0
| 3 | 3216-3217 | SpecialDay1_Time8 | SpecialDay1_Time8 | R/W |  |  |  | Grid priority enable | Storage |  |  | 0 | Type number : SpecialDay1_Time8 "Growatt_SpecialDay1_Time8" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay1_Time8", formatBeforePublish="SpecialDay1_Time8%s"] | Number Growatt_SpecialDay1_Time8 "SpecialDay1_Time8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay1_Time8"} |  | 17,1,SpecialDay1_Time8,5,3216-3217,0,2,0
| 3 | 3218-3219 | SpecialDay1_Time9 | SpecialDay1_Time9 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay1_Time9 "Growatt_SpecialDay1_Time9" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay1_Time9", formatBeforePublish="SpecialDay1_Time9%s"] | Number Growatt_SpecialDay1_Time9 "SpecialDay1_Time9" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay1_Time9"} |  | 17,1,SpecialDay1_Time9,5,3218-3219,0,2,0
| 3 | 3223-3224 | SpecialDay2_Time2 | SpecialDay2_Time2 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay2_Time2 "Growatt_SpecialDay2_Time2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay2_Time2", formatBeforePublish="SpecialDay2_Time2%s"] | Number Growatt_SpecialDay2_Time2 "SpecialDay2_Time2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay2_Time2"} |  | 17,1,SpecialDay2_Time2,5,3223-3224,0,2,0
| 3 | 3225-3226 | SpecialDay2_Time3 | SpecialDay2_Time3 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay2_Time3 "Growatt_SpecialDay2_Time3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay2_Time3", formatBeforePublish="SpecialDay2_Time3%s"] | Number Growatt_SpecialDay2_Time3 "SpecialDay2_Time3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay2_Time3"} |  | 17,1,SpecialDay2_Time3,5,3225-3226,0,2,0
| 3 | 3227-3228 | SpecialDay2_Time4 | SpecialDay2_Time4 | R/W |  |  |  | Grid priority enable | Storage |  |  | 0 | Type number : SpecialDay2_Time4 "Growatt_SpecialDay2_Time4" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay2_Time4", formatBeforePublish="SpecialDay2_Time4%s"] | Number Growatt_SpecialDay2_Time4 "SpecialDay2_Time4" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay2_Time4"} |  | 17,1,SpecialDay2_Time4,5,3227-3228,0,2,0
| 3 | 3229-3230 | SpecialDay2_Time5 | SpecialDay2_Time5 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay2_Time5 "Growatt_SpecialDay2_Time5" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay2_Time5", formatBeforePublish="SpecialDay2_Time5%s"] | Number Growatt_SpecialDay2_Time5 "SpecialDay2_Time5" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay2_Time5"} |  | 17,1,SpecialDay2_Time5,5,3229-3230,0,2,0
| 3 | 3231-3232 | SpecialDay2_Time6 | SpecialDay2_Time6 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay2_Time6 "Growatt_SpecialDay2_Time6" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay2_Time6", formatBeforePublish="SpecialDay2_Time6%s"] | Number Growatt_SpecialDay2_Time6 "SpecialDay2_Time6" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay2_Time6"} |  | 17,1,SpecialDay2_Time6,5,3231-3232,0,2,0
| 3 | 3233-3234 | SpecialDay2_Time7 | SpecialDay2_Time7 | R/W |  |  |  | Battery priority enable 1 | Storage |  |  | 0 | Type number : SpecialDay2_Time7 "Growatt_SpecialDay2_Time7" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay2_Time7", formatBeforePublish="SpecialDay2_Time7%s"] | Number Growatt_SpecialDay2_Time7 "SpecialDay2_Time7" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay2_Time7"} |  | 17,1,SpecialDay2_Time7,5,3233-3234,0,2,0
| 3 | 3235-3236 | SpecialDay2_Time8 | SpecialDay2_Time8 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay2_Time8 "Growatt_SpecialDay2_Time8" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay2_Time8", formatBeforePublish="SpecialDay2_Time8%s"] | Number Growatt_SpecialDay2_Time8 "SpecialDay2_Time8" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay2_Time8"} |  | 17,1,SpecialDay2_Time8,5,3235-3236,0,2,0
| 3 | 3237-3238 | SpecialDay2_Time9 | SpecialDay2_Time9 | R/W |  |  |  |  | Storage |  |  | 0 | Type number : SpecialDay2_Time9 "Growatt_SpecialDay2_Time9" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.SpecialDay2_Time9", formatBeforePublish="SpecialDay2_Time9%s"] | Number Growatt_SpecialDay2_Time9 "SpecialDay2_Time9" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:SpecialDay2_Time9"} |  | 17,1,SpecialDay2_Time9,5,3237-3238,0,2,0
| 3 | 3239-3249 | Reserve | Reserve | R/W |  |  |  | ASCII | TL_X-TL_XH |  |  | 0 | Type number : Reserve "Growatt_Reserve" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.Reserve", formatBeforePublish="Reserve%s"] | Number Growatt_Reserve "Reserve" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:Reserve"} |  | 17,1,Reserve,5,3239-3249,0,2,0
| 3 | 5000+(N-1)*40 | BDC_group_3 | Like Registers 3085-3124 |  |  |  |  | 0: Don't need | TL_X-TL_XH |  |  | 0 | Type number : BDC_group_3 "Growatt_BDC_group_3" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BDC_group_3", formatBeforePublish="BDC_group_3%s"] | Number Growatt_BDC_group_3 "BDC_group_3" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BDC_group_3"} |  | 17,1,BDC_group_3,5,5000+(N-1)*40,0,2,0
| 3 | 5000-2039 | BDC_group_1 | Like Registers 3085-3124 |  |  |  |  | BDC1 | TL_X-TL_XH |  |  | 0 | Type number : BDC_group_1 "Growatt_BDC_group_1" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BDC_group_1", formatBeforePublish="BDC_group_1%s"] | Number Growatt_BDC_group_1 "BDC_group_1" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BDC_group_1"} |  | 17,1,BDC_group_1,5,5000-2039,0,2,0
| 3 | 5040-5079 | BDC_group_2 | Like Registers 3085-3124 | [5 empty] | TL_X-TL_XH |  |  | 0 | Type number : BDC_group_2 "Growatt_BDC_group_2" [stateTopic="tele/WSABINV", commandTopic="cmnd/WSABINV", transformationPattern="JSONPATH:$.BDC_group_2", formatBeforePublish="BDC_group_2%s"] | Number Growatt_BDC_group_2 "BDC_group_2" <energy> (Photovoltaik, Boden) [PV-Anlage] {channel="mqtt:topic:growatt:BDC_group_2"} |  | 17,1,BDC_group_2,5,5040-5079,0,2,0

## SPH-WS-upload_old
NO. | Variable | Data Source | String | Modbus Slave Addr. | Modbus Function | Modbus RegAddr | 645 ID | 645 Type | Data Len | 4 Bytes Order | Data Format | Position of Bool | Decimal Position | Unit | With Qutation | Query Period | 645 version | Func sel | JSON array | substract | divide | FE number
1. | OnOff | Modbus RTU |  | 5 | 3 | 0 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
2. | InverterStatus | Modbus RTU |  | 5 | 4 | 0 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
3. | Ppv | Modbus RTU |  | 5 | 4 | 1 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
4. | Vpv1 | Modbus RTU |  | 5 | 4 | 3 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | V | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
5. | PV1Curr | Modbus RTU |  | 5 | 4 | 4 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | A | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
6. | Ppv1 | Modbus RTU |  | 5 | 4 | 5 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
7. | Vpv2 | Modbus RTU |  | 5 | 4 | 7 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | V | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
8. | PV2Curr | Modbus RTU |  | 5 | 4 | 8 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | A | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
9. | Ppv2 | Modbus RTU |  | 5 | 4 | 9 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
10. | Pac | Modbus RTU |  | 5 | 4 | 35 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
11. | Fac | Modbus RTU |  | 5 | 4 | 37 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | Hz | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
12. | Vac1 | Modbus RTU |  | 5 | 4 | 38 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | c | V | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
13. | Iac1 | Modbus RTU |  | 5 | 4 | 39 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | A | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
14. | Pac1 | Modbus RTU |  | 5 | 4 | 40 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | VA | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
16. | Vac2 | Modbus RTU |  | 5 | 4 | 42 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | V | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
18. | Eactotal | Modbus RTU |  | 5 | 4 | 55 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
19. | Epv1_today | Modbus RTU |  | 5 | 4 | 59 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
20. | Epv2_today | Modbus RTU |  | 5 | 4 | 63 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
21. | Temp1 | Modbus RTU |  | 5 | 4 | 93 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | C | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
22. | FaultMaincode | Modbus RTU |  | 5 | 4 | 105 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
23. | FaultSubcode | Modbus RTU |  | 5 | 4 | 107 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
24. | Warningbit | Modbus RTU |  | 5 | 4 | 110 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
25. | WarnSubcode | Modbus RTU |  | 5 | 4 | 111 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
26. | WarnMaincode | Modbus RTU |  | 5 | 4 | 112 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
27. | realPowerPercent | Modbus RTU |  | 5 | 4 | 113 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | % | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
28. | ACChargePower | Modbus RTU |  | 5 | 4 | 116 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
29. | Priority | Modbus RTU |  | 5 | 4 | 118 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
30. | uwSysWorkMode | Modbus RTU |  | 5 | 4 | 1000 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
31. | Pdischarge1 | Modbus RTU |  | 5 | 4 | 1009 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
32. | Pcharge1 | Modbus RTU |  | 5 | 4 | 1011 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
33. | Vbat | Modbus RTU |  | 5 | 4 | 1013 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | V | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
34. | SOC | Modbus RTU |  | 5 | 4 | 1014 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | % | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
35. | PactouserTotal | Modbus RTU |  | 5 | 4 | 1021 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
36. | Pactogridtotal | Modbus RTU |  | 5 | 4 | 1029 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
36. | PLocalLoadTotal | Modbus RTU |  | 5 | 4 | 1037 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 97 | 0 | 0 | 0 | 0 | 1.000001 | 0 | 255
37. | BatteryTemp | Modbus RTU |  | 5 | 4 | 1040 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | C | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
38. | Etouser_today | Modbus RTU |  | 5 | 4 | 1044 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
39. | Etouser_total | Modbus RTU |  | 5 | 4 | 1046 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
40. | Etogrid_today | Modbus RTU |  | 5 | 4 | 1048 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
41. | Etogrid_total | Modbus RTU |  | 5 | 4 | 1050 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
42. | Edischarge1_today | Modbus RTU |  | 5 | 4 | 1052 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
43. | Echarge1_today | Modbus RTU |  | 5 | 4 | 1056 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
44. | ElocalLoad_Today | Modbus RTU |  | 5 | 4 | 1060 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
45. | Loadpercent | Modbus RTU |  | 5 | 4 | 1080 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | % | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
46. | BMS_Status | Modbus RTU |  | 5 | 4 | 1083 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
47. | BMS_Error | Modbus RTU |  | 5 | 4 | 1085 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
48. | BMS_SOC | Modbus RTU |  | 5 | 4 | 1086 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | % | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
49. | BMS_BatteryVolt | Modbus RTU |  | 5 | 4 | 1087 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | V | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
50. | BMS_BatteryCur | Modbus RTU |  | 5 | 4 | 1088 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | A | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
51. | BMS_BatteryTemp | Modbus RTU |  | 5 | 4 | 1089 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 1 | C | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
52. | BMS_SOH | Modbus RTU |  | 5 | 4 | 1096 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | % | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
53. | BMS_WarnInfo | Modbus RTU |  | 5 | 4 | 1099 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
54. | BMS_BMSInfo | Modbus RTU |  | 5 | 4 | 1105 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 |  | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
55. | uwMaxCellVolt | Modbus RTU |  | 5 | 4 | 1108 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | V | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
56. | uwMinCellVolt | Modbus RTU |  | 5 | 4 | 1109 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | V | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
58. | MaxSOC | Modbus RTU |  | 5 | 4 | 1119 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | % | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
59. | MinSOC | Modbus RTU |  | 5 | 4 | 1120 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | % | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
60. | ACChargeEnergyToday | Modbus RTU |  | 5 | 4 | 1124 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
61. | ACChargePowerBMS | Modbus RTU |  | 5 | 4 | 1128 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
62. | Esystem_today | Modbus RTU |  | 5 | 4 | 1137 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
63. | Eself_today | Modbus RTU |  | 5 | 4 | 1141 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
64. | Psystem | Modbus RTU |  | 5 | 4 | 1145 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
65. | Pself | Modbus RTU |  | 5 | 4 | 1147 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | W | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
66. | EPVAll_Today | Modbus RTU |  | 5 | 4 | 1149 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 1 | kWh | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
Variable
OnOff
InverterStatus
PpvH
Vpv1
PV1Curr
Ppv1H
Vpv2
PV2Curr
Ppv2H
PacH
Fac
Vac1
Iac1
Pac1H
Pac1L
Vac2
EactodayL
EactotalH
Epv1_todayH
Epv2_todayH
Temp1
FaultMaincode
FaultSubcode
WarningbitH
WarnSubcode

## Units
| Typ | Verwendung | Beispiele für Einheiten
Cycle | Number | Allgemeiner numerischer Typ | Keine spezifische Einheit
°C | Number:Temperature | Temperaturwerte | °C, °F
km/h | Number:Speed | Geschwindigkeitswerte | km/h, m/s
M | Number:Length | Längenwerte | Meter, Kilometer
S | Number:Time | Zeitwerte (Dauern) | Sekunden, Minuten, Stunden
kWh | Number:Energy | Energiemengen | kWh, Joule
W | Number:Power | Leistungswerte | Watt, Kilowatt
V | Number:ElectricPotential | Spannungswerte | Volt
Hz | Number:Frequency | Frequenzwerte | Hertz
% | Number | Dimensionslos | %
hPa | Number:Pressure | Druckwerte | hPa, Bar
m² | Number:Area | Flächenwerte | Quadratmeter, Quadratkilometer
A | Number:ElectricCurrent | Stromwerte | Ampere
m/s² | Number:Acceleration | Beschleunigungswerte | m/s²
O | Number:Resistance | Widerstandswerte | Ohm
L | Number:Volume | Volumenwerte | Liter, Kubikmeter

## WS formats
NO. | JSON KeyWord | Data Source | String | Modbus Slave Addr. | Modbus Function | Modbus RegAddr | 645 ID | 645 Type | Data Len | 4 Bytes Order | Data Format | Position of Bool | Decimal Position | Unit | With Qutation | Query Period | 645 version | Func sel | JSON array | substract | divide | FE number
1. | uint16 | Modbus RTU |  | 5 | 3 | 1 | 1 | 9410 | 2 | 0 |  | 0 | 0 | unit | 0 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
2. | unint16+save | Modbus RTU |  | 5 | 3 | 2 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | unit | 0 | 100 | 97 | 8 | 0 | 0 | 1.000000 | 0 | 255
3. | uint16+s+set0 | Modbus RTU |  | 5 | 3 | 3 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | unit | 0 | 100 | 97 | 9 | 0 | 0 | 1.000000 | 0 | 255
4. | uint16+set0+set1 | Modbus RTU |  | 5 | 3 | 4 | 1 | 9410 | 2 | 0 | Unsigned int | 0 | 0 | unit | 0 | 100 | 97 | 11 | 0 | 0 | 1.000000 | 0 | 255
5. | sint16 | Modbus RTU |  | 5 | 3 | 5 | 1 | 9410 | 2 | 0 | Signed int | 0 | 0 | unit | 0 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
6. | bool | Modbus RTU |  | 5 | 3 | 6 | 1 | 9410 | 2 | 0 | bool | 0 | 0 | unit | 0 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
7. | float | Modbus RTU |  | 5 | 3 | 7 | 1 | 9410 | 4 | 0 | bool | 0 | 0 | unit | 0 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
8. | bigendian uint32 | Modbus RTU |  | 5 | 3 | 8 | 1 | 9410 | 4 | 0 | Unsigned int | 0 | 0 | unit | 0 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
9. | littleendian uint16 | Modbus RTU |  | 5 | 3 | 9 | 1 | 9410 | 2 | 1 | Unsigned int | 0 | 0 | unit | 0 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
10. | text | Modbus RTU |  | 5 | 3 | 10 | 1 | 9410 | 4 | 1 | Unsigned int | 0 | 0 | unit | 1 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
11. | unint16 1 decimal | Modbus RTU |  | 5 | 3 | 11 | 1 | 9410 | 2 | 1 | Unsigned int | 0 | 1 | unit | 0 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
12. | uint 2dec | Modbus RTU |  | 5 | 3 | 12 | 1 | 9410 | 2 | 1 | Unsigned int | 0 | 2 | unit | 0 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255
13. |  | Modbus RTU |  | 5 | 3 | 13 | 1 | 9410 | 2 | 1 | Unsigned int | 0 | 2 | unit | 0 | 100 | 97 | 0 | 0 | 0 | 1.000000 | 0 | 255